## Training_Data_48
Record_ID | H2 | CH4 | C2H6 | C2H4 | C2H2 | CO | CO2 | BDV | Moisture_PPM | WTI_HV | WTI_LV | OTI | Loading_pct | Ambient_Temp | Age_Years | IR_HV_E_1min | IR_LV_E_1min | IR_TV_E_1min | IR_HV_E_10min | IR_LV_E_10min | IR_TV_E_10min | PI_HV | PI_LV | PI_TV | Winding_HV_TanDelta_pct | Winding_LV_TanDelta_pct | Winding_TV_TanDelta_pct | Winding_HV_CapChange_pct | Winding_LV_CapChange_pct | Winding_TV_CapChange_pct | Bushing_HV_R_TanDelta_pct | Bushing_HV_Y_TanDelta_pct | Bushing_HV_B_TanDelta_pct | Bushing_HV_R_CapChange_pct | Bushing_HV_Y_CapChange_pct | Bushing_HV_B_CapChange_pct | Bushing_LV_R_TanDelta_pct | Bushing_LV_Y_TanDelta_pct | Bushing_LV_B_TanDelta_pct | Bushing_LV_R_CapChange_pct | Bushing_LV_Y_CapChange_pct | Bushing_LV_B_CapChange_pct | Bushing_TV_R_TanDelta_pct | Bushing_TV_Y_TanDelta_pct | Bushing_TV_B_TanDelta_pct | Bushing_TV_R_CapChange_pct | Bushing_TV_Y_CapChange_pct | Bushing_TV_B_CapChange_pct | Scenario_Generator | IR_Min_1min | IR_Min_10min | PI_Min | Max_Winding_TanDelta_pct | Max_Winding_CapChange_abs_pct | Max_Bushing_TanDelta_pct | Max_Bushing_CapChange_abs_pct | DGA_Subscore | Oil_Subscore | Thermal_Subscore | Age_Subscore | IR_PI_Subscore | Winding_TD_Cap_Subscore | Bushing_TD_Cap_Subscore | HI_PreCap | HI_Final | Condition | Binary_HI | Anomaly_Flag | Anomaly_Type | Hard_Cap_Flag | Hard_Cap_Reason | Dominant_Risk_Parameter
1 | 1766 | 982.4 | 144.9 | 197 | 33.2 | 1379 | 8750.7 | 55.8 | 23.6 | 83.3 | 86.5 | 76.7 | 89.4 | 37.7 | 23.6 | 7158.8 | 7761.2 | 97.3 | 11700.6 | 13544.9 | 165.5 | 1.634 | 1.745 | 1.701 | 0.575 | 0.594 | 0.592 | -3.5 | 3.03 | -2.99 | 0.641 | 0.631 | 0.596 | 3.17 | -3.18 | -3.79 | 0.609 | 0.618 | 0.623 | 4.35 | 3.42 | 4.39 | 0.591 | 0.559 | 0.605 | 2.31 | 3.41 | 3.66 | Critical_DGA | 97.3 | 165.5 | 1.634 | 0.594 | 3.5 | 0.641 | 4.39 | 0.0382 | 0.895 | 0.6865 | 0.628 | 0.85 | 0.722 | 0.6222 | 0.5661 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2 | 1600.4 | 842.7 | 140.6 | 193.8 | 34.1 | 1309.1 | 7992.9 | 33.7 | 46.4 | 106.2 | 109.3 | 94.7 | 117.4 | 45 | 33 | 1782.3 | 1780.3 | 1049.9 | 1972.9 | 2113.3 | 1204.3 | 1.107 | 1.187 | 1.147 | 0.987 | 0.981 | 0.944 | -9.33 | 9.49 | 8.91 | 0.771 | 0.82 | 0.99 | 7.6 | -6.97 | -8.92 | 0.769 | 0.926 | 0.817 | 7.72 | -7.07 | 8.27 | 0.966 | 0.805 | 0.852 | -8.41 | 6.3 | -8.97 | Very Poor_Mixed | 1049.9 | 1204.3 | 1.107 | 0.987 | 9.49 | 0.99 | 8.97 | 0.0848 | 0.6166 | 0.1047 | 0.2826 | 1 | 0.0568 | 0.1898 | 0.3219 | 0.3219 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
3 | 1433.5 | 865.7 | 133.2 | 175.2 | 25.9 | 1310.2 | 7080.4 | 34.9 | 46.6 | 101.7 | 99.3 | 91.3 | 109.5 | 43.5 | 31.1 | 1273.1 | 2506.9 | 3339.7 | 1546.2 | 3055.7 | 4334.3 | 1.215 | 1.219 | 1.298 | 0.963 | 0.99 | 0.949 | -9.34 | 8.01 | -9.36 | 0.807 | 0.945 | 0.886 | 5.33 | -7.58 | -6.54 | 0.901 | 0.874 | 0.935 | 8.82 | -7.52 | 5.28 | 0.854 | 0.886 | 0.747 | 8.53 | 6.04 | -8.53 | Very Poor_Mixed | 1273.1 | 1546.2 | 1.215 | 0.99 | 9.36 | 0.945 | 8.82 | 0.1648 | 0.6147 | 0.2556 | 0.3559 | 1 | 0.0763 | 0.1992 | 0.3648 | 0.3648 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
4 | 911.3 | 546.7 | 99.1 | 126.6 | 19 | 837.4 | 5620.8 | 45.6 | 32.6 | 92.9 | 90.6 | 83.7 | 97.3 | 40.3 | 24.9 | 5107.8 | 5398.5 | 5414.7 | 7617 | 8022.7 | 8431.5 | 1.491 | 1.486 | 1.557 | 0.7 | 0.717 | 0.734 | 5.46 | 5.79 | -5.76 | 0.611 | 0.653 | 0.685 | 4 | 3.57 | 5.16 | 0.649 | 0.625 | 0.687 | -4.33 | 4.16 | 3.97 | 0.711 | 0.666 | 0.628 | -5.33 | 3.8 | -4.56 | Poor_Mixed | 5107.8 | 7617 | 1.486 | 0.734 | 5.79 | 0.711 | 5.33 | 0.4168 | 0.7629 | 0.4904 | 0.5831 | 1 | 0.4361 | 0.5204 | 0.5887 | 0.5887 | Poor | 0 | 1 | DGA | 0 |  | C2H2
5 | 1091.5 | 588.8 | 110.7 | 120.4 | 15.3 | 873.9 | 5769.3 | 42.4 | 34.4 | 91.8 | 89.6 | 84 | 101.2 | 39.7 | 26.1 | 5930.4 | 4989.6 | 6066 | 9416.2 | 7411.3 | 10110 | 1.588 | 1.485 | 1.667 | 0.731 | 0.705 | 0.74 | 5.59 | 5.58 | 5.6 | 0.701 | 0.695 | 0.633 | 3.9 | -4.46 | 4.37 | 0.721 | 0.675 | 0.647 | 4.48 | -4.56 | 4.95 | 0.628 | 0.63 | 0.66 | 4.82 | -4.66 | -3.87 | Poor_Mixed | 4989.6 | 7411.3 | 1.485 | 0.74 | 5.6 | 0.721 | 4.95 | 0.4133 | 0.7414 | 0.4865 | 0.5407 | 1 | 0.4331 | 0.5043 | 0.5794 | 0.5794 | Poor | 0 | 1 | DGA | 0 |  | C2H2
6 | 1608.8 | 909.2 | 138.6 | 185.2 | 33.8 | 1293.7 | 8184.7 | 34.6 | 46.3 | 102.9 | 102.4 | 95.4 | 117.1 | 44.1 | 29.6 | 1021.2 | 1042.2 | 1694.4 | 1200 | 1200 | 1859.5 | 1.175 | 1.151 | 1.097 | 0.884 | 0.91 | 0.894 | -8.53 | 8.9 | 8.13 | 0.748 | 0.763 | 0.746 | 7.43 | 5.85 | 6.67 | 0.843 | 0.756 | 0.779 | -8.7 | -6.03 | 7.87 | 0.682 | 0.697 | 0.668 | 6.65 | 8.21 | 5.4 | Very Poor_Mixed | 1021.2 | 1200 | 1.097 | 0.91 | 8.9 | 0.843 | 8.7 | 0.086 | 0.6175 | 0.1656 | 0.4126 | 1 | 0.1441 | 0.3279 | 0.372 | 0.372 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
7 | 1329.5 | 835.2 | 132.2 | 180.8 | 33 | 1149.6 | 8141.8 | 34.6 | 46.4 | 107.1 | 105.7 | 91.6 | 113.4 | 44.1 | 31.3 | 2498 | 2037.3 | 1805.5 | 2954 | 2331.3 | 2043.4 | 1.183 | 1.144 | 1.132 | 0.942 | 0.967 | 0.903 | 9.28 | -8.77 | 8.66 | 0.882 | 0.83 | 0.753 | 6.09 | 7.59 | 6.36 | 0.751 | 0.856 | 0.685 | 7.67 | 6.44 | -6.71 | 0.761 | 0.806 | 0.772 | 6.38 | 7.04 | 6.27 | Very Poor_Mixed | 1805.5 | 2043.4 | 1.132 | 0.967 | 9.28 | 0.882 | 7.67 | 0.143 | 0.6166 | 0.1634 | 0.3483 | 1 | 0.0963 | 0.2886 | 0.3689 | 0.3689 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
8 | 766.1 | 487.3 | 101.3 | 108.7 | 12.7 | 684.5 | 5136.7 | 50.4 | 31.5 | 94 | 91.5 | 81 | 96 | 39.7 | 19.4 | 6971.2 | 6068.8 | 6508.6 | 11246.8 | 10258.4 | 10908.1 | 1.613 | 1.69 | 1.676 | 0.701 | 0.655 | 0.673 | 5.71 | -5.05 | -4.97 | 0.688 | 0.634 | 0.612 | 4.06 | 3.21 | 4.08 | 0.595 | 0.57 | 0.647 | -3.97 | 4.25 | 4.66 | 0.534 | 0.652 | 0.656 | 4.25 | -4.43 | 4.11 | Poor_Mixed | 6068.8 | 10258.4 | 1.613 | 0.701 | 5.71 | 0.688 | 4.66 | 0.518 | 0.7766 | 0.5052 | 0.7656 | 1 | 0.4984 | 0.5832 | 0.6462 | 0.6462 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
9 | 902.7 | 481.7 | 106.8 | 112.2 | 16.7 | 807.8 | 5887.1 | 49.8 | 32.6 | 88.9 | 86.1 | 81.3 | 93.6 | 39 | 25.3 | 5599.5 | 6927.1 | 6645.2 | 8268.5 | 11507.3 | 10966.6 | 1.477 | 1.661 | 1.65 | 0.719 | 0.731 | 0.733 | -4.96 | 5.29 | 5.06 | 0.677 | 0.635 | 0.593 | 4.69 | 5.04 | 4.91 | 0.722 | 0.708 | 0.656 | 4.8 | 3.17 | -3.85 | 0.706 | 0.607 | 0.662 | 4.14 | -4.88 | -4.53 | Poor_Mixed | 5599.5 | 8268.5 | 1.477 | 0.733 | 5.29 | 0.722 | 5.04 | 0.4484 | 0.7629 | 0.5892 | 0.569 | 1 | 0.4583 | 0.5101 | 0.607 | 0.607 | Fair | 1 | 1 | DGA | 0 |  | C2H2
10 | 420.1 | 235.1 | 74.2 | 83.1 | 4.3 | 499 | 3453.4 | 52.7 | 27.3 | 83.4 | 81.8 | 74.8 | 88.7 | 37.1 | 13.7 | 7616 | 8720.1 | 8214.6 | 12724 | 15563.4 | 14337.9 | 1.671 | 1.785 | 1.745 | 0.587 | 0.572 | 0.577 | 3.85 | 3.49 | 2.96 | 0.537 | 0.58 | 0.628 | 2.97 | 2.98 | 2.9 | 0.571 | 0.552 | 0.591 | 3.4 | 3.94 | -3.37 | 0.616 | 0.546 | 0.586 | 3.25 | 3.35 | 2.91 | Fair_Mixed | 7616 | 12724 | 1.671 | 0.587 | 3.85 | 0.628 | 3.94 | 0.7492 | 0.8337 | 0.742 | 0.9269 | 1 | 0.7163 | 0.6848 | 0.7914 | 0.7914 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
11 | 512.7 | 202.6 | 80.1 | 78.5 | 1 | 525.6 | 3482 | 29.1 | 23.5 | 83.3 | 86.1 | 75.7 | 89.4 | 37.5 | 13.3 | 1008.3 | 794.3 | 1121.3 | 1089.7 | 827.9 | 1294.9 | 1.081 | 1.042 | 1.155 | 0.702 | 0.711 | 0.764 | 5.22 | 5.63 | 6.6 | 0.517 | 0.548 | 0.535 | 2.3 | -3.23 | 2.48 | 0.559 | 0.51 | 0.5 | 2.8 | 3.15 | 3.65 | 0.506 | 0.555 | 0.535 | 2.92 | 3.27 | 2.7 | Critical_IR_PI | 794.3 | 827.9 | 1.042 | 0.764 | 6.6 | 0.559 | 3.65 | 0.8545 | 0.3136 | 0.6978 | 0.9367 | 0.925 | 0.421 | 0.814 | 0.7213 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
12 | 924.6 | 553.8 | 101.5 | 111.9 | 14.4 | 792.6 | 5501.1 | 47 | 33.4 | 93.4 | 90.5 | 83.5 | 99.1 | 39.8 | 24.8 | 6057.8 | 6469.8 | 5957.9 | 9474.9 | 9731.7 | 8623.3 | 1.564 | 1.504 | 1.447 | 0.792 | 0.75 | 0.862 | 6.68 | -5.85 | 7.04 | 0.689 | 0.653 | 0.615 | 4.29 | 5.61 | -4.27 | 0.714 | 0.691 | 0.621 | -4.11 | 5.29 | 4.7 | 0.638 | 0.659 | 0.661 | 4.59 | -3.71 | 5.69 | Poor_Mixed | 5957.9 | 8623.3 | 1.447 | 0.862 | 7.04 | 0.714 | 5.69 | 0.4643 | 0.7532 | 0.4834 | 0.5865 | 1 | 0.32 | 0.5025 | 0.5794 | 0.5794 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
13 | 1733.8 | 952.4 | 140.5 | 181 | 31.6 | 1271.9 | 7982.8 | 36.2 | 44.7 | 102.7 | 106.1 | 94.3 | 112.7 | 42.4 | 33.1 | 2988.4 | 1235.2 | 2348.2 | 3517.2 | 1429 | 2851.5 | 1.177 | 1.157 | 1.214 | 0.902 | 0.972 | 0.907 | 8.3 | -9.09 | 8.58 | 0.896 | 0.82 | 0.874 | -6.04 | 7.16 | 8.67 | 0.936 | 0.938 | 0.878 | 6.4 | 5.59 | 6.93 | 0.955 | 0.893 | 0.787 | 7.13 | 8.57 | -8.22 | Very Poor_Mixed | 1235.2 | 1429 | 1.157 | 0.972 | 9.09 | 0.955 | 8.67 | 0.0891 | 0.6328 | 0.1861 | 0.2787 | 1 | 0.1159 | 0.1825 | 0.3398 | 0.3398 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
14 | 1558.5 | 869.2 | 140.5 | 176.8 | 31.6 | 1182.3 | 8562.1 | 34.9 | 44.3 | 101.7 | 106 | 92.8 | 111.2 | 43.4 | 32.4 | 2188 | 1849.1 | 2424.8 | 2638.6 | 2123.5 | 2574.3 | 1.206 | 1.148 | 1.062 | 0.918 | 0.959 | 0.95 | -8.9 | 9.6 | 9.84 | 0.76 | 0.927 | 0.743 | 5.84 | 5.4 | -6.05 | 0.916 | 0.872 | 0.676 | -5.42 | -5.61 | 8.48 | 0.7 | 0.838 | 0.861 | 6.44 | 5.69 | 6.27 | Very Poor_Mixed | 1849.1 | 2123.5 | 1.062 | 0.959 | 9.84 | 0.927 | 8.48 | 0.1164 | 0.6367 | 0.2012 | 0.3059 | 1 | 0.0656 | 0.2909 | 0.3625 | 0.3625 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
15 | 787.3 | 523 | 104.1 | 129.9 | 15 | 834.3 | 5582.3 | 46.2 | 32.3 | 92.2 | 90.6 | 82.3 | 100.4 | 39.8 | 23.8 | 5359.8 | 6021.1 | 5537.5 | 8207.7 | 9265.6 | 8302.9 | 1.531 | 1.539 | 1.499 | 0.715 | 0.772 | 0.682 | -5.33 | 6.17 | 5.78 | 0.621 | 0.638 | 0.712 | -5 | 4.29 | 4.62 | 0.678 | 0.68 | 0.602 | 4.5 | 5 | 3.91 | 0.633 | 0.575 | 0.706 | 4.28 | 4.59 | -4.54 | Poor_Mixed | 5359.8 | 8207.7 | 1.499 | 0.772 | 6.17 | 0.712 | 5 | 0.4491 | 0.7666 | 0.4914 | 0.6212 | 1 | 0.4268 | 0.5249 | 0.5987 | 0.5987 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
16 | 1648.1 | 898.7 | 145.1 | 184.7 | 32.7 | 1344.7 | 8687.6 | 33.4 | 45.5 | 108.8 | 108.3 | 95.1 | 118.4 | 45.5 | 32.4 | 1687.9 | 1688.3 | 988.1 | 1859.6 | 1812.3 | 1200 | 1.102 | 1.073 | 1.214 | 0.988 | 0.962 | 0.905 | 9.84 | 8.54 | 7.98 | 0.755 | 0.861 | 0.94 | 9.09 | 6.07 | 8.52 | 0.765 | 0.782 | 0.914 | -7.77 | -5.33 | 7.1 | 0.903 | 0.912 | 0.761 | 6.4 | 6.35 | -7.2 | Very Poor_Mixed | 988.1 | 1200 | 1.073 | 0.988 | 9.84 | 0.94 | 9.09 | 0.0722 | 0.6251 | 0.085 | 0.3059 | 1 | 0.093 | 0.2255 | 0.3305 | 0.3305 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
17 | 824 | 506.4 | 97.3 | 106.1 | 13.9 | 828.6 | 5540.5 | 45 | 34.8 | 92.3 | 90.4 | 82.7 | 97.5 | 39.7 | 27.1 | 6140.9 | 5283.6 | 6064.8 | 9838.5 | 8415.7 | 9579.8 | 1.602 | 1.593 | 1.58 | 0.759 | 0.768 | 0.707 | -7.23 | 6.21 | 5.75 | 0.723 | 0.715 | 0.675 | 5.39 | 4.08 | -4.24 | 0.629 | 0.652 | 0.718 | -3.61 | 4.61 | 3.68 | 0.676 | 0.638 | 0.692 | 5.03 | 5.08 | -4.73 | Poor_Mixed | 5283.6 | 8415.7 | 1.58 | 0.768 | 7.23 | 0.723 | 5.39 | 0.485 | 0.7368 | 0.5047 | 0.5047 | 1 | 0.3728 | 0.4854 | 0.5849 | 0.5849 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
18 | 344.9 | 389.5 | 85.5 | 79.7 | 3.4 | 578.8 | 3774.9 | 55 | 27.4 | 86 | 85.6 | 78 | 90.7 | 38.5 | 13.9 | 8504.7 | 8060.6 | 7845.4 | 8393.7 | 14980.2 | 14201 | 0.987 | 1.858 | 1.81 | 0.962 | 0.99 | 0.917 | 9.84 | 9.53 | -9.32 | 0.537 | 0.614 | 0.618 | 3.08 | -3.15 | 3.23 | 0.525 | 0.572 | 0.572 | -2.25 | 3.64 | 3.62 | 0.577 | 0.549 | 0.579 | -2.28 | -3.28 | 3.57 | Critical_Winding_TD_Cap | 7845.4 | 8393.7 | 0.987 | 0.99 | 9.84 | 0.618 | 3.64 | 0.7356 | 0.8323 | 0.6526 | 0.9219 | 0.8187 | 0.0505 | 0.7045 | 0.66 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_HV
19 | 100 | 195.2 | 71.1 | 149.8 | 71 | 424.5 | 2985.6 | 58.8 | 22.6 | 106.2 | 103.8 | 96 | 118.3 | 44.2 | 15.4 | 7781.7 | 7233.1 | 6775.1 | 13089.9 | 12566.5 | 11856.4 | 1.682 | 1.737 | 1.75 | 0.584 | 0.536 | 0.582 | -3.39 | -2.91 | 3.04 | 0.579 | 0.533 | 0.566 | 3.21 | -3.43 | 2.89 | 0.628 | 0.576 | 0.557 | 2.97 | -4.18 | 4.14 | 0.609 | 0.594 | 0.56 | 3.73 | 3.18 | -3.45 | Critical_Thermal | 6775.1 | 11856.4 | 1.682 | 0.584 | 3.39 | 0.628 | 4.18 | 0.5307 | 0.915 | 0.1292 | 0.8828 | 1 | 0.7549 | 0.6754 | 0.6868 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
20 | 286.2 | 169.5 | 74.4 | 63.1 | 1 | 487.8 | 3019.6 | 56.1 | 22.3 | 82.2 | 84.9 | 75.9 | 87.5 | 37.5 | 19.9 | 1033.2 | 1420.4 | 690 | 1056.1 | 1568.7 | 703.8 | 1.022 | 1.104 | 1.02 | 0.709 | 0.724 | 2.046 | -5.21 | 5.53 | 5.27 | 0.566 | 0.5 | 0.537 | 3.05 | -2.25 | 2.49 | 0.55 | 0.562 | 0.566 | -2.7 | 2.06 | -2.92 | 0.581 | 0.531 | 0.521 | 2.17 | 2.11 | -2.1 | Critical_IR_PI | 690 | 703.8 | 1.02 | 2.046 | 5.53 | 0.581 | 3.05 | 0.9119 | 0.9215 | 0.7231 | 0.7499 | 0.925 | 0.3846 | 0.7976 | 0.7938 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_TV_TanDelta_pct
21 | 1667.6 | 819.8 | 138.6 | 173.2 | 33.6 | 1277.5 | 8283.7 | 35.7 | 44.3 | 102.3 | 103.7 | 92.9 | 112.3 | 43.4 | 31.7 | 1554.1 | 831 | 2958.7 | 1641.1 | 1200 | 3428.5 | 1.056 | 1.444 | 1.159 | 0.91 | 0.946 | 0.936 | 8.24 | -9.18 | 9.65 | 0.95 | 0.78 | 0.752 | 8.73 | 7.02 | 9.48 | 0.831 | 0.828 | 0.781 | 7.76 | 8.31 | 8.11 | 0.863 | 0.874 | 0.927 | -5.56 | 7.61 | -8.08 | Very Poor_Mixed | 831 | 1200 | 1.056 | 0.946 | 9.65 | 0.95 | 9.48 | 0.1029 | 0.6367 | 0.2046 | 0.3329 | 1 | 0.0948 | 0.2006 | 0.3486 | 0.3486 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
22 | 273.2 | 250.9 | 75.3 | 76.8 | 1.1 | 536.9 | 4193.5 | 55.4 | 71.7 | 85.6 | 83.6 | 77 | 87.4 | 37.9 | 16.6 | 690 | 690 | 690 | 730.9 | 735.5 | 752.5 | 1.059 | 1.066 | 1.091 | 0.728 | 0.702 | 0.733 | -5.89 | 5.38 | -5.68 | 0.558 | 0.538 | 0.5 | 2.86 | 3.16 | -3.05 | 0.529 | 0.54 | 0.575 | 2.89 | 2.37 | 3.54 | 0.536 | 0.538 | 0.559 | -3.02 | 3.55 | 2.65 | Critical_IR_PI | 690 | 730.9 | 1.059 | 0.733 | 5.89 | 0.575 | 3.55 | 0.8451 | 0.5833 | 0.6973 | 0.8493 | 0.775 | 0.4337 | 0.7765 | 0.718 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
23 | 340.2 | 174.1 | 70.3 | 64 | 2 | 464.5 | 3324.1 | 34.3 | 46.6 | 79 | 76.5 | 71.8 | 88 | 36.3 | 14.3 | 5799.6 | 5102.9 | 5416.2 | 8386.4 | 7615.1 | 5347.5 | 1.446 | 1.492 | 0.987 | 0.647 | 0.772 | 0.646 | 5.21 | 4.99 | -4.28 | 0.534 | 0.605 | 0.5 | 2.48 | 2.63 | 3 | 0.5 | 0.51 | 0.531 | 2.46 | 3 | -2.82 | 0.556 | 0.546 | 0.519 | 2.83 | -3 | 2.31 | Critical_Oil | 5102.9 | 5347.5 | 0.987 | 0.772 | 5.21 | 0.605 | 3 | 0.8436 | 0.6147 | 0.8609 | 0.9118 | 0.8125 | 0.5136 | 0.8227 | 0.7663 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
24 | 904.9 | 529.1 | 104.1 | 113 | 20.9 | 945.6 | 5394.6 | 59.5 | 20.8 | 76.1 | 77 | 71.3 | 81.7 | 35 | 12.6 | 8258.3 | 9620.6 | 8717.9 | 15611.8 | 18133 | 16969.8 | 1.89 | 1.885 | 1.947 | 0.502 | 0.559 | 0.57 | -2.01 | 2.97 | 2.27 | 0.5 | 0.504 | 0.549 | 2.13 | 2.73 | 2.4 | 0.535 | 0.538 | 0.54 | 3.12 | -2.47 | 3.1 | 0.548 | 0.515 | 0.535 | 2.01 | 2.8 | 2 | Poor_DGA | 8258.3 | 15611.8 | 1.885 | 0.57 | 2.97 | 0.549 | 3.12 | 0.407 | 0.9605 | 0.9274 | 0.953 | 1 | 0.8541 | 0.834 | 0.7871 | 0.7871 | Fair | 1 | 1 | DGA | 0 |  | C2H2
25 | 519.2 | 368 | 92.1 | 87 | 12.6 | 537.2 | 4559.4 | 55.4 | 25.5 | 79 | 79.8 | 74.4 | 84.2 | 36.4 | 15.1 | 7844.1 | 8379.4 | 8191.2 | 13838.6 | 15885.8 | 14874.9 | 1.764 | 1.896 | 1.816 | 0.654 | 0.585 | 0.592 | -4.57 | 3.53 | 3.6 | 0.6 | 0.599 | 0.612 | -3.54 | -3.72 | 3.19 | 0.582 | 0.542 | 0.608 | 2.81 | 3.19 | -3.43 | 0.615 | 0.592 | 0.547 | 2.76 | 2.81 | 3.32 | Fair_Mixed | 7844.1 | 13838.6 | 1.764 | 0.654 | 4.57 | 0.615 | 3.72 | 0.6088 | 0.8617 | 0.8246 | 0.8908 | 1 | 0.6493 | 0.6679 | 0.7537 | 0.7537 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
26 | 584.6 | 361.4 | 81.3 | 81.3 | 3.8 | 610.3 | 4593.5 | 55.6 | 23.4 | 75.9 | 75 | 70.8 | 82.4 | 35.2 | 10.8 | 10000 | 9203.1 | 8592.7 | 19238.7 | 17139 | 16244.2 | 1.924 | 1.862 | 1.89 | 0.765 | 0.757 | 0.744 | -5.23 | 5.85 | 6.05 | 0.533 | 0.508 | 0.553 | 2.49 | -2.07 | 2.08 | 0.569 | 0.565 | 0.506 | 2.19 | 2 | 2.12 | 0.565 | 0.52 | 0.523 | -2.52 | -3.07 | 2.22 | Poor_Winding_TD_Cap | 8592.7 | 16244.2 | 1.862 | 0.765 | 6.05 | 0.569 | 3.07 | 0.7 | 0.8988 | 0.9604 | 0.9892 | 1 | 0.4006 | 0.8205 | 0.7921 | 0.7921 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
27 | 287.3 | 287.2 | 83.9 | 75.3 | 3.2 | 439.5 | 3323.7 | 56.2 | 22.6 | 81.8 | 80 | 76.7 | 88.5 | 37.3 | 11.8 | 9076.4 | 8850.2 | 9384.6 | 16710.3 | 16807.8 | 18548.6 | 1.841 | 1.899 | 1.976 | 0.792 | 0.776 | 0.752 | -7.21 | 5.8 | 6.22 | 0.5 | 0.5 | 0.544 | 2.87 | -2.27 | 2.47 | 0.506 | 0.555 | 0.508 | 2.26 | -2.93 | -2.41 | 0.552 | 0.506 | 0.537 | -3.17 | 2.77 | 3.01 | Poor_Winding_TD_Cap | 8850.2 | 16710.3 | 1.841 | 0.792 | 7.21 | 0.555 | 3.17 | 0.7882 | 0.915 | 0.7554 | 0.9703 | 1 | 0.3477 | 0.8527 | 0.7931 | 0.7931 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
28 | 226.5 | 160.2 | 72.8 | 65 | 1.6 | 520.5 | 2943.2 | 55.5 | 25 | 78.8 | 85.5 | 75.3 | 88.8 | 35.7 | 13.1 | 8814.9 | 8957.7 | 9675.4 | 16873.7 | 17156.9 | 18648 | 1.914 | 1.915 | 1.927 | 0.755 | 0.84 | 0.813 | 7.01 | 7.53 | 6.94 | 0.522 | 0.577 | 0.514 | 2.99 | 2.2 | 2.92 | 0.525 | 0.593 | 0.557 | 4.15 | -2.9 | 2 | 0.58 | 0.589 | 0.616 | 3.06 | -3.1 | 2.72 | Poor_Winding_TD_Cap | 8814.9 | 16873.7 | 1.914 | 0.84 | 7.53 | 0.616 | 4.15 | 0.8605 | 0.87 | 0.7549 | 0.9414 | 1 | 0.2845 | 0.735 | 0.7742 | 0.7742 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
29 | 1600.9 | 813.7 | 140.1 | 164.8 | 32.9 | 1247.5 | 7830.2 | 36.8 | 42 | 101.9 | 103.3 | 89.8 | 114.1 | 43.2 | 30.7 | 2565.7 | 2389.9 | 788.6 | 3211.1 | 2904 | 1200 | 1.252 | 1.215 | 1.522 | 0.898 | 0.867 | 0.902 | 8.09 | 8.21 | -8.12 | 0.73 | 0.846 | 0.798 | 7.17 | -6.94 | 8.35 | 0.775 | 0.813 | 0.811 | -7.84 | 8.76 | 6.3 | 0.711 | 0.913 | 0.787 | 8.45 | -7.44 | 7.28 | Very Poor_Mixed | 788.6 | 1200 | 1.215 | 0.902 | 8.21 | 0.913 | 8.76 | 0.1265 | 0.6594 | 0.2192 | 0.3711 | 1 | 0.1685 | 0.2498 | 0.3798 | 0.3798 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
30 | 968.6 | 505.1 | 96.9 | 116.2 | 16.7 | 824.4 | 5635.3 | 43.1 | 36.4 | 88.4 | 90.5 | 82 | 98.1 | 39.4 | 25.6 | 6215.2 | 5049.7 | 6209.6 | 9886.6 | 7959.6 | 9636.4 | 1.591 | 1.576 | 1.552 | 0.727 | 0.714 | 0.724 | 5.26 | -5.47 | 5.96 | 0.703 | 0.61 | 0.689 | 5.29 | -4.43 | 5.56 | 0.664 | 0.759 | 0.714 | 3.99 | 5.14 | 4.82 | 0.695 | 0.691 | 0.669 | -5.68 | 4.72 | 5.24 | Poor_Mixed | 5049.7 | 7959.6 | 1.552 | 0.727 | 5.96 | 0.759 | 5.68 | 0.4444 | 0.7186 | 0.5331 | 0.5584 | 1 | 0.4378 | 0.4572 | 0.5821 | 0.5821 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
31 | 265.8 | 148.1 | 75.1 | 76.6 | 1.6 | 382.9 | 2967.7 | 58.8 | 20.8 | 79.9 | 85.9 | 75.7 | 89.3 | 37.6 | 10.8 | 10000 | 10000 | 9874.9 | 18982.5 | 20000 | 19749.8 | 1.898 | 2 | 2 | 0.5 | 0.509 | 0.511 | 2.25 | 2 | 2.19 | 0.54 | 0.5 | 0.571 | 2.11 | 2 | -2.53 | 0.541 | 0.577 | 0.552 | 2 | 2.72 | 3.02 | 0.546 | 0.5 | 0.523 | 2.69 | 2.55 | 2.13 | Fair_Thermal | 9874.9 | 18982.5 | 1.898 | 0.511 | 2.25 | 0.577 | 3.02 | 0.8653 | 0.9605 | 0.7269 | 0.9892 | 1 | 0.9513 | 0.8229 | 0.895 | 0.895 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
32 | 252.8 | 158 | 67.5 | 147.6 | 2.5 | 425.8 | 3215.7 | 50.7 | 27.5 | 109.3 | 107.6 | 96.5 | 117.9 | 45.2 | 12.2 | 5667.5 | 396 | 6910.2 | 8892.8 | 617.7 | 11976 | 1.569 | 1.56 | 1.733 | 0.578 | 0.662 | 0.632 | 2.74 | 4.52 | 3.62 | 0.5 | 0.519 | 0.542 | -2 | -2 | 3.24 | 0.561 | 0.552 | 0.573 | -2.34 | 2.12 | -2 | 0.509 | 0.565 | 0.557 | 2.95 | 3.16 | -2 | Critical_Thermal | 396 | 617.7 | 1.56 | 0.662 | 4.52 | 0.573 | 3.24 | 0.7609 | 0.8308 | 0.0832 | 0.9618 | 0.85 | 0.6521 | 0.8114 | 0.7197 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H4
33 | 875.7 | 525.5 | 109.6 | 109.1 | 18.8 | 826.3 | 5927.9 | 56.8 | 23.2 | 75.8 | 75.8 | 71.7 | 80 | 35.7 | 16.5 | 9285.1 | 9112.8 | 10000 | 17554 | 17998.3 | 20000 | 1.891 | 1.975 | 2 | 0.533 | 0.585 | 0.595 | -2.57 | 2.89 | 3.53 | 0.589 | 0.577 | 0.521 | 2.85 | 2.76 | 2 | 0.501 | 0.559 | 0.536 | -2 | 2.23 | -2.35 | 0.521 | 0.503 | 0.523 | -2.99 | 2.29 | -3.24 | Poor_DGA | 9112.8 | 17554 | 1.891 | 0.595 | 3.53 | 0.589 | 3.24 | 0.4308 | 0.9027 | 0.948 | 0.8522 | 1 | 0.7592 | 0.8197 | 0.7672 | 0.7672 | Fair | 1 | 1 | DGA | 0 |  | C2H2
34 | 952.2 | 451.5 | 97.3 | 112.3 | 18.5 | 772.5 | 4937.5 | 44.6 | 31.7 | 89.7 | 90.4 | 82.2 | 97.4 | 40.1 | 24 | 4708.5 | 6876 | 5821.4 | 6986.3 | 11266.5 | 9319 | 1.484 | 1.639 | 1.601 | 0.743 | 0.741 | 0.729 | 5.65 | 6.19 | -5.6 | 0.614 | 0.619 | 0.67 | 4.94 | 4.43 | 4.17 | 0.692 | 0.775 | 0.675 | -3.3 | 4.26 | 3.8 | 0.695 | 0.695 | 0.741 | 4.59 | 4.32 | 4.3 | Poor_Mixed | 4708.5 | 6986.3 | 1.484 | 0.743 | 6.19 | 0.775 | 4.94 | 0.4576 | 0.7741 | 0.5227 | 0.6143 | 1 | 0.4099 | 0.4891 | 0.5957 | 0.5957 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
35 | 1527.8 | 913.2 | 139.7 | 183.4 | 31.9 | 1165.2 | 8190.4 | 36.6 | 41.8 | 105.6 | 105.4 | 96 | 113.3 | 43.5 | 31.7 | 2563.1 | 1838 | 1943.1 | 3219.1 | 2280.3 | 2229.7 | 1.256 | 1.241 | 1.147 | 0.894 | 0.913 | 0.878 | -7.52 | 7.96 | 7.56 | 0.86 | 0.763 | 0.884 | 5.68 | 5.54 | 6.3 | 0.823 | 0.867 | 0.735 | -7.82 | 8.39 | 7.49 | 0.747 | 0.888 | 0.875 | -8.18 | 8.79 | -7.75 | Very Poor_Mixed | 1838 | 2229.7 | 1.147 | 0.913 | 7.96 | 0.888 | 8.79 | 0.1145 | 0.6614 | 0.1536 | 0.3329 | 1 | 0.188 | 0.2324 | 0.3681 | 0.3681 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
36 | 1425 | 833.4 | 126 | 163.1 | 33.6 | 1113.1 | 7460.5 | 36 | 46.7 | 103.5 | 105.1 | 93.1 | 112.1 | 43.8 | 32.2 | 2670.1 | 3562.5 | 1811.5 | 3270.2 | 4846.4 | 2171.8 | 1.225 | 1.36 | 1.199 | 0.956 | 0.903 | 0.855 | 9.14 | -8.47 | -7.75 | 0.729 | 0.868 | 0.895 | 7.95 | 6.21 | 6.49 | 0.852 | 0.706 | 0.706 | 6.87 | 5.86 | 7.99 | 0.87 | 0.844 | 0.786 | 7.65 | 7.54 | 6.36 | Very Poor_Mixed | 1811.5 | 2171.8 | 1.199 | 0.956 | 9.14 | 0.895 | 7.99 | 0.1661 | 0.6137 | 0.1869 | 0.3137 | 1 | 0.1421 | 0.264 | 0.377 | 0.377 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
37 | 882.5 | 475.6 | 110.8 | 123.4 | 18.9 | 761.8 | 5753.7 | 45.8 | 32.5 | 91.7 | 88.4 | 83.5 | 98.6 | 39.9 | 24.5 | 4707.8 | 5594.4 | 5213.2 | 6653.6 | 8469 | 8255.5 | 1.413 | 1.514 | 1.584 | 0.702 | 0.755 | 0.751 | 5.15 | -6.01 | 5.14 | 0.655 | 0.669 | 0.691 | 3.52 | 6.15 | -6.24 | 0.647 | 0.671 | 0.573 | 5.32 | 6.41 | 5.33 | 0.67 | 0.661 | 0.614 | 5.68 | -5.78 | 3.83 | Poor_Mixed | 4707.8 | 6653.6 | 1.413 | 0.755 | 6.01 | 0.691 | 6.41 | 0.4304 | 0.7641 | 0.5101 | 0.597 | 1 | 0.433 | 0.4928 | 0.5895 | 0.5895 | Poor | 0 | 1 | DGA | 0 |  | C2H2
38 | 100 | 120 | 69.9 | 65.8 | 3.4 | 367.9 | 2651.3 | 56.9 | 22.6 | 75 | 75.6 | 71.6 | 80 | 35 | 13.7 | 9035.5 | 9038 | 9371.9 | 17287.4 | 17759 | 18743.8 | 1.913 | 1.965 | 2 | 0.532 | 0.513 | 0.5 | -2.19 | 2.04 | -2.37 | 0.535 | 0.51 | 0.567 | 2 | 2 | 2.84 | 0.515 | 0.514 | 0.56 | 2.62 | 2.02 | 2.56 | 0.5 | 0.537 | 0.583 | -2.55 | -2 | 2.32 | Good_Mixed | 9035.5 | 17287.4 | 1.913 | 0.532 | 2.37 | 0.583 | 2.84 | 0.8653 | 0.915 | 0.969 | 0.9269 | 1 | 0.9262 | 0.8327 | 0.9089 | 0.9089 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
39 | 274.8 | 305.3 | 81.8 | 74 | 3.7 | 589.4 | 3750.8 | 32.4 | 82.5 | 84.3 | 87.5 | 81.3 | 92.9 | 38.8 | 13.8 | 6082.2 | 5470.8 | 4933.7 | 9148 | 8040.5 | 7522.1 | 1.504 | 1.47 | 1.525 | 0.69 | 0.63 | 0.642 | -5.76 | 3.47 | -3.93 | 0.554 | 0.636 | 0.656 | -4.04 | 2.42 | 3.42 | 0.584 | 0.566 | 0.556 | 3.64 | 4.35 | 3.84 | 0.563 | 0.626 | 0.606 | 3.56 | -2.65 | 3.83 | Critical_Oil | 4933.7 | 7522.1 | 1.47 | 0.69 | 5.76 | 0.656 | 4.35 | 0.7548 | 0.5833 | 0.6167 | 0.9244 | 1 | 0.5722 | 0.647 | 0.7232 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
40 | 284.2 | 201.1 | 71.2 | 106 | 1 | 457.8 | 3227.9 | 59.4 | 21.1 | 92.7 | 88.3 | 83.2 | 98.2 | 39.4 | 14.8 | 8822 | 8435.9 | 8926.8 | 16827.3 | 15839.8 | 16329.5 | 1.907 | 1.878 | 1.829 | 0.538 | 0.573 | 0.592 | -2 | 2.62 | 3.31 | 0.508 | 0.537 | 0.5 | 2.57 | 2 | 2.47 | 0.5 | 0.551 | 0.509 | 2.32 | 2.09 | 2 | 0.541 | 0.533 | 0.54 | -2.1 | 2.78 | 2 | Poor_Thermal | 8435.9 | 15839.8 | 1.829 | 0.592 | 3.31 | 0.551 | 2.78 | 0.863 | 0.9514 | 0.5114 | 0.8988 | 1 | 0.7901 | 0.8691 | 0.8531 | 0.8531 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
41 | 875.9 | 502.7 | 110.9 | 117.9 | 16.7 | 845 | 6060.3 | 44.6 | 36.2 | 88.7 | 89.1 | 81.5 | 96.4 | 39.9 | 26.9 | 5988.1 | 6186.6 | 5653.3 | 9034.6 | 9717.9 | 9137.9 | 1.509 | 1.571 | 1.616 | 0.765 | 0.711 | 0.704 | 6.15 | 5.45 | 4.88 | 0.697 | 0.598 | 0.746 | -4.9 | 5.09 | -6.37 | 0.708 | 0.665 | 0.746 | 4.41 | 5.72 | 4.09 | 0.654 | 0.632 | 0.63 | 5.55 | 3.88 | -4.5 | Poor_Mixed | 5653.3 | 9034.6 | 1.509 | 0.765 | 6.15 | 0.746 | 6.37 | 0.433 | 0.7208 | 0.5489 | 0.512 | 1 | 0.4381 | 0.4768 | 0.5824 | 0.5824 | Poor | 0 | 1 | DGA | 0 |  | C2H2
42 | 356.6 | 207.2 | 79.7 | 69.7 | 2.4 | 419.8 | 3463.4 | 25.7 | 25.9 | 86.4 | 88 | 77.3 | 91.3 | 38.5 | 15.8 | 8114.8 | 8397.8 | 8196.4 | 14470.3 | 15345.5 | 15016.4 | 1.783 | 1.827 | 1.832 | 0.572 | 0.615 | 0.589 | 3.62 | 3.92 | -3.21 | 0.552 | 0.546 | 0.963 | 3.32 | 2.38 | 9.33 | 0.595 | 0.554 | 0.525 | -3.02 | 3.35 | -3.88 | 0.609 | 0.523 | 0.591 | -2.95 | 2.02 | 4.13 | Critical_Bushing_TD_Cap | 8114.8 | 14470.3 | 1.783 | 0.615 | 3.92 | 0.963 | 9.33 | 0.8208 | 0.2719 | 0.6348 | 0.8718 | 1 | 0.6899 | 0.6499 | 0.7185 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
43 | 975.5 | 495.4 | 100.9 | 110 | 16.5 | 781 | 5409.2 | 56.7 | 22.5 | 75 | 75.5 | 72.1 | 80 | 35 | 14.3 | 9690.6 | 9467.9 | 9703.1 | 19381.3 | 17928.9 | 18745.4 | 2 | 1.894 | 1.932 | 0.557 | 0.538 | 0.535 | 2.84 | 2.01 | 2.85 | 0.501 | 0.5 | 0.565 | 2.6 | 2.75 | -2.99 | 0.526 | 0.545 | 0.512 | -2.4 | 2.56 | -2.56 | 0.5 | 0.51 | 0.591 | 3 | 2 | 3.08 | Fair_DGA | 9467.9 | 17928.9 | 1.894 | 0.557 | 2.85 | 0.591 | 3.08 | 0.4574 | 0.9171 | 0.9658 | 0.9118 | 1 | 0.8309 | 0.8471 | 0.7954 | 0.7954 | Fair | 1 | 1 | DGA | 0 |  | C2H2
44 | 923.6 | 544.7 | 108.2 | 133.3 | 16.3 | 946.6 | 6079.2 | 42.9 | 36.3 | 95 | 91.1 | 83.1 | 102.4 | 39.1 | 25.4 | 5904.1 | 5495.1 | 4292.4 | 9393.1 | 8193.6 | 6321.4 | 1.591 | 1.491 | 1.473 | 0.761 | 0.794 | 0.779 | 6.57 | 6.39 | 6.97 | 0.689 | 0.727 | 0.611 | 4.19 | -4.29 | 4.1 | 0.744 | 0.578 | 0.668 | -5.15 | 5.68 | 4.31 | 0.735 | 0.625 | 0.674 | 5.71 | -4.13 | 5.4 | Poor_Mixed | 4292.4 | 6321.4 | 1.473 | 0.794 | 6.97 | 0.744 | 5.71 | 0.4019 | 0.7197 | 0.4599 | 0.5655 | 1 | 0.3311 | 0.4878 | 0.5553 | 0.5553 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
45 | 1689.2 | 940.5 | 148.3 | 194.2 | 34.3 | 1344.7 | 8421.3 | 55.8 | 54 | 80 | 77.9 | 73.8 | 84.7 | 35.6 | 14.3 | 8617.1 | 9270.1 | 8421.2 | 16085.2 | 17673.1 | 15375.7 | 1.867 | 1.906 | 1.826 | 0.635 | 0.624 | 0.588 | -3.45 | 3.93 | 3.56 | 0.526 | 0.558 | 0.562 | 2.64 | -3.01 | 3.68 | 0.569 | 0.542 | 0.545 | -2.8 | 2.8 | -3.04 | 0.572 | 0.557 | 0.527 | 2.77 | 2.73 | 3.32 | Critical_DGA | 8421.2 | 15375.7 | 1.826 | 0.635 | 3.93 | 0.572 | 3.68 | 0.051 | 0.5833 | 0.8394 | 0.9118 | 1 | 0.6573 | 0.7482 | 0.599 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
46 | 112.7 | 164.9 | 72.5 | 50 | 4.2 | 350 | 2546 | 58.9 | 21.3 | 75 | 76.7 | 70 | 81 | 35.2 | 15.4 | 9613.5 | 10000 | 10000 | 18991.6 | 19698.2 | 19845.5 | 1.976 | 1.97 | 1.985 | 0.563 | 0.596 | 0.58 | 2.76 | -2.62 | -2.88 | 0.543 | 0.5 | 0.525 | 2.49 | 2.14 | 2.42 | 0.526 | 0.564 | 0.62 | 2.01 | 2.15 | -3.14 | 0.5 | 0.565 | 0.505 | -2.68 | -2.82 | 3.36 | Good_Mixed | 9613.5 | 18991.6 | 1.97 | 0.596 | 2.88 | 0.62 | 3.36 | 0.8777 | 0.9458 | 0.9686 | 0.8828 | 1 | 0.7604 | 0.8228 | 0.8885 | 0.8885 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
47 | 1256.4 | 705.4 | 129.7 | 159.6 | 27.3 | 1139 | 6744.4 | 39.9 | 41 | 98.3 | 99.9 | 91.3 | 108.8 | 42.5 | 32.1 | 3782.5 | 3083.5 | 3610.9 | 4987.4 | 3871.2 | 4503.1 | 1.319 | 1.255 | 1.247 | 0.817 | 0.805 | 2.382 | 6.97 | 8.56 | 8.1 | 0.751 | 0.792 | 0.824 | -4.97 | -4.13 | 5.03 | 0.686 | 0.66 | 0.73 | -6.32 | 7.58 | -6.96 | 0.723 | 0.799 | 0.794 | 6.12 | 5.19 | 7.03 | Critical_Mixed | 3083.5 | 3871.2 | 1.247 | 2.382 | 8.56 | 0.824 | 7.58 | 0.2274 | 0.6696 | 0.2825 | 0.3175 | 1 | 0.1959 | 0.3549 | 0.4326 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
48 | 1578.7 | 900.3 | 140 | 185.2 | 27.3 | 1214.6 | 7714.6 | 33.6 | 43.7 | 106.2 | 107.5 | 93.1 | 115.5 | 44.2 | 31.7 | 1477.4 | 747.8 | 690 | 1633.6 | 1200 | 1200 | 1.106 | 1.605 | 1.739 | 0.967 | 0.958 | 0.925 | 9.56 | 9.12 | -8.38 | 0.779 | 0.868 | 0.856 | 8.2 | 7.75 | 6.24 | 0.7 | 0.964 | 0.699 | 8.32 | -7.86 | 7.15 | 0.805 | 0.857 | 0.79 | -5.81 | -7.51 | 5.06 | Very Poor_Mixed | 690 | 1200 | 1.106 | 0.967 | 9.56 | 0.964 | 8.32 | 0.1326 | 0.6425 | 0.1388 | 0.3329 | 1 | 0.0819 | 0.2549 | 0.3581 | 0.3581 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
49 | 730.4 | 483.1 | 94 | 102.3 | 18.6 | 699.1 | 5263.2 | 57.3 | 21.8 | 75 | 75.3 | 72.3 | 81 | 35.2 | 13 | 8313 | 9371.2 | 8732.7 | 15191.5 | 18485.4 | 16973.3 | 1.827 | 1.973 | 1.944 | 0.553 | 0.512 | 0.627 | -2.69 | 2.33 | -3.61 | 0.54 | 0.571 | 0.564 | -3.35 | 2.64 | 2.8 | 0.568 | 0.551 | 0.571 | -4.01 | 3.2 | 2.25 | 0.563 | 0.612 | 0.566 | 2.77 | -2.18 | 3.3 | Poor_DGA | 8313 | 15191.5 | 1.827 | 0.627 | 3.61 | 0.612 | 4.01 | 0.4899 | 0.9331 | 0.9618 | 0.9438 | 1 | 0.7868 | 0.7169 | 0.777 | 0.777 | Fair | 1 | 1 | DGA | 0 |  | C2H2
50 | 850.4 | 487.3 | 100.9 | 129 | 12.8 | 835 | 5296 | 44.6 | 34.5 | 90.9 | 93.7 | 81.2 | 97.6 | 40.1 | 25.6 | 5812.1 | 5989.8 | 4234.4 | 8812.4 | 9182 | 6062.1 | 1.516 | 1.533 | 1.432 | 0.736 | 0.671 | 0.741 | -5.59 | 4.45 | 6.21 | 0.722 | 0.713 | 0.622 | -5.89 | 4.31 | -4.23 | 0.684 | 0.637 | 0.742 | 4.27 | -5.08 | 4.17 | 0.729 | 0.765 | 0.724 | 5.5 | 5.46 | 4.04 | Poor_Mixed | 4234.4 | 6062.1 | 1.432 | 0.741 | 6.21 | 0.765 | 5.89 | 0.47 | 0.7403 | 0.4991 | 0.5584 | 1 | 0.4525 | 0.4472 | 0.588 | 0.588 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
51 | 615.4 | 370 | 85.9 | 91.6 | 13 | 734.9 | 4539.9 | 47.6 | 29.3 | 85.6 | 86.7 | 79.1 | 91.5 | 40.4 | 20.5 | 5091.2 | 7385.7 | 7416.7 | 7129.9 | 12713.6 | 12515 | 1.4 | 1.721 | 1.687 | 0.686 | 0.618 | 0.686 | 4.45 | -3.99 | -4.8 | 0.591 | 0.565 | 0.575 | 4.81 | 3.87 | -3.36 | 0.547 | 0.608 | 0.629 | 4.06 | 4.23 | 3.98 | 0.616 | 0.616 | 0.606 | 4.15 | 4.04 | 3.1 | Fair_Mixed | 5091.2 | 7129.9 | 1.4 | 0.686 | 4.8 | 0.629 | 4.81 | 0.5691 | 0.8054 | 0.6242 | 0.7308 | 1 | 0.5602 | 0.6257 | 0.6889 | 0.6889 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
52 | 328.4 | 260.3 | 80.6 | 70.3 | 4.5 | 526.7 | 3209 | 54.9 | 25.6 | 87.3 | 83.9 | 78.4 | 93.5 | 38.1 | 20.1 | 7011.9 | 8217.2 | 8976.6 | 11843.9 | 14504.2 | 16752.5 | 1.689 | 1.765 | 1.866 | 0.625 | 0.624 | 0.621 | -3.86 | -3.97 | 3.87 | 0.63 | 0.561 | 0.62 | 2.48 | -3.55 | 3.09 | 0.572 | 0.612 | 0.625 | 3.48 | -3.89 | 4.04 | 0.567 | 0.548 | 0.575 | 2.29 | 2.27 | 3.39 | Fair_Mixed | 7011.9 | 11843.9 | 1.689 | 0.625 | 3.97 | 0.63 | 4.04 | 0.7609 | 0.86 | 0.6416 | 0.7436 | 1 | 0.6319 | 0.6688 | 0.7636 | 0.7636 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
53 | 486.9 | 323 | 88.4 | 90.1 | 10.3 | 574.3 | 3518.3 | 47.4 | 31.1 | 84.9 | 87.4 | 78.5 | 94.2 | 39.2 | 18 | 6651.3 | 6944.3 | 5932.1 | 10863.5 | 11990.5 | 9484.9 | 1.633 | 1.727 | 1.599 | 0.645 | 0.672 | 0.609 | 4.25 | -4.14 | 4.34 | 0.569 | 0.652 | 0.605 | -3.78 | 2.58 | 3.15 | 0.59 | 0.577 | 0.623 | 4 | 5.29 | 3.53 | 0.596 | 0.591 | 0.558 | 3.58 | -3.59 | 3.37 | Fair_Mixed | 5932.1 | 9484.9 | 1.599 | 0.672 | 4.34 | 0.652 | 5.29 | 0.6376 | 0.7817 | 0.6226 | 0.8084 | 1 | 0.5918 | 0.637 | 0.7134 | 0.7134 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
54 | 284.2 | 235 | 67.9 | 59.5 | 1 | 350 | 2897.3 | 54.1 | 25.3 | 76.6 | 77.1 | 70 | 82.7 | 35 | 13.4 | 4903.1 | 5584.5 | 4271.6 | 7006.7 | 8476.1 | 5959.1 | 1.429 | 1.518 | 1.395 | 0.59 | 0.571 | 0.585 | 4.31 | 3.7 | 3.73 | 0.526 | 0.548 | 0.602 | 2.49 | 2.42 | -3.09 | 0.552 | 0.569 | 0.5 | 3.1 | -2.32 | -2.25 | 0.5 | 0.544 | 0.504 | 2.33 | 2 | -2.23 | Poor_IR_PI | 4271.6 | 5959.1 | 1.395 | 0.59 | 4.31 | 0.602 | 3.1 | 0.9414 | 0.865 | 0.9315 | 0.9342 | 1 | 0.6817 | 0.8269 | 0.8833 | 0.8833 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
55 | 100 | 229 | 70.1 | 58.2 | 1 | 350 | 2500 | 56.1 | 22.7 | 75.9 | 76.3 | 73.3 | 80.5 | 35.2 | 13.7 | 9143.4 | 9265.3 | 9677.8 | 17499.9 | 17361.6 | 18968.8 | 1.914 | 1.874 | 1.96 | 0.506 | 0.511 | 0.544 | -2 | 2.53 | 2.74 | 0.562 | 0.512 | 0.515 | 2.3 | -2.11 | 2 | 0.525 | 0.504 | 0.515 | 2.5 | 2.17 | -2.6 | 0.52 | 0.525 | 0.553 | 2.29 | -2.52 | 2.08 | Good_Mixed | 9143.4 | 17361.6 | 1.874 | 0.544 | 2.74 | 0.562 | 2.6 | 0.9658 | 0.9129 | 0.9255 | 0.9269 | 1 | 0.8919 | 0.8517 | 0.9281 | 0.9281 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
56 | 569.5 | 394.6 | 94.1 | 84.8 | 14.1 | 657.5 | 4534.3 | 50 | 29.9 | 84.5 | 85.6 | 76.6 | 90.1 | 38.7 | 23.8 | 6234.9 | 7636.2 | 7132.8 | 10173.3 | 13545 | 11808.6 | 1.632 | 1.774 | 1.656 | 0.646 | 0.635 | 0.679 | 4.16 | 4.39 | 4.75 | 0.635 | 0.61 | 0.62 | 3.78 | 3.72 | 3.26 | 0.576 | 0.602 | 0.635 | 3.84 | 3.87 | -4.23 | 0.6 | 0.646 | 0.649 | 4.11 | 3.56 | -4.76 | Fair_Mixed | 6234.9 | 10173.3 | 1.632 | 0.679 | 4.75 | 0.649 | 4.76 | 0.5746 | 0.7973 | 0.6752 | 0.6212 | 1 | 0.5682 | 0.5886 | 0.6834 | 0.6834 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
57 | 1466.6 | 800.7 | 134.7 | 175.5 | 30.5 | 1199.8 | 7803 | 35.8 | 45.3 | 104.7 | 102.7 | 92 | 113.5 | 44.6 | 31.2 | 2859.6 | 2482 | 2559.5 | 3518.8 | 3268.5 | 3106 | 1.231 | 1.317 | 1.214 | 0.924 | 0.952 | 0.906 | -9.52 | 9.42 | 8.28 | 0.72 | 0.858 | 0.941 | 7.32 | 8.76 | 8.29 | 0.857 | 0.908 | 0.726 | -5.44 | 7.46 | 7.3 | 0.85 | 0.795 | 0.804 | 5.91 | 9.12 | 8.19 | Very Poor_Mixed | 2482 | 3106 | 1.214 | 0.952 | 9.52 | 0.941 | 9.12 | 0.1491 | 0.627 | 0.1871 | 0.3521 | 1 | 0.0946 | 0.225 | 0.3626 | 0.3626 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
58 | 287.6 | 255.1 | 75.9 | 63.8 | 1.1 | 477.5 | 2857.1 | 57.2 | 22.1 | 75 | 75 | 70 | 81.9 | 35.8 | 12.4 | 8772.1 | 9456.8 | 9063.3 | 16571.6 | 18838.3 | 16993 | 1.889 | 1.992 | 1.875 | 0.57 | 0.544 | 0.511 | 2.95 | -2.22 | 2 | 0.51 | 0.51 | 0.521 | 2.6 | 2 | 2.87 | 0.524 | 0.505 | 0.634 | -3.15 | 3.37 | 4.31 | 0.525 | 0.511 | 0.583 | 2.86 | -2.03 | 2.32 | Fair_Bushing_TD_Cap | 8772.1 | 16571.6 | 1.875 | 0.57 | 2.95 | 0.634 | 4.31 | 0.8788 | 0.926 | 0.9875 | 0.9575 | 1 | 0.8529 | 0.8104 | 0.9027 | 0.9027 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
59 | 1754.2 | 861.3 | 139.2 | 180.1 | 30.9 | 1284.8 | 8002.3 | 35.7 | 47.8 | 106.3 | 101.5 | 92.8 | 115.5 | 44 | 31.6 | 2252.3 | 1205.7 | 1600.1 | 2576.8 | 1266 | 1757.6 | 1.144 | 1.05 | 1.098 | 0.942 | 0.919 | 0.936 | 9.53 | -8.15 | 9.84 | 0.753 | 0.913 | 0.859 | -6.92 | 7.35 | 7.26 | 0.796 | 0.783 | 0.838 | -6.94 | -7.88 | -8.09 | 0.83 | 0.888 | 0.969 | -6.05 | 8.91 | 7.27 | Very Poor_Mixed | 1205.7 | 1266 | 1.05 | 0.942 | 9.84 | 0.969 | 8.91 | 0.1009 | 0.6035 | 0.1749 | 0.3368 | 1 | 0.0862 | 0.2102 | 0.3419 | 0.3419 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
60 | 1341.2 | 845.9 | 138.5 | 162.5 | 33.4 | 1134.1 | 7528.1 | 32.3 | 43.8 | 103.8 | 105.8 | 92.2 | 117.2 | 43.6 | 29.2 | 2476 | 1879 | 1727.5 | 2855.2 | 2096.3 | 1949.5 | 1.153 | 1.116 | 1.129 | 0.947 | 0.94 | 0.882 | 9.05 | 8.82 | -8.22 | 0.864 | 0.854 | 0.761 | -6.55 | 5.92 | 5.64 | 0.941 | 0.78 | 0.767 | 6.28 | 9.16 | 6.19 | 0.897 | 0.753 | 0.842 | 6.96 | 8.92 | -7.57 | Very Poor_Mixed | 1727.5 | 1949.5 | 1.116 | 0.947 | 9.05 | 0.941 | 9.16 | 0.1593 | 0.6415 | 0.1624 | 0.4276 | 1 | 0.1166 | 0.2409 | 0.3741 | 0.3741 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
61 | 524 | 402.9 | 92.1 | 94.1 | 8.1 | 730.3 | 4296.2 | 51 | 30.9 | 86.9 | 87.3 | 76.1 | 91.7 | 38.5 | 20.3 | 7276 | 6954.4 | 6647.4 | 12911.3 | 11715.1 | 11238.6 | 1.775 | 1.685 | 1.691 | 0.697 | 0.661 | 0.619 | -4.41 | 5.29 | -3.74 | 0.549 | 0.591 | 0.645 | -3.58 | 3.53 | -3.42 | 0.569 | 0.583 | 0.622 | 3.64 | 3.61 | 3.86 | 0.593 | 0.572 | 0.628 | 3.29 | 4.18 | 3.48 | Fair_Mixed | 6647.4 | 11238.6 | 1.685 | 0.697 | 5.29 | 0.645 | 4.18 | 0.6111 | 0.7842 | 0.6427 | 0.7372 | 1 | 0.5611 | 0.6396 | 0.7017 | 0.7017 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
62 | 152.7 | 120.4 | 73.3 | 60.9 | 3.2 | 455.4 | 2917.1 | 57.3 | 22.2 | 80.6 | 79.5 | 73.1 | 85.9 | 36.5 | 10 | 9435 | 8472.8 | 8892 | 17956.9 | 15748.4 | 17159.9 | 1.903 | 1.859 | 1.93 | 0.841 | 0.837 | 0.786 | -8.43 | 6.73 | 5.61 | 0.5 | 0.555 | 0.51 | 2 | -2 | -2.62 | 0.5 | 0.542 | 0.5 | 2.13 | 2 | -2.39 | 0.549 | 0.502 | 0.543 | -2.32 | 2.18 | 2.4 | Poor_Winding_TD_Cap | 8472.8 | 15748.4 | 1.859 | 0.841 | 8.43 | 0.555 | 2.62 | 0.8489 | 0.9238 | 0.8147 | 1 | 1 | 0.2832 | 0.8867 | 0.8138 | 0.8138 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
63 | 1634.3 | 942.3 | 143.5 | 197 | 30.4 | 1344 | 8525.9 | 33.5 | 44.5 | 105.8 | 106.9 | 93.7 | 115 | 45 | 34 | 2278.4 | 2022 | 2296.5 | 2610.6 | 2183.7 | 2720.2 | 1.146 | 1.08 | 1.184 | 0.917 | 0.973 | 0.899 | 9.24 | -9.78 | 9.02 | 0.807 | 0.783 | 0.701 | 6.46 | -5.76 | -7.54 | 0.812 | 0.795 | 0.938 | 5.38 | -8.66 | 5.97 | 0.879 | 0.821 | 0.809 | 8.28 | 7.02 | 9.67 | Very Poor_Mixed | 2022 | 2183.7 | 1.08 | 0.973 | 9.78 | 0.938 | 9.67 | 0.0723 | 0.6347 | 0.1376 | 0.2434 | 1 | 0.0794 | 0.2474 | 0.3358 | 0.3358 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
64 | 1077.7 | 642.6 | 117.9 | 138.8 | 22.9 | 976.3 | 6521 | 57.1 | 23.9 | 81.9 | 81.5 | 76.1 | 88.5 | 35.7 | 12.4 | 8049.6 | 8660.2 | 9342.7 | 15127.9 | 16987.8 | 17346 | 1.879 | 1.962 | 1.857 | 0.569 | 0.531 | 0.557 | -2.85 | 2 | -2.95 | 0.5 | 0.511 | 0.502 | -2 | 2 | 2.39 | 0.5 | 0.542 | 0.556 | -2.08 | 2 | 2 | 0.506 | 0.506 | 0.529 | -2.6 | 2.28 | 2.31 | Poor_DGA | 8049.6 | 15127.9 | 1.857 | 0.569 | 2.95 | 0.556 | 2.6 | 0.3192 | 0.8894 | 0.7544 | 0.9575 | 1 | 0.8151 | 0.9008 | 0.7461 | 0.7461 | Fair | 1 | 1 | DGA | 0 |  | C2H2
65 | 488.2 | 294.5 | 80 | 92.2 | 3 | 577.6 | 3184.4 | 59.7 | 21.7 | 77.8 | 79.4 | 71.5 | 83.5 | 36 | 13.5 | 6850.6 | 6163.5 | 5942.1 | 11080 | 9219.1 | 9560.3 | 1.617 | 1.496 | 1.609 | 0.607 | 0.592 | 0.68 | 4.21 | 2.69 | 4.3 | 0.5 | 0.5 | 0.528 | 2.81 | 2.05 | 3.34 | 0.529 | 0.5 | 0.532 | 2.28 | 2.67 | -2 | 0.544 | 0.5 | 0.5 | 2.53 | 2 | -2.38 | Poor_IR_PI | 5942.1 | 9219.1 | 1.496 | 0.68 | 4.3 | 0.544 | 3.34 | 0.7349 | 0.9355 | 0.87 | 0.9318 | 1 | 0.643 | 0.9028 | 0.8421 | 0.8421 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
66 | 1086.4 | 624.5 | 112.6 | 130.7 | 16.6 | 1002.4 | 5726.2 | 54.4 | 25.5 | 80.5 | 79.9 | 75.5 | 86.1 | 36.7 | 16.4 | 7605.2 | 8186.9 | 8219.9 | 13237.7 | 15079.7 | 15105.9 | 1.741 | 1.842 | 1.838 | 0.552 | 0.537 | 0.5 | 2.24 | 2.81 | 2.7 | 0.547 | 0.539 | 0.558 | 2.14 | 2.29 | 2 | 0.536 | 0.504 | 0.536 | 2.56 | 2.7 | 2 | 0.609 | 0.585 | 0.506 | 2.05 | 2.93 | 2.36 | Poor_DGA | 7605.2 | 13237.7 | 1.741 | 0.552 | 2.81 | 0.609 | 2.93 | 0.3749 | 0.8617 | 0.7911 | 0.855 | 1 | 0.8672 | 0.8023 | 0.7448 | 0.7448 | Fair | 1 | 1 | DGA | 0 |  | C2H2
67 | 613.9 | 403.4 | 85.8 | 100.3 | 1 | 2609 | 24784.4 | 31.3 | 48.8 | 79.5 | 80.7 | 75.9 | 88.5 | 36.2 | 11.7 | 5481.2 | 5534.8 | 5930.2 | 8243.9 | 8453 | 9279.1 | 1.504 | 1.527 | 1.565 | 0.705 | 0.647 | 0.722 | 5.37 | 4.52 | 5.29 | 0.562 | 0.545 | 0.501 | 2.79 | -2.5 | -2.52 | 0.556 | 0.559 | 0.544 | -2.85 | 3.31 | 2.66 | 0.5 | 0.542 | 0.518 | 2.19 | 2.57 | 2.84 | Critical_Oil | 5481.2 | 8243.9 | 1.504 | 0.722 | 5.37 | 0.562 | 3.31 | 0.6129 | 0.5942 | 0.7805 | 0.9724 | 1 | 0.4951 | 0.8102 | 0.7263 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | Moisture_PPM
68 | 535.2 | 351.5 | 91 | 154.7 | 2.4 | 655.1 | 4149.1 | 52.1 | 80.2 | 109.1 | 108.6 | 96.1 | 117.7 | 45.2 | 13.8 | 7889.5 | 8192.4 | 7349.7 | 14266.4 | 14091.6 | 13283.3 | 1.808 | 1.72 | 1.807 | 0.614 | 0.5 | 0.527 | 3.68 | 2.34 | -2.22 | 0.516 | 0.522 | 0.553 | 3.24 | -2.67 | -2.6 | 0.585 | 0.513 | 0.56 | 2.46 | 2.98 | 2.5 | 0.57 | 0.539 | 0.556 | 2.67 | 3.26 | 2.36 | Critical_Thermal | 7349.7 | 13283.3 | 1.72 | 0.614 | 3.68 | 0.585 | 3.26 | 0.6518 | 0.5833 | 0.082 | 0.9244 | 1 | 0.8365 | 0.7743 | 0.7039 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
69 | 341.7 | 252.8 | 73.4 | 68.5 | 2.6 | 488.5 | 2902.4 | 53.8 | 81.9 | 82.6 | 81.4 | 76.8 | 86 | 36.3 | 13.7 | 6739.8 | 5577.9 | 6892.6 | 10910.5 | 8428.3 | 11943.7 | 1.619 | 1.511 | 1.733 | 0.563 | 0.612 | 0.604 | -2.7 | 3.46 | 2.86 | 0.564 | 0.677 | 0.975 | -3.96 | 3.95 | 9.32 | 0.618 | 0.505 | 0.61 | 2.11 | 4.26 | -2.41 | 0.587 | 0.522 | 0.582 | 3.18 | 3.7 | -4.34 | Critical_Bushing_TD_Cap | 5577.9 | 8428.3 | 1.511 | 0.612 | 3.46 | 0.975 | 9.32 | 0.8091 | 0.5833 | 0.7543 | 0.9269 | 1 | 0.7269 | 0.6095 | 0.7655 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
70 | 1482.8 | 867.5 | 132.7 | 170.6 | 34.3 | 1304.7 | 7925.3 | 34.6 | 46.1 | 107.6 | 103.4 | 92.3 | 114.8 | 43.7 | 32.9 | 2687.4 | 1664.7 | 3015.1 | 3282.4 | 1870.9 | 3706.3 | 1.221 | 1.124 | 1.229 | 0.943 | 0.925 | 0.89 | 8.58 | 9.41 | 7.79 | 0.828 | 0.88 | 0.942 | -5.98 | 6.41 | 8.08 | 0.901 | 0.798 | 0.862 | 5.86 | 6.79 | -7.29 | 0.826 | 0.775 | 0.836 | 8.48 | 8.42 | 6.66 | Very Poor_Mixed | 1664.7 | 1870.9 | 1.124 | 0.943 | 9.41 | 0.942 | 8.48 | 0.1164 | 0.6194 | 0.1655 | 0.2865 | 1 | 0.1245 | 0.2173 | 0.3509 | 0.3509 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
71 | 954.6 | 534.3 | 95.7 | 115.5 | 16.7 | 943.6 | 5604.1 | 53.5 | 23.8 | 76.6 | 75 | 70.9 | 81.3 | 35 | 10 | 8069.4 | 8874.1 | 8376.1 | 14727.8 | 16574.4 | 16331.1 | 1.825 | 1.868 | 1.95 | 0.52 | 0.589 | 0.569 | 2.94 | 3.5 | 3.57 | 0.509 | 0.551 | 0.55 | 2.33 | 2.27 | 2.9 | 0.603 | 0.521 | 0.549 | 2.87 | 3.31 | 2.77 | 0.525 | 0.537 | 0.527 | -2.35 | 2.56 | 2 | Poor_DGA | 8069.4 | 14727.8 | 1.825 | 0.589 | 3.57 | 0.603 | 3.31 | 0.4295 | 0.8912 | 0.9567 | 1 | 1 | 0.7552 | 0.7944 | 0.7687 | 0.7687 | Fair | 1 | 1 | DGA | 0 |  | C2H2
72 | 527.2 | 358.5 | 84.7 | 76.3 | 4.8 | 618.6 | 3742.4 | 30.6 | 46.9 | 77.4 | 79.4 | 75.1 | 83.6 | 37.4 | 16.9 | 5478.4 | 98.5 | 5301.5 | 7814 | 103.7 | 8053.2 | 1.426 | 1.053 | 1.519 | 0.717 | 0.69 | 0.682 | 5.27 | 5.25 | 4.78 | 0.559 | 0.604 | 0.572 | 3.31 | 2.86 | 3.87 | 0.593 | 0.566 | 0.604 | 2.75 | -3.06 | 3.59 | 0.568 | 0.597 | 0.608 | 2.87 | -3.74 | 3.91 | Critical_Oil | 98.5 | 103.7 | 1.053 | 0.717 | 5.27 | 0.608 | 3.91 | 0.6998 | 0.6119 | 0.8362 | 0.8407 | 0.85 | 0.4871 | 0.6655 | 0.698 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
73 | 773.3 | 555.2 | 98.9 | 114.1 | 17.5 | 781.5 | 4988.7 | 44.9 | 34.4 | 92.9 | 91.6 | 82.6 | 98.7 | 39.9 | 25.6 | 4860.5 | 5315.9 | 5599.9 | 6811 | 7915.5 | 8520.6 | 1.401 | 1.489 | 1.522 | 0.703 | 0.758 | 0.72 | 5.86 | 5.75 | 5.23 | 0.646 | 0.65 | 0.729 | 4.85 | 4.32 | 4.6 | 0.675 | 0.684 | 0.658 | 4.1 | 5.67 | 4.64 | 0.703 | 0.645 | 0.733 | -4.5 | 4.81 | 5.49 | Poor_Mixed | 4860.5 | 6811 | 1.401 | 0.758 | 5.86 | 0.733 | 5.67 | 0.4617 | 0.7414 | 0.4864 | 0.5584 | 1 | 0.4307 | 0.4738 | 0.5865 | 0.5865 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
74 | 1005.8 | 613.9 | 110.6 | 145 | 26.6 | 960 | 6513.5 | 58.2 | 20.2 | 80.6 | 78 | 73.9 | 84.4 | 36.4 | 15.1 | 7875.8 | 9077.7 | 8926.7 | 14685.2 | 17069.7 | 16735.1 | 1.865 | 1.88 | 1.875 | 0.535 | 0.531 | 0.52 | -2.87 | 2.91 | 2.03 | 0.58 | 0.594 | 0.534 | -3.12 | 2.84 | -2.63 | 0.527 | 0.508 | 0.554 | -3.01 | 2.94 | 3.43 | 0.526 | 0.537 | 0.567 | 2.05 | -2.13 | 2.35 | Poor_DGA | 7875.8 | 14685.2 | 1.865 | 0.535 | 2.91 | 0.594 | 3.43 | 0.3106 | 0.984 | 0.8302 | 0.8908 | 1 | 0.855 | 0.7747 | 0.7424 | 0.7424 | Fair | 1 | 1 | DGA | 0 |  | C2H2
75 | 929.9 | 573.4 | 101.5 | 121.6 | 18.4 | 874.2 | 5945.7 | 45.8 | 32.8 | 89.6 | 90.4 | 83.1 | 99.8 | 40.2 | 25.4 | 5983.9 | 4146.5 | 6424.8 | 8943.8 | 6122.7 | 10034.6 | 1.495 | 1.477 | 1.562 | 0.78 | 0.742 | 0.79 | 6.06 | 5.81 | 6.42 | 0.648 | 0.712 | 0.692 | 4.57 | -4.92 | 4.83 | 0.613 | 0.622 | 0.667 | 4.65 | 4.29 | -5.58 | 0.624 | 0.635 | 0.737 | -4.52 | -5.36 | 5.05 | Poor_Mixed | 4146.5 | 6122.7 | 1.477 | 0.79 | 6.42 | 0.737 | 5.58 | 0.411 | 0.7605 | 0.5051 | 0.5655 | 1 | 0.3668 | 0.4958 | 0.5734 | 0.5734 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
76 | 1021.4 | 558.6 | 112.2 | 115.8 | 18.1 | 922.9 | 5906.4 | 47.9 | 32.8 | 91.2 | 92.6 | 81.3 | 99.4 | 40.4 | 23.7 | 6039.2 | 4853.5 | 4698.2 | 9321.4 | 6950.7 | 7108.6 | 1.543 | 1.432 | 1.513 | 0.712 | 0.745 | 0.755 | -5.24 | 5.45 | 5.89 | 0.593 | 0.702 | 0.705 | 4.17 | -5.14 | 4.41 | 0.703 | 0.658 | 0.611 | -4.69 | 4.27 | 4.68 | 0.575 | 0.651 | 0.644 | 5.24 | 4 | 5.04 | Poor_Mixed | 4698.2 | 6950.7 | 1.432 | 0.755 | 5.89 | 0.705 | 5.24 | 0.3998 | 0.7605 | 0.4925 | 0.6246 | 1 | 0.4263 | 0.5219 | 0.5853 | 0.5853 | Poor | 0 | 1 | DGA | 0 |  | C2H2
77 | 791 | 451.4 | 103.2 | 121.6 | 14.5 | 755.7 | 5035.5 | 46.2 | 34.1 | 92.6 | 96.3 | 83.6 | 100.8 | 40 | 25.2 | 6039.3 | 5472 | 6167.2 | 9528.2 | 8502.6 | 9559.4 | 1.578 | 1.554 | 1.55 | 0.732 | 0.735 | 0.666 | 5.14 | -5.52 | 5.21 | 0.654 | 0.628 | 0.707 | 4.9 | 5.65 | 4.82 | 0.722 | 0.686 | 0.765 | -5.18 | -3.78 | -5.65 | 0.715 | 0.722 | 0.562 | 5.27 | -4.8 | 5.17 | Poor_Mixed | 5472 | 8502.6 | 1.55 | 0.735 | 5.52 | 0.765 | 5.65 | 0.4844 | 0.7449 | 0.4415 | 0.5725 | 1 | 0.4636 | 0.4642 | 0.5917 | 0.5917 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
78 | 1054.4 | 520.4 | 110.8 | 115.4 | 17.7 | 871.3 | 5957.1 | 45.6 | 35.4 | 91.8 | 88.6 | 79.6 | 100.2 | 38.7 | 26.3 | 5680.6 | 5395.4 | 5178.5 | 9221 | 8158.7 | 8044.4 | 1.623 | 1.512 | 1.553 | 0.776 | 0.716 | 0.739 | 5.88 | 4.82 | 5.82 | 0.624 | 0.658 | 0.666 | 5.6 | 5 | 4.28 | 0.658 | 0.634 | 0.589 | 4.1 | 4.08 | -4.69 | 0.633 | 0.703 | 0.672 | -5.92 | -4.18 | -3.58 | Poor_Mixed | 5178.5 | 8044.4 | 1.512 | 0.776 | 5.88 | 0.703 | 5.92 | 0.4112 | 0.7299 | 0.5328 | 0.5335 | 1 | 0.4224 | 0.5215 | 0.5833 | 0.5833 | Poor | 0 | 1 | DGA | 0 |  | C2H2
79 | 1766 | 972.8 | 145.2 | 191.5 | 34.3 | 1379 | 9084.2 | 34.2 | 45.5 | 108.2 | 108.3 | 93.5 | 116 | 45.1 | 33.2 | 2274.2 | 1430 | 690 | 2540.7 | 1550 | 1200 | 1.117 | 1.084 | 1.739 | 0.972 | 0.926 | 0.957 | -9.18 | 8.68 | -9.22 | 0.893 | 0.937 | 0.883 | 8.44 | 8.74 | 7.54 | 0.925 | 0.931 | 0.855 | 8.13 | 5.68 | 7.41 | 0.806 | 0.892 | 0.823 | -5.45 | 7.04 | 6.63 | Very Poor_Mixed | 690 | 1200 | 1.084 | 0.972 | 9.22 | 0.937 | 8.74 | 0.0342 | 0.6251 | 0.1121 | 0.2748 | 1 | 0.0803 | 0.184 | 0.3129 | 0.3129 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
80 | 804.7 | 457.8 | 103.7 | 114.1 | 14 | 864.3 | 5594.4 | 47.5 | 36.1 | 92.2 | 91.2 | 83.4 | 102.5 | 40.6 | 23.7 | 5799.7 | 4438.9 | 6207.1 | 9749.8 | 6715.8 | 10024.5 | 1.681 | 1.513 | 1.615 | 0.739 | 0.775 | 0.749 | -6.42 | 6.59 | 6.23 | 0.621 | 0.685 | 0.672 | 4.28 | 4.23 | 5.54 | 0.723 | 0.686 | 0.656 | -3.92 | 4.34 | -5.35 | 0.715 | 0.647 | 0.673 | 5.59 | 5.71 | 4.44 | Poor_Mixed | 4438.9 | 6715.8 | 1.513 | 0.775 | 6.59 | 0.723 | 5.71 | 0.4737 | 0.722 | 0.4649 | 0.6246 | 1 | 0.363 | 0.4784 | 0.5797 | 0.5797 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
81 | 1746.3 | 925.6 | 141.3 | 194.3 | 33.1 | 1298.1 | 8730.9 | 31.5 | 49.4 | 106.5 | 106.1 | 97.2 | 118.1 | 45.1 | 35.1 | 1266.2 | 1040.4 | 1760.2 | 1363.5 | 1200 | 1943.6 | 1.077 | 1.153 | 1.104 | 0.976 | 0.96 | 0.935 | 9.84 | 9.23 | -8.68 | 0.921 | 0.896 | 0.87 | 7.15 | 8.26 | 6.97 | 0.76 | 0.859 | 0.744 | -7.42 | -5.39 | 8.25 | 0.751 | 0.848 | 0.839 | 7.48 | 6.74 | 9.24 | Very Poor_Mixed | 1040.4 | 1200 | 1.077 | 0.976 | 9.84 | 0.921 | 9.24 | 0.0603 | 0.5888 | 0.1026 | 0.1998 | 1 | 0.0656 | 0.2241 | 0.3155 | 0.3155 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
82 | 1013.2 | 482.4 | 92.9 | 104.4 | 19.8 | 851.5 | 4845.2 | 45 | 35.1 | 89.6 | 89.3 | 82.2 | 98.3 | 38.9 | 24.9 | 5244.7 | 7119.3 | 4964.4 | 7766.4 | 11478.9 | 7561.1 | 1.481 | 1.612 | 1.523 | 0.688 | 0.763 | 0.682 | 5.31 | 5.3 | 4.67 | 0.744 | 0.609 | 0.732 | 6.05 | 4.98 | 5.13 | 0.712 | 0.756 | 0.696 | -5.81 | 5.74 | 5.27 | 0.774 | 0.65 | 0.671 | 5.44 | 4.93 | -4.4 | Poor_Mixed | 4964.4 | 7561.1 | 1.481 | 0.763 | 5.31 | 0.774 | 6.05 | 0.4437 | 0.7333 | 0.5337 | 0.5831 | 1 | 0.475 | 0.4274 | 0.5849 | 0.5849 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
83 | 1198.2 | 642.1 | 111.7 | 148.1 | 22.4 | 1066.8 | 6881.4 | 55.9 | 23.8 | 79.3 | 78 | 74.9 | 83.4 | 35.5 | 12 | 7763.5 | 8440.2 | 10000 | 14335.9 | 15942.9 | 19263.6 | 1.847 | 1.889 | 1.926 | 0.56 | 0.588 | 0.556 | 3.01 | 3.27 | 2.79 | 0.538 | 0.5 | 0.5 | 2.01 | 2.43 | 2.04 | 0.515 | 0.545 | 0.5 | -2 | 2.35 | 2.91 | 0.5 | 0.524 | 0.524 | 2.17 | 2.94 | 2.62 | Poor_DGA | 7763.5 | 14335.9 | 1.847 | 0.588 | 3.27 | 0.545 | 2.94 | 0.2943 | 0.8912 | 0.8429 | 0.9661 | 1 | 0.7583 | 0.8956 | 0.7405 | 0.7405 | Fair | 1 | 1 | DGA | 0 |  | C2H2
84 | 1601.7 | 917.3 | 141 | 182.8 | 34.3 | 1245.4 | 8487.8 | 33.9 | 47.1 | 107.4 | 106 | 94.6 | 115.8 | 44.1 | 32.7 | 690 | 690 | 1341.6 | 1200 | 1200 | 1516.1 | 1.739 | 1.739 | 1.13 | 0.977 | 0.95 | 0.984 | 9.84 | 9.51 | 9.84 | 0.921 | 0.902 | 0.791 | 6.99 | 5.84 | 5.81 | 0.853 | 0.976 | 0.726 | -6.37 | -7.04 | 7.68 | 0.735 | 0.926 | 0.861 | 6.76 | 6.16 | 7.82 | Very Poor_Mixed | 690 | 1200 | 1.13 | 0.984 | 9.84 | 0.976 | 7.82 | 0.0849 | 0.61 | 0.1313 | 0.2943 | 1 | 0.0327 | 0.2284 | 0.328 | 0.328 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
85 | 199.3 | 140.5 | 67.4 | 113.1 | 3.5 | 367.4 | 3446.7 | 57.9 | 21.9 | 91.5 | 92.2 | 82.3 | 100 | 40.1 | 13.8 | 8814.5 | 9421.4 | 8790.7 | 17201.9 | 18733.1 | 16636.6 | 1.952 | 1.988 | 1.893 | 0.558 | 0.5 | 0.5 | 2.4 | 2 | 2.05 | 0.545 | 0.52 | 0.509 | 2.61 | -2.6 | 2.87 | 0.5 | 0.55 | 0.551 | 2.66 | 2.95 | -2.23 | 0.524 | 0.506 | 0.512 | 3.05 | -2 | 3.11 | Poor_Thermal | 8790.7 | 16636.6 | 1.893 | 0.558 | 2.4 | 0.551 | 3.11 | 0.7911 | 0.9307 | 0.4856 | 0.9244 | 1 | 0.9368 | 0.8419 | 0.8469 | 0.8469 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
86 | 1444.5 | 867.1 | 138.1 | 176.4 | 42.9 | 1243.8 | 7868.5 | 35.6 | 46 | 102.8 | 104.4 | 91.8 | 112.5 | 43.2 | 36.7 | 2716.2 | 2241.2 | 3394.4 | 3411.9 | 2811.9 | 4407.6 | 1.256 | 1.255 | 1.298 | 0.923 | 0.94 | 0.925 | -8.56 | 9.6 | -8.13 | 0.699 | 0.77 | 0.894 | -6.05 | 6.32 | 8.11 | 0.759 | 0.81 | 0.786 | 7.47 | 7.77 | 6.35 | 0.813 | 0.75 | 0.785 | 7.72 | -6.94 | 7.81 | Critical_Mixed | 2241.2 | 2811.9 | 1.255 | 0.94 | 9.6 | 0.894 | 8.11 | 0.1145 | 0.6203 | 0.2044 | 0.1356 | 1 | 0.1088 | 0.2767 | 0.3553 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
87 | 157.7 | 132.3 | 75.3 | 64.6 | 4 | 421.9 | 2500 | 57 | 24.3 | 78.9 | 77.2 | 70 | 81.9 | 35 | 11.1 | 8864.4 | 10000 | 10000 | 16193.6 | 20000 | 20000 | 1.827 | 2 | 2 | 0.666 | 0.607 | 0.673 | -4.51 | -3.82 | -5.19 | 0.519 | 0.527 | 0.522 | -2 | 2 | -2.27 | 0.5 | 0.5 | 0.5 | 2.25 | 2 | 2 | 0.5 | 0.5 | 0.531 | 2.4 | -2 | -2.41 | Fair_Winding_TD_Cap | 8864.4 | 16193.6 | 1.827 | 0.673 | 5.19 | 0.531 | 2.41 | 0.8335 | 0.8821 | 0.9109 | 0.984 | 1 | 0.57 | 0.9303 | 0.8618 | 0.8618 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
88 | 1598.4 | 826 | 135.3 | 169 | 25.4 | 1287.3 | 7966.4 | 37.5 | 62.3 | 102.9 | 102.4 | 92.5 | 111.2 | 43.5 | 36.8 | 3081 | 1471.6 | 2256.8 | 3971.4 | 1536.7 | 2850.3 | 1.289 | 1.044 | 1.263 | 0.876 | 0.959 | 0.929 | 8.31 | 8.87 | 9.66 | 0.762 | 0.842 | 0.826 | 8.33 | 8.88 | 7.6 | 0.886 | 0.733 | 0.9 | 5.13 | 8.23 | -5.16 | 0.853 | 0.702 | 0.872 | 7.19 | 5.25 | -6.61 | Critical_Mixed | 1471.6 | 1536.7 | 1.044 | 0.959 | 9.66 | 0.9 | 8.88 | 0.1547 | 0.5833 | 0.2156 | 0.1315 | 1 | 0.1054 | 0.2536 | 0.3572 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
89 | 259.1 | 246.7 | 75.5 | 59.9 | 49.8 | 418.3 | 3393.5 | 52 | 29.7 | 82 | 81.6 | 75.3 | 87.2 | 37.2 | 11.4 | 7970.3 | 8620 | 8204 | 14356.6 | 16358.3 | 14949.3 | 1.801 | 1.898 | 1.822 | 0.637 | 0.57 | 0.58 | 3.76 | -2.32 | 2.55 | 0.602 | 0.545 | 0.626 | 4.21 | 4.17 | 2.72 | 0.546 | 0.972 | 0.562 | 2.55 | 8.97 | 3.42 | 0.631 | 0.633 | 0.628 | 3.89 | 2.8 | -3.77 | Critical_Bushing_TD_Cap | 7970.3 | 14356.6 | 1.801 | 0.637 | 3.76 | 0.972 | 8.97 | 0.5989 | 0.8 | 0.7577 | 0.9783 | 1 | 0.7349 | 0.5815 | 0.738 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
90 | 154.1 | 220.7 | 75.6 | 154.4 | 2.1 | 411.5 | 2718.7 | 49.4 | 30.5 | 109 | 106.7 | 94.7 | 116.6 | 44.2 | 11.9 | 8062.8 | 7321.3 | 8086.3 | 14075.7 | 12963.2 | 14831.1 | 1.746 | 1.771 | 1.834 | 1.303 | 0.604 | 0.587 | -3.88 | 3.72 | 3.86 | 0.563 | 0.576 | 0.502 | 3.26 | 2.76 | 2.9 | 0.529 | 0.576 | 0.586 | 2.32 | 2.45 | -3.03 | 0.527 | 0.567 | 0.553 | 2.39 | -3.01 | 2.56 | Critical_Thermal | 7321.3 | 12963.2 | 1.746 | 1.303 | 3.88 | 0.586 | 3.26 | 0.7689 | 0.7894 | 0.1135 | 0.9682 | 1 | 0.5574 | 0.7623 | 0.722 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | C2H4
91 | 1416.4 | 789.7 | 129.7 | 163.7 | 30.3 | 1149 | 7461 | 38 | 44.1 | 98.8 | 99.1 | 90.5 | 108 | 43.5 | 32.9 | 2676.5 | 1947.9 | 1526.6 | 3491.1 | 2312 | 1655.7 | 1.304 | 1.187 | 1.085 | 0.879 | 0.875 | 1.063 | 7.76 | -7.93 | 8.4 | 0.74 | 0.87 | 0.734 | 5.18 | -7.62 | 6.04 | 0.775 | 0.716 | 0.737 | -8.64 | 8.3 | 4.94 | 0.709 | 0.778 | 0.832 | 6.45 | 4.87 | 6.15 | Critical_Mixed | 1526.6 | 1655.7 | 1.085 | 1.063 | 8.4 | 0.87 | 8.64 | 0.1788 | 0.6386 | 0.2858 | 0.2865 | 1 | 0.1549 | 0.321 | 0.4037 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
92 | 973.9 | 656.7 | 112.4 | 120.8 | 19.2 | 904.9 | 6085.6 | 57.5 | 24.9 | 82 | 83.6 | 71.4 | 84.1 | 36.7 | 13.3 | 9034.7 | 8308.9 | 8183.7 | 18020.8 | 14764.3 | 14707.4 | 1.995 | 1.777 | 1.797 | 0.514 | 0.5 | 0.516 | -2.15 | 2.25 | -2.66 | 0.571 | 0.644 | 0.571 | 2.63 | -2.71 | 2.31 | 0.576 | 0.504 | 0.539 | 3.16 | 2 | 3 | 0.565 | 0.534 | 0.561 | -2.65 | 2.58 | 3.15 | Poor_DGA | 8183.7 | 14707.4 | 1.777 | 0.516 | 2.66 | 0.644 | 3.16 | 0.3811 | 0.8717 | 0.7929 | 0.9367 | 1 | 0.9245 | 0.7472 | 0.7499 | 0.7499 | Fair | 1 | 1 | DGA | 0 |  | C2H2
93 | 1510.8 | 758.9 | 135.6 | 179.6 | 29.9 | 1134.9 | 7561 | 35.5 | 44.7 | 103.8 | 102.9 | 94.8 | 114.1 | 43.2 | 29.9 | 3145.5 | 3740.4 | 4162 | 3911.6 | 5150 | 5697.2 | 1.244 | 1.377 | 1.369 | 0.905 | 0.94 | 0.942 | 9.53 | 8.61 | 9.23 | 0.697 | 0.802 | 0.856 | -6.04 | 8.25 | -7.11 | 0.722 | 0.72 | 0.847 | 6.59 | 6.38 | -7.21 | 0.85 | 0.88 | 0.743 | 7.62 | 6.85 | -7.14 | Very Poor_Mixed | 3145.5 | 3911.6 | 1.244 | 0.942 | 9.53 | 0.88 | 8.25 | 0.1595 | 0.6328 | 0.1824 | 0.4014 | 1 | 0.0908 | 0.2775 | 0.3768 | 0.3768 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
94 | 100 | 132.6 | 65 | 62.4 | 1.8 | 350 | 2500 | 58.6 | 21 | 76.8 | 75 | 71.9 | 81 | 36.1 | 12.5 | 9443.4 | 9970.4 | 8594.6 | 18742.1 | 19712 | 15932.9 | 1.985 | 1.977 | 1.854 | 0.501 | 0.5 | 0.517 | 2.11 | 2 | -2 | 0.5 | 0.511 | 0.536 | 2.7 | 2.28 | 2.4 | 0.5 | 0.5 | 0.543 | -2 | 2 | 2 | 0.508 | 0.546 | 0.528 | -2.94 | -2.13 | 2.83 | Good_Mixed | 8594.6 | 15932.9 | 1.854 | 0.517 | 2.11 | 0.546 | 2.94 | 0.9144 | 0.9543 | 0.9417 | 0.9552 | 1 | 0.9682 | 0.8844 | 0.9398 | 0.9398 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
95 | 270.3 | 145.9 | 71.7 | 68.9 | 2.9 | 412.8 | 3446.6 | 56.7 | 23.1 | 77.8 | 79.2 | 71.7 | 83.6 | 37.2 | 11.5 | 8880.1 | 8153.1 | 9529.5 | 16753.1 | 14769.5 | 17475.3 | 1.887 | 1.812 | 1.834 | 0.802 | 0.751 | 0.752 | 7.07 | 6.59 | 6.17 | 0.573 | 0.538 | 0.557 | 2.37 | -3.23 | 2.81 | 0.565 | 0.632 | 0.531 | -3.6 | -3.06 | 3.11 | 0.546 | 0.548 | 0.565 | 2.8 | 3.01 | 3.07 | Poor_Winding_TD_Cap | 8153.1 | 14769.5 | 1.812 | 0.802 | 7.07 | 0.632 | 3.6 | 0.8326 | 0.9047 | 0.8633 | 0.9764 | 1 | 0.3411 | 0.7267 | 0.7904 | 0.7904 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
96 | 408.4 | 235 | 75.2 | 72 | 3.4 | 557 | 3015.9 | 57.6 | 20.6 | 80.2 | 82.4 | 76.5 | 84.6 | 36.2 | 10.2 | 8828.9 | 9280.9 | 9839.8 | 17352.7 | 17741.5 | 19356.9 | 1.965 | 1.912 | 1.967 | 0.546 | 0.551 | 0.562 | 2.84 | 3.69 | 2.9 | 0.559 | 0.5 | 0.536 | 3.11 | 3.09 | 2.22 | 0.528 | 0.567 | 0.741 | 2 | -2.59 | 6.4 | 0.55 | 0.59 | 0.558 | 2.21 | -3.25 | 3.25 | Poor_Bushing_TD_Cap | 8828.9 | 17352.7 | 1.912 | 0.562 | 3.69 | 0.741 | 6.4 | 0.7721 | 0.9672 | 0.7756 | 0.9981 | 1 | 0.7727 | 0.7307 | 0.8363 | 0.8363 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
97 | 192.9 | 213.8 | 69.6 | 53.1 | 1.3 | 359.6 | 3066.1 | 57.1 | 23.3 | 76.6 | 75.5 | 71.1 | 82.9 | 35.6 | 15.6 | 7573.7 | 10000 | 8741.8 | 13082 | 20000 | 16840.3 | 1.727 | 2 | 1.926 | 0.989 | 0.947 | 0.924 | 9.29 | 9.84 | 9.65 | 0.555 | 0.515 | 0.547 | 2.77 | -2.74 | 2.56 | 0.501 | 0.53 | 0.566 | -21.08 | -2.76 | 3.03 | 0.635 | 0.575 | 0.542 | -2.35 | 2.83 | 2.39 | Critical_Winding_TD_Cap | 7573.7 | 13082 | 1.727 | 0.989 | 9.84 | 0.635 | 21.08 | 0.9216 | 0.9008 | 0.9341 | 0.8773 | 1 | 0.051 | 0.7445 | 0.7769 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_CapChange_pct>=10% abs: critical bushing capacitance change | Winding_HV_TanDelta_pct
98 | 176.4 | 233.1 | 74.2 | 59.3 | 2.3 | 1668.2 | 13918.5 | 32.1 | 49.4 | 83.8 | 85.1 | 77.4 | 89.5 | 36 | 20.8 | 4716 | 5351.1 | 4896.4 | 6630.3 | 7855.5 | 7239.2 | 1.406 | 1.468 | 1.478 | 0.685 | 0.656 | 0.715 | 4.07 | 3.97 | -4.28 | 0.639 | 0.657 | 0.692 | 4.23 | -4.11 | 3.24 | 0.611 | 0.614 | 0.74 | 3.92 | 4.55 | 3.93 | 0.627 | 0.68 | 0.611 | 4.19 | 3.16 | 3.33 | Critical_Oil | 4716 | 6630.3 | 1.406 | 0.715 | 4.28 | 0.74 | 4.55 | 0.6575 | 0.5888 | 0.6962 | 0.7211 | 1 | 0.5559 | 0.5466 | 0.6769 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | Moisture_PPM
99 | 227.3 | 183.3 | 68.2 | 75.7 | 2.7 | 470.1 | 3278.1 | 57.9 | 23.4 | 75.7 | 76.2 | 70 | 80 | 35 | 14.2 | 10000 | 9393.7 | 9374.6 | 20000 | 18188.2 | 17230.7 | 2 | 1.936 | 1.838 | 0.509 | 0.5 | 0.503 | 2 | -2.07 | -2.06 | 0.519 | 0.521 | 0.53 | 2 | 2 | 2 | 0.526 | 0.509 | 0.547 | 2.22 | 2.11 | -2.95 | 0.565 | 0.535 | 0.554 | 2 | -2.48 | 2.21 | Good_Mixed | 9374.6 | 17230.7 | 1.838 | 0.509 | 2.07 | 0.565 | 2.95 | 0.8208 | 0.8988 | 0.9668 | 0.9144 | 1 | 0.9705 | 0.8314 | 0.901 | 0.901 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
100 | 1276 | 714.4 | 119.5 | 150.6 | 30.9 | 1083.4 | 6989.6 | 39.2 | 40.6 | 100.5 | 102 | 89.2 | 109.5 | 42.5 | 33.4 | 3917.8 | 3853.8 | 1834.4 | 5204.5 | 5167.2 | 2376.9 | 1.328 | 1.341 | 1.296 | 0.921 | 0.881 | 0.91 | 8.22 | -7.45 | 8.28 | 0.766 | 2.166 | 0.794 | 7.92 | 4.84 | 5.71 | 0.711 | 0.783 | 0.685 | -7.82 | 5.73 | 6.92 | 0.784 | 0.695 | 0.724 | 5.41 | 5.91 | 7.12 | Critical_Mixed | 1834.4 | 2376.9 | 1.296 | 0.921 | 8.28 | 2.166 | 7.92 | 0.2271 | 0.6737 | 0.2661 | 0.267 | 1 | 0.1661 | 0.3213 | 0.4187 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
101 | 672.9 | 346.2 | 92.2 | 97.3 | 11.4 | 722.8 | 4317.4 | 58.1 | 21.6 | 76.4 | 75.5 | 70.5 | 80 | 35.5 | 11.6 | 9331.5 | 10000 | 9658.6 | 18328.9 | 19862.1 | 18942 | 1.964 | 1.986 | 1.961 | 0.516 | 0.5 | 0.507 | -2.02 | 2 | -2.31 | 0.501 | 0.523 | 0.516 | 2.73 | -2.71 | 3.21 | 0.531 | 0.515 | 0.546 | 2.56 | 2.85 | -3.01 | 0.529 | 0.521 | 0.533 | -3.43 | 2.8 | 3.07 | Fair_DGA | 9331.5 | 18328.9 | 1.961 | 0.516 | 2.31 | 0.546 | 3.43 | 0.5727 | 0.938 | 0.9581 | 0.9744 | 1 | 0.9529 | 0.8217 | 0.8416 | 0.8416 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
102 | 306.2 | 270.7 | 83.5 | 69.3 | 1 | 503.4 | 3259 | 54.9 | 23.1 | 80 | 79.2 | 73.2 | 85 | 36.7 | 14.2 | 9248.4 | 8512.1 | 9730.7 | 17463 | 15034.8 | 18870.1 | 1.888 | 1.766 | 1.939 | 0.736 | 0.779 | 0.796 | 5.51 | 7.15 | -6.43 | 0.503 | 0.522 | 0.536 | -2.53 | 2.2 | 2 | 0.573 | 0.548 | 0.538 | -2.19 | 2.8 | 2.69 | 0.5 | 0.511 | 0.538 | 2.36 | 2.26 | 2.15 | Poor_Winding_TD_Cap | 8512.1 | 15034.8 | 1.766 | 0.796 | 7.15 | 0.573 | 2.8 | 0.8796 | 0.9047 | 0.8252 | 0.9144 | 1 | 0.3531 | 0.8439 | 0.818 | 0.818 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
103 | 260.8 | 230.4 | 72.7 | 64.2 | 2.9 | 419 | 3138.1 | 12.9 | 26.7 | 84.4 | 83.5 | 77.2 | 85.9 | 37.6 | 13.8 | 7604.8 | 8571.8 | 8681.4 | 13390.1 | 16746.8 | 16019.1 | 1.761 | 1.954 | 1.845 | 0.973 | 0.986 | 0.94 | 9.54 | -9.84 | 9.49 | 0.533 | 0.534 | 0.503 | 2 | 2.84 | 2.64 | 0.558 | 0.529 | 0.532 | 2 | 3.05 | 3.03 | 0.5 | 0.528 | 0.506 | -3.08 | 2.79 | 2.21 | Critical_Winding_TD_Cap | 7604.8 | 13390.1 | 1.761 | 0.986 | 9.84 | 0.558 | 3.08 | 0.83 | 0.2594 | 0.7147 | 0.9244 | 1 | 0.0407 | 0.8435 | 0.6739 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
104 | 1118.8 | 692.2 | 118.6 | 155.6 | 21.8 | 981.3 | 6793.7 | 58.9 | 23.1 | 76.3 | 80.6 | 72.9 | 83.2 | 35.8 | 12.6 | 8908.7 | 8676.2 | 8074.4 | 17411.3 | 16615.2 | 14965.9 | 1.954 | 1.915 | 1.853 | 0.545 | 0.551 | 0.544 | -2.31 | -3.68 | 2.29 | 0.5 | 0.538 | 0.5 | 2 | 3.08 | 2 | 0.505 | 0.5 | 0.546 | -2.13 | 2.15 | -2.64 | 0.567 | 0.502 | 0.502 | 2.48 | 2.38 | 2 | Poor_DGA | 8074.4 | 14965.9 | 1.853 | 0.551 | 3.68 | 0.567 | 3.08 | 0.2973 | 0.9047 | 0.8658 | 0.953 | 1 | 0.8109 | 0.9006 | 0.7528 | 0.7528 | Fair | 1 | 1 | DGA | 0 |  | C2H2
105 | 864.4 | 479.3 | 103.5 | 112.4 | 14.5 | 791.3 | 5595.6 | 46.4 | 33.3 | 86 | 90.3 | 80 | 93.1 | 39.3 | 23.7 | 6365.1 | 6040.2 | 5754.8 | 10624.1 | 10043.8 | 8246 | 1.669 | 1.663 | 1.433 | 0.685 | 0.654 | 0.718 | -4.12 | 5.75 | 5.26 | 0.59 | 0.705 | 0.679 | -4.43 | 4.73 | 5.42 | 0.613 | 0.654 | 0.654 | 3.76 | -4.83 | 4.11 | 0.646 | 0.68 | 0.641 | 5.05 | -4.06 | 3.88 | Poor_Mixed | 5754.8 | 8246 | 1.433 | 0.718 | 5.75 | 0.705 | 5.42 | 0.4739 | 0.7544 | 0.5898 | 0.6246 | 1 | 0.5016 | 0.5226 | 0.6235 | 0.6235 | Fair | 1 | 1 | DGA | 0 |  | C2H2
106 | 233.5 | 144.5 | 70.3 | 78.2 | 1 | 420.6 | 3224.6 | 56.9 | 21.7 | 86.8 | 86.8 | 78.2 | 92.3 | 38.3 | 14.4 | 9588.5 | 8803.8 | 9408.2 | 18472.1 | 16461.5 | 18499.8 | 1.926 | 1.87 | 1.966 | 0.544 | 0.507 | 0.535 | 2.82 | 2.26 | -3.13 | 0.5 | 0.506 | 0.5 | 2 | 3.12 | -2 | 0.524 | 0.507 | 0.505 | 2.41 | 2.08 | 2 | 0.531 | 0.5 | 0.5 | 2.12 | -2.33 | -2 | Fair_Thermal | 8803.8 | 16461.5 | 1.87 | 0.544 | 3.13 | 0.531 | 3.12 | 0.9129 | 0.9355 | 0.6302 | 0.9092 | 1 | 0.8484 | 0.9335 | 0.8958 | 0.8958 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
107 | 1575.2 | 885.7 | 133.1 | 182.3 | 32.6 | 1293.1 | 7919.2 | 34.6 | 48.1 | 103 | 103.3 | 92.8 | 110.6 | 44.2 | 33.6 | 1171.3 | 1971.2 | 2320.6 | 1229.8 | 2162.5 | 2763.3 | 1.05 | 1.097 | 1.191 | 0.99 | 0.97 | 0.969 | 9.57 | 9.84 | -9.27 | 0.815 | 0.804 | 0.772 | -4.93 | 7.34 | -7.97 | 0.902 | 0.772 | 0.715 | -6.95 | -8.57 | 7.69 | 0.89 | 0.77 | 0.924 | 6.23 | 6.01 | 6.66 | Very Poor_Mixed | 1171.3 | 1229.8 | 1.05 | 0.99 | 9.84 | 0.924 | 8.57 | 0.1065 | 0.6007 | 0.2062 | 0.2591 | 1 | 0.0372 | 0.2542 | 0.3432 | 0.3432 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
108 | 764.4 | 409.8 | 91 | 104.3 | 12 | 738 | 4654 | 47.3 | 31.8 | 88.6 | 86.7 | 81.1 | 98.2 | 38.3 | 22.6 | 5494.1 | 6527.1 | 5653.5 | 9155.3 | 10266.3 | 8274.2 | 1.666 | 1.573 | 1.464 | 0.723 | 0.722 | 0.683 | -5.97 | 6.49 | 5.34 | 0.682 | 0.63 | 0.655 | -4.38 | 4.26 | 3.98 | 0.668 | 0.646 | 0.617 | 4.28 | 4.86 | 3.87 | 0.584 | 0.655 | 0.664 | -3.78 | 4.03 | -3.63 | Poor_Mixed | 5494.1 | 8274.2 | 1.464 | 0.723 | 6.49 | 0.682 | 4.86 | 0.5416 | 0.7728 | 0.5695 | 0.6619 | 1 | 0.4289 | 0.5447 | 0.6363 | 0.6363 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
109 | 405.3 | 228.5 | 79.4 | 74.9 | 2.1 | 448.7 | 3329.1 | 56.6 | 26.6 | 81.8 | 79.2 | 73.6 | 84.9 | 37.2 | 14.3 | 8360.2 | 8644.9 | 8997.7 | 15668.2 | 16001.4 | 17416.8 | 1.874 | 1.851 | 1.936 | 0.99 | 0.979 | 0.99 | -9.84 | 9.51 | 9.84 | 0.546 | 0.514 | 0.559 | 2.59 | 2.92 | 3.16 | 0.587 | 0.533 | 0.598 | 2.57 | -2.6 | 3.3 | 1.116 | 0.507 | 0.592 | 2.91 | -2.27 | -2.76 | Critical_Winding_TD_Cap | 8360.2 | 15668.2 | 1.851 | 0.99 | 9.84 | 1.116 | 3.3 | 0.8108 | 0.8443 | 0.8047 | 0.9118 | 1 | 0.0222 | 0.7031 | 0.7197 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_R_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_HV_TanDelta_pct
110 | 857.5 | 500.1 | 102.7 | 111.6 | 16.1 | 811.1 | 4824 | 46.3 | 35.7 | 92.7 | 91.2 | 80.2 | 99 | 40.4 | 25.1 | 5568.7 | 5611.7 | 4939 | 8344.2 | 8715.8 | 7319.1 | 1.498 | 1.553 | 1.482 | 0.699 | 0.75 | 0.672 | 4.93 | 5.36 | -4.73 | 0.709 | 0.738 | 0.718 | 5.25 | -3.89 | 3.9 | 0.652 | 0.731 | 0.693 | 5.81 | 3.82 | 4.48 | 0.585 | 0.681 | 0.668 | 4.78 | 4.38 | 5.03 | Poor_Mixed | 4939 | 7319.1 | 1.482 | 0.75 | 5.36 | 0.738 | 5.81 | 0.4679 | 0.7265 | 0.5011 | 0.576 | 1 | 0.4833 | 0.4758 | 0.5964 | 0.5964 | Poor | 0 | 1 | DGA | 0 |  | C2H2
111 | 912.5 | 532.9 | 112.9 | 116 | 21.1 | 890 | 5597.2 | 47.9 | 29.9 | 89.2 | 93.1 | 82.3 | 97.1 | 39.6 | 23.9 | 5345.3 | 5946.7 | 5750 | 8119.9 | 9124.6 | 8540.1 | 1.519 | 1.534 | 1.485 | 0.713 | 0.722 | 0.746 | 5.43 | 5.57 | 6.04 | 0.755 | 0.687 | 0.731 | 3.37 | 5.89 | 5.31 | 0.653 | 0.671 | 0.654 | 5.58 | 3.93 | 4.73 | 0.71 | 0.631 | 0.64 | 4.2 | 4.58 | 5.52 | Poor_Mixed | 5345.3 | 8119.9 | 1.485 | 0.746 | 6.04 | 0.755 | 5.89 | 0.4 | 0.7973 | 0.5127 | 0.6177 | 1 | 0.4267 | 0.4734 | 0.5828 | 0.5828 | Poor | 0 | 1 | DGA | 0 |  | C2H2
112 | 1583 | 904 | 143.8 | 184.8 | 32 | 1278.8 | 7900.1 | 33.5 | 46 | 103.7 | 105.3 | 93.3 | 113.7 | 44.2 | 32.7 | 2645.8 | 2388 | 2588.9 | 3328.3 | 2861.9 | 3047.5 | 1.258 | 1.198 | 1.177 | 0.897 | 0.93 | 0.909 | 9.05 | 9.64 | -9.17 | 0.82 | 0.754 | 0.717 | 6.82 | 7.01 | 7.74 | 0.808 | 0.861 | 0.787 | 7.61 | 8.31 | -7.91 | 0.909 | 0.827 | 0.853 | 6.33 | 6.48 | 5.97 | Very Poor_Mixed | 2388 | 2861.9 | 1.177 | 0.93 | 9.64 | 0.909 | 8.31 | 0.0978 | 0.6203 | 0.1727 | 0.2943 | 1 | 0.0943 | 0.2491 | 0.3489 | 0.3489 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
113 | 798.3 | 474 | 99.5 | 111.7 | 15.3 | 738.1 | 5446.8 | 45.8 | 35.4 | 91.3 | 92.1 | 83.2 | 100.9 | 40.4 | 23.9 | 5268.5 | 5680.8 | 6065.5 | 7770.2 | 8339.8 | 9784.5 | 1.475 | 1.468 | 1.613 | 0.713 | 0.798 | 0.718 | -5.99 | -6.35 | 4.61 | 0.68 | 0.65 | 0.691 | 3.89 | -4.26 | 5.64 | 0.701 | 0.635 | 0.651 | 4.38 | -5.12 | -4.64 | 0.686 | 0.667 | 0.664 | 4.29 | 5.71 | 4.57 | Poor_Mixed | 5268.5 | 7770.2 | 1.468 | 0.798 | 6.35 | 0.701 | 5.71 | 0.4862 | 0.7299 | 0.4754 | 0.6177 | 1 | 0.4159 | 0.4885 | 0.5937 | 0.5937 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
114 | 1596.6 | 831.3 | 134 | 175.9 | 34.3 | 1214.3 | 7801.8 | 33.3 | 45.9 | 101.8 | 105 | 93 | 110.5 | 44.3 | 31.9 | 1856.9 | 1163 | 893.3 | 2082 | 1283.3 | 1200 | 1.121 | 1.103 | 1.343 | 0.96 | 0.949 | 0.892 | 9.55 | 8.63 | 8.39 | 0.782 | 0.725 | 0.831 | 5.64 | -7.93 | 7.49 | 0.884 | 0.827 | 0.905 | 7.78 | -8.12 | 6.33 | 0.886 | 0.895 | 0.807 | -7.55 | 6.31 | 8.79 | Very Poor_Mixed | 893.3 | 1200 | 1.103 | 0.96 | 9.55 | 0.905 | 8.79 | 0.1182 | 0.6213 | 0.2021 | 0.3252 | 1 | 0.1013 | 0.2217 | 0.3547 | 0.3547 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
115 | 315.1 | 200.6 | 68.4 | 62 | 1 | 476.3 | 3097.1 | 55.7 | 22.8 | 75 | 75.2 | 70.4 | 80 | 35 | 11.2 | 9561.6 | 9572.6 | 9123.4 | 18484.3 | 18635.1 | 18246.8 | 1.933 | 1.947 | 2 | 0.511 | 0.535 | 0.537 | 2.06 | 3.07 | 3.04 | 0.5 | 0.545 | 0.5 | 2.59 | 2.45 | -2.5 | 0.5 | 0.501 | 0.5 | 3.08 | 2.17 | -2 | 0.5 | 0.518 | 0.542 | -2.19 | 2 | 2.28 | Good_Mixed | 9123.4 | 18246.8 | 1.933 | 0.537 | 3.07 | 0.545 | 3.08 | 0.9116 | 0.9108 | 0.9885 | 0.9821 | 1 | 0.8505 | 0.921 | 0.93 | 0.93 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
116 | 673.8 | 331.7 | 87.2 | 84 | 4.9 | 566.9 | 3953.1 | 17.2 | 25.1 | 83.7 | 86.3 | 77.6 | 91 | 38 | 15.3 | 690 | 1143.4 | 2059.5 | 750.4 | 1204 | 2280.3 | 1.088 | 1.053 | 1.107 | 0.687 | 0.705 | 0.648 | 5.78 | 5.78 | -4.28 | 0.556 | 0.614 | 0.562 | -3.95 | 3.2 | -3.26 | 0.58 | 0.541 | 0.594 | 3.74 | -3.1 | 3.41 | 0.53 | 0.571 | 0.631 | 3.16 | 3.03 | -3.51 | Critical_IR_PI | 690 | 750.4 | 1.053 | 0.705 | 5.78 | 0.631 | 3.95 | 0.684 | 0.285 | 0.6687 | 0.8855 | 0.925 | 0.4935 | 0.6851 | 0.6568 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
117 | 1712.5 | 975 | 148.3 | 193.2 | 34.3 | 1371.1 | 8551.2 | 50.8 | 31.9 | 83.3 | 84.4 | 76.1 | 89.4 | 37.6 | 14.1 | 8127.7 | 8274.6 | 7210.1 | 15415.7 | 14434.3 | 12868.7 | 1.897 | 1.744 | 1.785 | 0.61 | 0.586 | 0.608 | 3.17 | 3.48 | 3.46 | 0.638 | 0.501 | 0.62 | 3.07 | 2.43 | -3.72 | 0.578 | 0.542 | 0.522 | -3.81 | 2.31 | 3.19 | 0.602 | 1.207 | 0.554 | 3.56 | 3.88 | -2.99 | Critical_DGA | 7210.1 | 12868.7 | 1.744 | 0.61 | 3.48 | 1.207 | 3.88 | 0.0419 | 0.7716 | 0.7066 | 0.9169 | 1 | 0.6912 | 0.6634 | 0.5958 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
118 | 771.6 | 520.4 | 101.4 | 117.1 | 19.7 | 865.2 | 5701 | 48.5 | 32.9 | 93.6 | 92.2 | 85 | 101.4 | 40.2 | 23.8 | 6005.9 | 5735 | 5420.6 | 9472.9 | 8953.9 | 8134.9 | 1.577 | 1.561 | 1.501 | 0.748 | 0.775 | 0.771 | -5.87 | 6.4 | 5.94 | 0.626 | 0.637 | 0.737 | 4.55 | -5.84 | -4.58 | 0.67 | 0.696 | 0.692 | 4.34 | -4.4 | -5.1 | 0.689 | 0.706 | 0.753 | 4.14 | 5.41 | -4.83 | Poor_Mixed | 5420.6 | 8134.9 | 1.501 | 0.775 | 6.4 | 0.753 | 5.84 | 0.4299 | 0.7593 | 0.4477 | 0.6212 | 1 | 0.373 | 0.4625 | 0.5699 | 0.5699 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
119 | 723.3 | 335.2 | 84.8 | 86.4 | 1.8 | 621 | 4390.7 | 56.6 | 69 | 76.5 | 77.3 | 71.3 | 83.3 | 36.7 | 17.2 | 8571.8 | 9147.2 | 7506.2 | 15608.3 | 17248.1 | 13103.7 | 1.821 | 1.886 | 1.746 | 0.981 | 0.987 | 0.99 | 9.15 | 9.81 | 9.61 | 0.54 | 0.5 | 0.5 | 2.58 | 2.35 | 2 | 0.5 | 0.5 | 0.5 | -2.47 | 2 | 2 | 0.5 | 0.535 | 0.547 | -3 | 2.07 | 2.21 | Critical_Winding_TD_Cap | 7506.2 | 13103.7 | 1.746 | 0.99 | 9.81 | 0.547 | 3 | 0.7285 | 0.5833 | 0.9039 | 0.832 | 1 | 0.0327 | 0.9223 | 0.7147 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
120 | 905.7 | 575.9 | 110.9 | 121.9 | 20.4 | 923.7 | 6256.3 | 57.9 | 21.2 | 79 | 79.1 | 71.2 | 82.4 | 37.6 | 13.5 | 9408 | 9501.9 | 10000 | 18816 | 19003.7 | 20000 | 2 | 2 | 2 | 0.568 | 0.561 | 0.56 | 2.84 | 3.09 | 3.21 | 0.566 | 0.584 | 0.537 | 2.19 | -2.69 | -2.89 | 0.572 | 0.579 | 0.543 | -2 | 2.72 | 2.03 | 0.601 | 0.54 | 0.538 | -2.52 | 3.2 | 2.27 | Poor_DGA | 9408 | 18816 | 2 | 0.568 | 3.21 | 0.601 | 3.2 | 0.3842 | 0.9486 | 0.8614 | 0.9318 | 1 | 0.7632 | 0.7504 | 0.7445 | 0.7445 | Fair | 1 | 1 | DGA | 0 |  | C2H2
121 | 1458.1 | 897.9 | 136.4 | 165.8 | 29.2 | 1246.5 | 8313.5 | 36.5 | 42.5 | 107.3 | 105.8 | 92.8 | 117.8 | 43.5 | 30.4 | 2004.4 | 2882.9 | 1757.5 | 2280.8 | 3394.6 | 1892.6 | 1.138 | 1.177 | 1.077 | 0.94 | 0.942 | 0.925 | -9.34 | 8.84 | 8.17 | 0.726 | 0.796 | 0.768 | 7.16 | 7.8 | 6.66 | 0.774 | 0.821 | 0.856 | 6.19 | 8.28 | 5.95 | 0.791 | 0.76 | 0.815 | -5.35 | 6.98 | 5.8 | Very Poor_Mixed | 1757.5 | 1892.6 | 1.077 | 0.942 | 9.34 | 0.856 | 8.28 | 0.1402 | 0.6544 | 0.1373 | 0.3825 | 1 | 0.1034 | 0.2876 | 0.3727 | 0.3727 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
122 | 1350.6 | 867.3 | 135.6 | 172.8 | 29.9 | 1247.9 | 8286.5 | 34 | 43.6 | 105.2 | 101.1 | 94.3 | 112.1 | 43.7 | 32.7 | 1913.4 | 2350.9 | 736.7 | 2076 | 2468.5 | 1200 | 1.085 | 1.05 | 1.629 | 0.954 | 0.922 | 0.925 | 9.58 | 9.15 | -8.24 | 0.841 | 0.737 | 0.831 | 8.12 | 6.46 | 8.68 | 0.727 | 0.865 | 0.885 | 5.45 | 7.85 | 7.21 | 0.735 | 0.731 | 0.885 | -6.61 | 7.75 | -6.55 | Very Poor_Mixed | 736.7 | 1200 | 1.05 | 0.954 | 9.58 | 0.885 | 8.68 | 0.143 | 0.6435 | 0.1941 | 0.2943 | 1 | 0.0944 | 0.2592 | 0.367 | 0.367 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
123 | 485.6 | 255.2 | 80.6 | 84.4 | 2.7 | 559.6 | 3531.6 | 54.2 | 26.9 | 78.5 | 79.5 | 73 | 83.1 | 37.5 | 12.4 | 2300.5 | 1801.1 | 2615.1 | 2657.5 | 1990.9 | 3254.8 | 1.155 | 1.105 | 1.245 | 0.691 | 0.721 | 0.698 | 5.46 | 5.17 | 5.72 | 0.543 | 2.11 | 0.587 | -3.33 | 2.96 | 3.82 | 0.547 | 0.595 | 0.575 | 3.63 | 3.65 | 3.61 | 0.578 | 0.575 | 0.594 | -3.59 | 2.17 | 2.89 | Critical_IR_PI | 1801.1 | 1990.9 | 1.105 | 0.721 | 5.72 | 2.11 | 3.82 | 0.7547 | 0.8397 | 0.843 | 0.9575 | 1 | 0.4608 | 0.6374 | 0.7609 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
124 | 526.8 | 366.2 | 81.3 | 98.5 | 4.1 | 493.3 | 3867.1 | 58.4 | 24.3 | 83.6 | 82.2 | 78.2 | 91.7 | 38.5 | 16.3 | 8576.5 | 7906 | 8832 | 16608.8 | 6455.1 | 16233.2 | 1.937 | 0.816 | 1.838 | 0.949 | 0.91 | 0.919 | 9.23 | 8.3 | 8.62 | 0.574 | 0.611 | 0.598 | 3.36 | 4.02 | 4.09 | 0.573 | 0.596 | 0.543 | -2.99 | 3.38 | 3.98 | 0.605 | 0.548 | 0.597 | 2.79 | 3.31 | 3.6 | Critical_Winding_TD_Cap | 7906 | 6455.1 | 0.816 | 0.949 | 9.23 | 0.611 | 4.09 | 0.7039 | 0.8821 | 0.6896 | 0.8578 | 0.8187 | 0.1134 | 0.6644 | 0.6602 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_LV
125 | 1425.2 | 856.7 | 129.8 | 178.4 | 26.9 | 1148.1 | 7341.6 | 37.4 | 43.1 | 101.7 | 100.2 | 88.8 | 107.6 | 42.8 | 32.8 | 3313.8 | 2911.4 | 1778.2 | 4380 | 3508.3 | 2061.4 | 1.322 | 1.205 | 1.159 | 0.891 | 0.876 | 0.894 | 8.27 | -8.28 | 9.07 | 0.881 | 0.759 | 0.859 | 7.85 | 6.1 | -5.38 | 0.808 | 0.892 | 0.745 | 6.23 | 7.13 | 7.61 | 0.794 | 0.688 | 0.859 | 7.11 | 7.09 | -7.04 | Very Poor_Mixed | 1778.2 | 2061.4 | 1.159 | 0.894 | 9.07 | 0.892 | 7.85 | 0.1761 | 0.6484 | 0.2793 | 0.2904 | 1 | 0.1495 | 0.2653 | 0.393 | 0.393 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
126 | 493.7 | 380.5 | 84.1 | 83.9 | 2.8 | 576.1 | 4363 | 55 | 24.5 | 81.6 | 79.8 | 75.9 | 84.3 | 35.9 | 15 | 690 | 2220.6 | 1236.3 | 749.7 | 2664.4 | 1261 | 1.087 | 1.2 | 1.02 | 0.73 | 0.679 | 0.697 | 4.93 | -17.08 | -5.26 | 0.582 | 0.588 | 0.545 | -2.95 | -2.31 | 3.05 | 0.51 | 0.612 | 0.586 | 3.09 | 3.61 | 3.32 | 0.546 | 0.548 | 0.562 | 3.11 | 3.03 | -3.63 | Critical_IR_PI | 690 | 749.7 | 1.02 | 0.73 | 17.08 | 0.612 | 3.63 | 0.7265 | 0.8786 | 0.7927 | 0.8935 | 0.925 | 0.3966 | 0.7192 | 0.744 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_LV_CapChange_pct
127 | 535.5 | 272.7 | 78.9 | 84.2 | 2.8 | 3200.8 | 14279 | 59 | 23.6 | 85.9 | 85.8 | 77.8 | 95.2 | 38.8 | 13.8 | 9063.2 | 9201.5 | 8494.4 | 18036.9 | 17195.8 | 16144.7 | 1.99 | 1.869 | 1.901 | 0.99 | 0.99 | 0.955 | 9.42 | -9.61 | 9.75 | 0.612 | 0.605 | 0.557 | 3.09 | 3.84 | 3.78 | 0.627 | 0.52 | 0.594 | -4.03 | 2.92 | 3.44 | 0.625 | 0.557 | 0.603 | 2.98 | 3.07 | -3.28 | Critical_Winding_TD_Cap | 8494.4 | 16144.7 | 1.869 | 0.99 | 9.75 | 0.627 | 4.03 | 0.5715 | 0.895 | 0.6289 | 0.9244 | 1 | 0.0343 | 0.6629 | 0.6435 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
128 | 205.6 | 120 | 65 | 54.5 | 1 | 350 | 3207.4 | 58.8 | 20 | 76.6 | 77 | 70 | 80 | 35 | 10 | 10000 | 9377.9 | 9409.1 | 20000 | 17868.9 | 18674.4 | 2 | 1.905 | 1.985 | 0.538 | 0.547 | 0.563 | 2.47 | 3.01 | 2.91 | 0.5 | 0.508 | 0.5 | 2 | 2.56 | 2.3 | 0.519 | 0.514 | 0.519 | 2 | 2.31 | 2 | 0.527 | 0.527 | 0.5 | 2 | 2.09 | 2.51 | Good_Mixed | 9377.9 | 17868.9 | 1.905 | 0.563 | 3.01 | 0.527 | 2.56 | 0.972 | 1 | 0.9461 | 1 | 1 | 0.8023 | 0.9107 | 0.9438 | 0.9438 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
129 | 100 | 168.1 | 65.1 | 51.6 | 2.9 | 350 | 2761.8 | 42.3 | 37.9 | 77.2 | 76.6 | 72.7 | 85.8 | 36 | 11.7 | 7468.6 | 6263 | 5663.4 | 13074.3 | 10393.9 | 9412.8 | 1.751 | 1.66 | 1.662 | 0.59 | 0.615 | 0.625 | -3.3 | 3.69 | 3.76 | 0.564 | 0.529 | 0.565 | 2.45 | -2.77 | 2.75 | 0.511 | 0.594 | 0.506 | 3.25 | -2 | -2.95 | 0.556 | 0.5 | 0.557 | 2.49 | -2.7 | -2.41 | Poor_Oil | 5663.4 | 9412.8 | 1.66 | 0.625 | 3.76 | 0.594 | 3.25 | 0.9001 | 0.7021 | 0.8819 | 0.9724 | 1 | 0.6675 | 0.8006 | 0.8436 | 0.8436 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
130 | 1009.4 | 605.9 | 104.6 | 122.7 | 23.4 | 866.1 | 4977 | 46.7 | 30.7 | 93.8 | 89.6 | 82.2 | 100.4 | 40.1 | 26.1 | 5399.9 | 4694.8 | 5010.8 | 8037 | 6927.4 | 7598.8 | 1.488 | 1.476 | 1.516 | 0.732 | 0.77 | 0.75 | 5.83 | 6.63 | 6.05 | 0.633 | 0.713 | 0.685 | -4.66 | 4.11 | 3 | 0.67 | 0.673 | 0.659 | 5.21 | 4.75 | -5.91 | 0.615 | 0.72 | 0.654 | 4.42 | 3.51 | 4.96 | Poor_Mixed | 4694.8 | 6927.4 | 1.476 | 0.77 | 6.63 | 0.72 | 5.91 | 0.3805 | 0.7868 | 0.4866 | 0.5407 | 1 | 0.3794 | 0.4989 | 0.5682 | 0.5682 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
131 | 1730.5 | 912.7 | 137.1 | 185.5 | 34.3 | 1314.5 | 8683.5 | 30.6 | 45.9 | 106.1 | 107 | 95 | 116 | 45 | 33.7 | 2314.3 | 1190.5 | 1752.3 | 2494.6 | 1413.4 | 1978.1 | 1.078 | 1.187 | 1.129 | 0.99 | 0.99 | 0.965 | 9.52 | 9.63 | 8.7 | 0.756 | 0.772 | 0.917 | 8.27 | 7.56 | 6.79 | 0.756 | 0.711 | 0.769 | 6.65 | -5.7 | 6.69 | 0.787 | 0.723 | 0.805 | 7.73 | 7.12 | 5.31 | Very Poor_Mixed | 1190.5 | 1413.4 | 1.078 | 0.99 | 9.63 | 0.917 | 8.27 | 0.067 | 0.6213 | 0.1231 | 0.2552 | 1 | 0.0476 | 0.2951 | 0.3361 | 0.3361 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
132 | 898.8 | 493.5 | 98.3 | 117.5 | 14.8 | 795.4 | 5170.5 | 45.9 | 36.2 | 91.3 | 92.5 | 82.6 | 98.3 | 40.8 | 25.6 | 6801.2 | 5598.2 | 5370.6 | 10990.6 | 8772.2 | 7958.4 | 1.616 | 1.567 | 1.482 | 0.706 | 0.697 | 0.701 | 5.48 | 6.02 | -5.4 | 0.681 | 0.629 | 0.741 | 4.9 | 5.66 | -5.2 | 0.657 | 0.715 | 0.676 | 3.81 | 4.83 | -5.14 | 0.664 | 0.661 | 0.721 | -3.63 | 5 | 5.15 | Poor_Mixed | 5370.6 | 7958.4 | 1.482 | 0.706 | 6.02 | 0.741 | 5.66 | 0.4701 | 0.7208 | 0.487 | 0.5584 | 1 | 0.4523 | 0.4698 | 0.5885 | 0.5885 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
133 | 883.7 | 475.3 | 105.9 | 112 | 20.2 | 852 | 5082.8 | 45.2 | 34.1 | 88.7 | 91 | 79.2 | 95.8 | 39.7 | 24.9 | 5486.3 | 5351.1 | 4994.2 | 8230 | 8169.4 | 7191.8 | 1.5 | 1.527 | 1.44 | 0.734 | 0.709 | 0.736 | 5.68 | 5.04 | -5.27 | 0.635 | 0.687 | 0.665 | 4.61 | -4.01 | 5.99 | 0.59 | 0.668 | 0.613 | 4.1 | 4.09 | 5.31 | 0.574 | 0.754 | 0.662 | 4.03 | -4.75 | 4.99 | Poor_Mixed | 4994.2 | 7191.8 | 1.44 | 0.736 | 5.68 | 0.754 | 5.99 | 0.4329 | 0.7449 | 0.5558 | 0.5831 | 1 | 0.4468 | 0.5211 | 0.5987 | 0.5987 | Poor | 0 | 1 | DGA | 0 |  | C2H2
134 | 1630 | 916.2 | 144 | 182 | 30.9 | 1345.5 | 8403.1 | 33.1 | 46 | 104.8 | 104.4 | 93.4 | 114.9 | 44.5 | 28.6 | 3168.4 | 2127.5 | 2062.1 | 3947.7 | 2540.3 | 2547.5 | 1.246 | 1.194 | 1.235 | 0.894 | 0.922 | 0.922 | 8.52 | 9.71 | -9.46 | 0.855 | 0.886 | 0.76 | 7.34 | 8.19 | 7.2 | 0.867 | 0.885 | 0.836 | -6.61 | -7.9 | 5.7 | 0.82 | 0.768 | 0.855 | 8.15 | 5.59 | 6.22 | Very Poor_Mixed | 2062.1 | 2540.3 | 1.194 | 0.922 | 9.71 | 0.886 | 8.19 | 0.0865 | 0.6203 | 0.1628 | 0.4498 | 1 | 0.0968 | 0.2329 | 0.3503 | 0.3503 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
135 | 1712.5 | 883.1 | 138.1 | 190.8 | 29.9 | 1318.6 | 8469.1 | 34.1 | 47.3 | 105.6 | 105.3 | 93.6 | 118.9 | 44.1 | 33.9 | 1640.3 | 2282.6 | 1996.6 | 1752 | 2719.6 | 2379.9 | 1.068 | 1.191 | 1.192 | 0.938 | 0.92 | 0.915 | -9.84 | 9.65 | 8.43 | 0.822 | 0.776 | 0.735 | 6.34 | 7.05 | 5.94 | 0.847 | 0.749 | 0.87 | 6.31 | -6.77 | 8.86 | 0.775 | 0.88 | 0.836 | 5.62 | -7.47 | 6.32 | Very Poor_Mixed | 1640.3 | 1752 | 1.068 | 0.938 | 9.84 | 0.88 | 8.86 | 0.0883 | 0.6081 | 0.1351 | 0.2473 | 1 | 0.0849 | 0.2667 | 0.3408 | 0.3408 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
136 | 1554.8 | 980.7 | 140.3 | 189.6 | 31.4 | 1339.1 | 8165.6 | 36.4 | 44.4 | 107.9 | 102.6 | 92.5 | 116.1 | 45.3 | 35 | 1337.1 | 829.1 | 953.5 | 1455.2 | 1200 | 1200 | 1.088 | 1.447 | 1.259 | 0.906 | 0.953 | 0.923 | 9 | 9.1 | 8.4 | 0.928 | 0.8 | 0.912 | 7.53 | 7.01 | 7.21 | 0.825 | 0.73 | 0.934 | 6.94 | 5.07 | 6.22 | 0.775 | 0.857 | 0.91 | -6.27 | 6.06 | 6.09 | Very Poor_Mixed | 829.1 | 1200 | 1.088 | 0.953 | 9.1 | 0.934 | 7.53 | 0.0831 | 0.6357 | 0.1491 | 0.2038 | 1 | 0.1066 | 0.237 | 0.3397 | 0.3397 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
137 | 387.7 | 398.7 | 86.7 | 84.1 | 3.9 | 566.2 | 4144.4 | 52.8 | 26.4 | 78.3 | 82 | 73.5 | 86.7 | 36.3 | 17.6 | 8577.2 | 8091.1 | 8332.8 | 15837.3 | 14754.7 | 15530.5 | 1.846 | 1.824 | 1.864 | 0.99 | 0.99 | 1.114 | -9.52 | 9.53 | 9.84 | 0.521 | 0.524 | 0.5 | 2.1 | 2 | 2 | 0.507 | 0.512 | 0.5 | 2.14 | -2 | -2 | 0.516 | 0.5 | 0.519 | 2.38 | 2.56 | -2 | Critical_Winding_TD_Cap | 8091.1 | 14754.7 | 1.824 | 1.114 | 9.84 | 0.524 | 2.56 | 0.7148 | 0.8474 | 0.808 | 0.8203 | 1 | 0.0226 | 0.9205 | 0.7311 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
138 | 461.2 | 328.7 | 79.2 | 89.6 | 1.4 | 530.6 | 3407.4 | 30.6 | 87.4 | 79.7 | 77.4 | 70 | 81.2 | 35 | 16.6 | 5687.8 | 5627.8 | 5115.5 | 8482.4 | 8266.6 | 7436.3 | 1.491 | 1.469 | 1.454 | 0.639 | 0.708 | 0.651 | -4.69 | 4.96 | 4.17 | 0.548 | 0.578 | 0.596 | 3.46 | 3.07 | 2.97 | 0.618 | 0.629 | 0.605 | 2.89 | -2.94 | 3.02 | 0.565 | 0.592 | 0.595 | 3.96 | -2.67 | 3.19 | Critical_Oil | 5115.5 | 7436.3 | 1.454 | 0.708 | 4.96 | 0.629 | 3.96 | 0.7882 | 0.5833 | 0.905 | 0.8493 | 1 | 0.5458 | 0.6648 | 0.7561 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
139 | 834.5 | 492.1 | 95 | 121.1 | 16.4 | 887.1 | 5198.7 | 48.6 | 34 | 92.2 | 91.9 | 84.7 | 98.4 | 40 | 25.3 | 5704.7 | 5495.7 | 4685 | 8977.7 | 7930.9 | 6754.7 | 1.574 | 1.443 | 1.442 | 0.732 | 0.725 | 0.71 | 5.96 | 5.18 | 5.75 | 0.63 | 0.679 | 0.737 | 5.6 | -3.7 | 4.21 | 0.671 | 0.66 | 0.646 | 4.41 | 5.28 | 4.29 | 0.684 | 0.693 | 0.71 | 4.01 | 5.41 | 4.86 | Poor_Mixed | 4685 | 6754.7 | 1.442 | 0.732 | 5.96 | 0.737 | 5.6 | 0.4517 | 0.7461 | 0.4767 | 0.569 | 1 | 0.4336 | 0.4807 | 0.5858 | 0.5858 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
140 | 648.8 | 317.3 | 84.7 | 86.7 | 8.1 | 662.9 | 3983.8 | 53.3 | 26.1 | 84.7 | 84.2 | 75.3 | 88.4 | 36.4 | 18.1 | 8138 | 7869.7 | 8458.3 | 14814.5 | 13635.9 | 14887.8 | 1.82 | 1.733 | 1.76 | 0.571 | 0.561 | 0.597 | 3.07 | 2.5 | 3.86 | 0.557 | 0.587 | 0.543 | 3.14 | 3.43 | 4.2 | 0.619 | 0.608 | 0.586 | -3.18 | 4.1 | 3.83 | 0.561 | 0.587 | 0.636 | 4.29 | 3.5 | 3.21 | Fair_Mixed | 7869.7 | 13635.9 | 1.733 | 0.597 | 3.86 | 0.636 | 4.29 | 0.6352 | 0.852 | 0.7149 | 0.8054 | 1 | 0.7399 | 0.6515 | 0.7537 | 0.7537 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
141 | 1657.3 | 875.9 | 132.9 | 174.7 | 31.9 | 1221.5 | 7893.5 | 37 | 43 | 102.4 | 106.2 | 93.3 | 112.9 | 43.7 | 31.4 | 2429.2 | 1203.8 | 3027.3 | 2987.3 | 1371.4 | 3875.4 | 1.23 | 1.139 | 1.28 | 0.936 | 0.904 | 0.887 | 8.92 | 8.41 | 8.7 | 0.759 | 0.733 | 0.826 | 7.13 | 8.67 | 5.56 | 0.78 | 0.802 | 0.902 | -8.21 | 7.37 | 7.15 | 0.79 | 0.823 | 0.708 | -6.19 | 8.19 | 6.24 | Very Poor_Mixed | 1203.8 | 1371.4 | 1.139 | 0.936 | 8.92 | 0.902 | 8.67 | 0.1195 | 0.6494 | 0.1827 | 0.3444 | 1 | 0.1271 | 0.2704 | 0.3698 | 0.3698 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
142 | 917.2 | 523.9 | 106.8 | 119.9 | 18 | 881.1 | 5069.1 | 43.7 | 35.8 | 95.2 | 92.5 | 82.3 | 102.1 | 39.5 | 24 | 4980.5 | 4847.4 | 5228 | 7541 | 6956.7 | 7870.1 | 1.514 | 1.435 | 1.505 | 0.763 | 0.745 | 0.781 | 6.67 | 5.45 | -6.69 | 0.758 | 0.772 | 0.709 | 5.23 | -4.39 | -5.66 | 0.655 | 0.619 | 0.648 | 4.94 | -3.88 | 5.72 | 0.664 | 0.674 | 0.648 | 4.84 | -6.09 | 5.83 | Poor_Mixed | 4847.4 | 6956.7 | 1.435 | 0.781 | 6.69 | 0.772 | 6.09 | 0.4262 | 0.7253 | 0.4537 | 0.6143 | 1 | 0.3638 | 0.458 | 0.563 | 0.563 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
143 | 245.8 | 132.9 | 68.9 | 58.3 | 6.7 | 431 | 2934.4 | 56.9 | 22.9 | 77 | 75.4 | 71.5 | 80.4 | 36.3 | 12.9 | 10000 | 8764.2 | 9423.9 | 20000 | 17019.9 | 18451.6 | 2 | 1.942 | 1.958 | 0.5 | 0.5 | 0.503 | 2 | -2 | 3 | 0.523 | 0.59 | 0.553 | -2.19 | 2.17 | -2.01 | 0.545 | 0.516 | 0.504 | 2 | 2.97 | 2 | 0.555 | 0.549 | 0.532 | -2.7 | 2 | 2.3 | Good_Mixed | 8764.2 | 17019.9 | 1.942 | 0.503 | 3 | 0.59 | 2.97 | 0.7978 | 0.9088 | 0.9365 | 0.9461 | 1 | 0.9653 | 0.8163 | 0.8915 | 0.8915 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
144 | 909.4 | 530.8 | 99.4 | 118.8 | 19.1 | 836.9 | 5131.8 | 47.1 | 34.2 | 89.9 | 87.5 | 81.5 | 98.9 | 40.2 | 24.2 | 6100.8 | 5436.9 | 5115.3 | 9428.4 | 7965.7 | 7583.5 | 1.545 | 1.465 | 1.483 | 0.683 | 0.733 | 0.758 | 5.44 | -5.94 | -6.24 | 0.593 | 0.612 | 0.614 | 4.03 | 4 | 4.64 | 0.661 | 0.722 | 0.589 | 4.11 | 4.28 | 4.28 | 0.705 | 0.669 | 0.709 | 4.33 | 3.39 | 5.02 | Poor_Mixed | 5115.3 | 7583.5 | 1.465 | 0.758 | 6.24 | 0.722 | 5.02 | 0.4305 | 0.7438 | 0.5373 | 0.6074 | 1 | 0.4188 | 0.5327 | 0.5955 | 0.5955 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
145 | 1352.1 | 762.5 | 134.8 | 171.3 | 33.4 | 1122 | 7720.9 | 36.5 | 44.2 | 102.7 | 103.3 | 91.6 | 113.6 | 43.4 | 35.1 | 463.3 | 800.1 | 2502.6 | 734 | 908.4 | 2960.8 | 1.584 | 1.135 | 1.183 | 0.874 | 0.876 | 0.905 | -7.8 | 8.01 | 8.16 | 0.704 | 0.697 | 0.776 | -5.47 | 7.02 | -7.64 | 0.762 | 0.807 | 0.798 | 7.57 | 7.96 | 6.25 | 0.743 | 0.829 | 0.784 | 7 | 6.53 | 6.77 | Critical_Mixed | 463.3 | 734 | 1.135 | 0.905 | 8.16 | 0.829 | 7.96 | 0.1619 | 0.6376 | 0.2054 | 0.1998 | 0.775 | 0.1791 | 0.3035 | 0.3512 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
146 | 1690.4 | 968.6 | 147.8 | 194.8 | 34.3 | 1351.5 | 8588.7 | 59.1 | 85.7 | 81.7 | 77.9 | 75.8 | 87.9 | 36.8 | 14.9 | 9310.6 | 10000 | 8829.5 | 18173.9 | 20000 | 17057.2 | 1.952 | 2 | 1.932 | 0.609 | 0.612 | 0.583 | 3.63 | 3.29 | 3.82 | 0.582 | 0.556 | 0.564 | -2 | 2.5 | 2.79 | 0.511 | 0.518 | 0.535 | 2.48 | 2 | 2.8 | 0.573 | 0.549 | 0.55 | 2 | 2.29 | 2.86 | Critical_DGA | 8829.5 | 17057.2 | 1.932 | 0.612 | 3.82 | 0.582 | 2.86 | 0.0449 | 0.5833 | 0.788 | 0.8962 | 1 | 0.678 | 0.7866 | 0.6013 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
147 | 1667 | 893.2 | 135.9 | 179.5 | 27.3 | 1266.9 | 7984.5 | 33.8 | 46.1 | 105 | 103.3 | 93.8 | 112.2 | 43.8 | 31.3 | 909.1 | 1273.9 | 690 | 1200 | 1337.6 | 1200 | 1.32 | 1.05 | 1.739 | 0.952 | 0.926 | 0.927 | 8.83 | -8.59 | -9.24 | 0.782 | 0.797 | 0.804 | 6.54 | -7.13 | -5.71 | 0.868 | 0.7 | 0.823 | 6.68 | 8.18 | 6.27 | 0.754 | 0.835 | 0.866 | 8.69 | 8.25 | 6.18 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.952 | 9.24 | 0.868 | 8.69 | 0.1258 | 0.6194 | 0.1842 | 0.3483 | 1 | 0.0986 | 0.2627 | 0.3627 | 0.3627 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
148 | 1629.2 | 826.8 | 135.3 | 173.3 | 32.2 | 1177 | 7510.4 | 35.7 | 45.4 | 103.6 | 108 | 92.9 | 112.6 | 44.1 | 31.9 | 2486.9 | 3621.1 | 3029.8 | 3118.5 | 4761.3 | 3809.4 | 1.254 | 1.315 | 1.257 | 0.874 | 0.934 | 0.89 | 8.01 | 8.84 | 8.93 | 0.816 | 0.829 | 0.89 | 7.91 | -5.47 | 7.67 | 0.866 | 0.846 | 0.703 | 7.44 | -6.12 | 5.81 | 0.857 | 0.792 | 0.77 | -8.03 | -5.9 | 6 | Very Poor_Mixed | 2486.9 | 3118.5 | 1.254 | 0.934 | 8.93 | 0.89 | 8.03 | 0.1346 | 0.6261 | 0.1669 | 0.3252 | 1 | 0.1383 | 0.2601 | 0.3679 | 0.3679 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
149 | 1515.8 | 867.8 | 133.2 | 172.5 | 33.6 | 1234 | 7840.7 | 30.6 | 46.7 | 105.4 | 107.4 | 94.1 | 116.3 | 43.7 | 33.5 | 3426.5 | 690 | 963.5 | 4300.6 | 1200 | 1200 | 1.255 | 1.739 | 1.245 | 0.926 | 0.934 | 0.975 | 8.9 | 9.77 | 9.79 | 0.93 | 0.872 | 0.889 | 7.66 | -8.51 | -5.28 | 0.885 | 0.872 | 0.747 | 7.25 | 8.58 | 5.68 | 0.897 | 0.773 | 0.774 | 9.29 | -8.71 | 8.62 | Very Poor_Mixed | 690 | 1200 | 1.245 | 0.975 | 9.79 | 0.93 | 9.29 | 0.1239 | 0.6137 | 0.1378 | 0.2631 | 1 | 0.0619 | 0.1995 | 0.3361 | 0.3361 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
150 | 1562.4 | 872.4 | 136.5 | 181.3 | 30.5 | 1210.5 | 8127.1 | 33.2 | 50.6 | 104.4 | 102.5 | 90.1 | 111.2 | 41.7 | 35.7 | 2961.8 | 3103.5 | 1886.3 | 3579.6 | 3783.9 | 2147 | 1.209 | 1.219 | 1.138 | 0.841 | 0.851 | 0.832 | 8.15 | 8.25 | 7.36 | 0.86 | 0.904 | 0.848 | 5.34 | -6.51 | 7.8 | 0.825 | 0.83 | 0.73 | 7.74 | 8.15 | 7.65 | 0.65 | 0.821 | 0.906 | 5.61 | 5.71 | -8.21 | Critical_Mixed | 1886.3 | 2147 | 1.138 | 0.851 | 8.25 | 0.906 | 8.21 | 0.1228 | 0.5833 | 0.2328 | 0.1758 | 1 | 0.2146 | 0.2537 | 0.3685 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
151 | 1650.7 | 893.1 | 143.9 | 179.9 | 28.9 | 1266.3 | 8168 | 32.4 | 49.2 | 104.4 | 103.8 | 92.9 | 114 | 44.2 | 33.8 | 2069.2 | 690 | 2015.6 | 2474.9 | 1200 | 2116.4 | 1.196 | 1.739 | 1.05 | 0.946 | 0.911 | 0.969 | 9.26 | 8.84 | -8.36 | 0.82 | 0.896 | 0.763 | 6.13 | -6.3 | -6.99 | 0.939 | 0.785 | 0.855 | 8.35 | 6.05 | -6.61 | 0.77 | 0.866 | 0.853 | 8.53 | 6.26 | 8.67 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.969 | 9.26 | 0.939 | 8.67 | 0.1103 | 0.5906 | 0.1779 | 0.2513 | 1 | 0.0973 | 0.2285 | 0.3435 | 0.3435 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
152 | 352.6 | 294.9 | 85.1 | 138.1 | 3.9 | 572.7 | 3438.1 | 56.7 | 25.5 | 104.4 | 104.1 | 93 | 114.7 | 44 | 18 | 10000 | 9423.3 | 8357.7 | 18600 | 18188.2 | 15623.5 | 1.86 | 1.93 | 1.869 | 0.623 | 0.577 | 0.551 | -4.06 | 3.7 | 24.89 | 0.5 | 0.507 | 0.5 | -2.16 | 2.47 | -2 | 0.522 | 0.513 | 0.517 | 2.42 | 2.36 | 2.18 | 0.51 | 0.549 | 0.501 | -2.88 | 2.5 | 2.27 | Critical_Thermal | 8357.7 | 15623.5 | 1.86 | 0.623 | 24.89 | 0.549 | 2.88 | 0.681 | 0.8617 | 0.1736 | 0.8084 | 1 | 0.5744 | 0.8988 | 0.7336 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H4
153 | 1466.7 | 799.4 | 135.2 | 167.2 | 27.8 | 1196.5 | 7341.3 | 34.5 | 43 | 103.8 | 103 | 93.5 | 110.6 | 43.9 | 31.3 | 1708.5 | 3002.4 | 3132.7 | 2155.7 | 3884.8 | 4017.1 | 1.262 | 1.294 | 1.282 | 0.918 | 0.92 | 0.877 | 7.82 | -8.38 | -8.01 | 0.831 | 0.799 | 0.789 | 6.76 | -7.27 | 6.56 | 0.839 | 0.87 | 0.813 | 8.48 | 7.37 | 6.47 | 0.888 | 0.832 | 0.741 | 7.26 | -4.38 | 4.92 | Very Poor_Mixed | 1708.5 | 2155.7 | 1.262 | 0.92 | 8.38 | 0.888 | 8.48 | 0.1747 | 0.6494 | 0.2016 | 0.3483 | 1 | 0.1609 | 0.2594 | 0.3884 | 0.3884 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
154 | 786.2 | 514 | 107.6 | 109.2 | 17.3 | 876.5 | 6033.7 | 55.9 | 21.8 | 78.4 | 76.3 | 76.4 | 88.2 | 36.4 | 15.7 | 8528.7 | 10000 | 9229.6 | 16058 | 19505.9 | 18459.3 | 1.883 | 1.951 | 2 | 0.573 | 0.529 | 0.573 | 2.71 | 2 | -2.72 | 0.553 | 0.544 | 0.566 | -3.33 | 2.96 | -2.08 | 0.579 | 0.592 | 0.646 | 2.82 | 2.37 | -2 | 0.552 | 0.558 | 0.521 | 3.09 | 3.07 | -2.04 | Poor_DGA | 8528.7 | 16058 | 1.883 | 0.573 | 2.72 | 0.646 | 3.33 | 0.4424 | 0.9331 | 0.8304 | 0.8746 | 1 | 0.8153 | 0.7362 | 0.756 | 0.756 | Fair | 1 | 1 | DGA | 0 |  | C2H2
155 | 109.7 | 222.8 | 71.7 | 71.4 | 1.1 | 432.5 | 3258.4 | 53.7 | 26.5 | 84.4 | 75 | 70 | 83.3 | 35.4 | 10.5 | 8471.5 | 8255.2 | 8649.8 | 15825.9 | 14041.3 | 16369.6 | 1.868 | 1.701 | 1.892 | 0.842 | 0.823 | 0.834 | 7.24 | 7.24 | -7.65 | 0.594 | 0.529 | 0.568 | 3.64 | -2.41 | 3.49 | 0.599 | 0.548 | 0.628 | 2.54 | 3.31 | -2.73 | 0.563 | 0.56 | 0.57 | 2.13 | -2.39 | 2.78 | Poor_Winding_TD_Cap | 8255.2 | 14041.3 | 1.701 | 0.842 | 7.65 | 0.628 | 3.64 | 0.8997 | 0.8458 | 0.8889 | 0.994 | 1 | 0.2491 | 0.714 | 0.7884 | 0.7884 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
156 | 181 | 139.3 | 65 | 50 | 2.6 | 441.8 | 2500 | 58.8 | 20.3 | 77.6 | 78.6 | 70.4 | 81.9 | 35.6 | 10 | 10000 | 9790.2 | 10000 | 20000 | 19580.5 | 19649.3 | 2 | 2 | 1.965 | 0.507 | 0.515 | 0.5 | 2.67 | -2 | -2.03 | 0.5 | 0.5 | 0.5 | 2.42 | 2.28 | -2.38 | 0.5 | 0.514 | 0.511 | 2.39 | -2.27 | -2 | 0.534 | 0.511 | 0.5 | 2.4 | 2.09 | 2.65 | Good_Mixed | 9790.2 | 19580.5 | 1.965 | 0.515 | 2.67 | 0.534 | 2.65 | 0.886 | 0.9791 | 0.9011 | 1 | 1 | 0.9443 | 0.9304 | 0.9388 | 0.9388 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
157 | 761.6 | 493.4 | 100.6 | 111.7 | 17.3 | 750.5 | 5091.3 | 46.2 | 35 | 88.8 | 95.6 | 82 | 98.5 | 39.4 | 23.2 | 6075 | 5339.7 | 5108.3 | 9351.6 | 8380.4 | 7532.6 | 1.539 | 1.569 | 1.475 | 0.762 | 0.701 | 0.757 | 6.6 | 5.22 | 5.98 | 0.774 | 0.659 | 0.672 | -5.11 | 5.59 | -4.48 | 0.639 | 0.677 | 0.628 | 3.76 | 5.87 | 4.11 | 0.712 | 0.642 | 0.715 | 5.38 | 4.29 | 3.89 | Poor_Mixed | 5108.3 | 7532.6 | 1.475 | 0.762 | 6.6 | 0.774 | 5.87 | 0.475 | 0.7345 | 0.4961 | 0.6416 | 1 | 0.4021 | 0.4782 | 0.5909 | 0.5909 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
158 | 1005.3 | 573.5 | 106.8 | 133.1 | 19.3 | 862.1 | 5930.6 | 60 | 22.2 | 75 | 76.3 | 70.8 | 80 | 35.2 | 11.7 | 10000 | 9850.2 | 9086.3 | 19388.1 | 19476.3 | 17392.1 | 1.939 | 1.977 | 1.914 | 0.57 | 0.509 | 0.585 | 3.03 | 2 | -2.9 | 0.509 | 0.5 | 0.5 | 2.2 | 2 | 2.84 | 0.539 | 0.5 | 0.5 | 2.23 | 2.25 | -2 | 0.508 | 0.51 | 0.5 | -2.04 | 2.38 | 2.15 | Poor_DGA | 9086.3 | 17392.1 | 1.914 | 0.585 | 3.03 | 0.539 | 2.84 | 0.3867 | 0.9238 | 0.9673 | 0.9724 | 1 | 0.8161 | 0.9393 | 0.7962 | 0.7962 | Fair | 1 | 1 | DGA | 0 |  | C2H2
159 | 431.6 | 245.6 | 78.9 | 85.7 | 1.4 | 484.3 | 3389.2 | 57.8 | 21.6 | 77.6 | 79.5 | 73.8 | 84.8 | 36 | 12.7 | 9137.6 | 9017.6 | 9304.2 | 17355.8 | 16533.3 | 17327.1 | 1.899 | 1.833 | 1.862 | 0.814 | 0.775 | 0.862 | 6.61 | -6.51 | -6.7 | 0.524 | 0.535 | 0.54 | 2.68 | 2 | 2.9 | 0.528 | 0.577 | 0.505 | 2.15 | 2.98 | -2.56 | 0.505 | 0.519 | 0.543 | 3.13 | 3.28 | 2.13 | Poor_Winding_TD_Cap | 9017.6 | 16533.3 | 1.833 | 0.862 | 6.7 | 0.577 | 3.28 | 0.8125 | 0.938 | 0.8446 | 0.9507 | 1 | 0.3026 | 0.8209 | 0.7978 | 0.7978 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
160 | 882.4 | 543.1 | 104.2 | 117.9 | 14.8 | 918.6 | 5454.1 | 47.5 | 33.8 | 90.8 | 89.7 | 83.2 | 100.8 | 41.1 | 26.6 | 5683.1 | 5729.8 | 6115.7 | 8406 | 9110 | 9720.3 | 1.479 | 1.59 | 1.589 | 0.718 | 0.744 | 0.755 | 6.11 | 5.89 | 5.28 | 0.682 | 0.728 | 0.548 | -4.19 | 4.33 | 4.1 | 0.619 | 0.636 | 0.552 | 4.58 | 5.24 | 4.5 | 0.579 | 0.612 | 0.666 | -4.24 | 4.27 | 3.53 | Poor_Mixed | 5683.1 | 8406 | 1.479 | 0.755 | 6.11 | 0.728 | 5.24 | 0.4431 | 0.7485 | 0.4902 | 0.5228 | 1 | 0.4119 | 0.5714 | 0.5963 | 0.5963 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
161 | 779.4 | 503.2 | 100.5 | 108.6 | 14.7 | 777.9 | 4711.4 | 48.9 | 30.7 | 85.6 | 85.5 | 75.9 | 93.6 | 38.1 | 22.4 | 6176 | 6218.2 | 7288.4 | 9923.9 | 9215.8 | 12303.7 | 1.607 | 1.482 | 1.688 | 0.721 | 0.662 | 0.721 | 5.28 | -4.89 | 5.4 | 0.594 | 0.566 | 0.636 | -4.4 | 3.92 | 5.51 | 0.648 | 0.7 | 0.668 | 3.33 | -4.22 | 5.33 | 0.682 | 0.602 | 0.579 | 4.78 | 5.13 | 3.77 | Poor_Mixed | 6176 | 9215.8 | 1.482 | 0.721 | 5.4 | 0.7 | 5.51 | 0.4931 | 0.7868 | 0.6591 | 0.6686 | 1 | 0.4779 | 0.5536 | 0.6436 | 0.6436 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
162 | 445.5 | 297.5 | 73.1 | 147.7 | 1 | 499.1 | 3721.8 | 53.1 | 65.4 | 103.5 | 99.8 | 94.8 | 110.5 | 42.7 | 12.1 | 9578.7 | 9151.8 | 8865.1 | 17887.9 | 16675 | 16476.8 | 1.867 | 1.822 | 1.859 | 0.562 | 0.551 | 0.56 | -3.2 | -3.16 | -2.99 | 0.587 | 0.558 | 0.598 | -4.53 | 3.56 | 2.55 | 0.629 | 0.587 | 0.583 | 3.28 | 3 | -2.72 | 0.598 | 0.594 | 0.583 | -3.4 | 3.88 | 2.76 | Critical_Thermal | 8865.1 | 16476.8 | 1.822 | 0.562 | 3.2 | 0.629 | 4.53 | 0.7857 | 0.5833 | 0.2235 | 0.964 | 1 | 0.7665 | 0.6585 | 0.7228 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
163 | 140.3 | 120 | 72.7 | 53.8 | 1 | 393.1 | 2650.1 | 57.6 | 21.4 | 76.5 | 78.3 | 71.4 | 83.2 | 35.4 | 15 | 9611.4 | 9763.9 | 9867.3 | 18678.7 | 19527.8 | 18702.5 | 1.943 | 2 | 1.895 | 0.5 | 0.5 | 0.559 | 2 | -2.26 | -3.16 | 0.5 | 0.554 | 0.54 | 2.37 | -2.4 | 3.17 | 0.542 | 0.507 | 0.539 | 2.11 | 2.06 | 2 | 0.536 | 0.508 | 0.549 | 2 | 3.18 | 2.71 | Fair_Age | 9611.4 | 18678.7 | 1.895 | 0.559 | 3.16 | 0.554 | 3.18 | 0.9689 | 0.9432 | 0.8994 | 0.8935 | 1 | 0.9121 | 0.8365 | 0.9283 | 0.9283 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
164 | 1645.5 | 844.2 | 135.9 | 179.1 | 31.2 | 1183.7 | 8324.5 | 33.1 | 47.1 | 105 | 102.1 | 92.2 | 112 | 43.4 | 31 | 2256.8 | 1596.1 | 1787.5 | 2528.2 | 1792.4 | 2007.3 | 1.12 | 1.123 | 1.123 | 0.942 | 0.931 | 0.939 | 8.59 | 9.11 | 9.59 | 0.709 | 0.745 | 0.768 | 6.59 | 6.18 | 7.65 | 0.773 | 0.887 | 0.857 | 8.02 | -6.83 | 7.99 | 0.738 | 0.712 | 0.838 | 8.31 | -6.45 | 6.8 | Very Poor_Mixed | 1596.1 | 1792.4 | 1.12 | 0.942 | 9.59 | 0.887 | 8.31 | 0.1195 | 0.61 | 0.2039 | 0.3597 | 1 | 0.0864 | 0.281 | 0.3641 | 0.3641 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
165 | 485.6 | 324 | 83.9 | 87.2 | 4.5 | 604 | 3879.9 | 31.1 | 48.8 | 118.3 | 79.2 | 74.4 | 85.7 | 36.9 | 17.4 | 4888.5 | 4763.4 | 4694.6 | 7523.1 | 6383.1 | 7349 | 1.539 | 1.34 | 1.565 | 0.711 | 0.703 | 0.632 | 4.32 | 5.05 | 4.5 | 0.548 | 0.629 | 0.546 | -3.27 | -4.1 | 2.58 | 0.582 | 0.624 | 0.636 | -2.74 | 3.97 | 3.24 | 0.622 | 0.629 | 0.563 | 3.7 | 4.28 | 3.51 | Critical_Oil | 4694.6 | 6383.1 | 1.34 | 0.711 | 5.05 | 0.636 | 4.28 | 0.7004 | 0.5942 | 0.6191 | 0.8262 | 1 | 0.5295 | 0.643 | 0.6995 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature | Moisture_PPM
166 | 706.6 | 448.1 | 94.3 | 113.4 | 14.8 | 737.4 | 5107.3 | 47.9 | 30.7 | 90.8 | 88.2 | 78.7 | 94.6 | 39.2 | 21.5 | 6132.1 | 6373.4 | 6697.7 | 9928.8 | 10886.1 | 11028.9 | 1.619 | 1.708 | 1.647 | 0.647 | 0.68 | 0.692 | -3.93 | 4.6 | 5.06 | 0.663 | 0.679 | 0.606 | 5.02 | 4.44 | -4.12 | 0.728 | 0.667 | 0.611 | -3.43 | -4.88 | 4.07 | 0.591 | 0.604 | 0.648 | -4.67 | -4.31 | 5.23 | Poor_Mixed | 6132.1 | 9928.8 | 1.619 | 0.692 | 5.06 | 0.728 | 5.23 | 0.5055 | 0.7868 | 0.573 | 0.6984 | 1 | 0.5429 | 0.5341 | 0.6452 | 0.6452 | Fair | 1 | 1 | DGA | 0 |  | C2H2
167 | 653.3 | 438.3 | 96.7 | 111.3 | 14.1 | 694.3 | 4704.2 | 58.2 | 23.7 | 75 | 77.7 | 73.6 | 83.9 | 35.7 | 11.5 | 9115.9 | 8636.8 | 8398.1 | 18107.6 | 16031.4 | 15850.8 | 1.986 | 1.856 | 1.887 | 0.553 | 0.566 | 0.544 | 3.41 | 2.44 | 2.59 | 0.5 | 0.536 | 0.542 | 2.43 | 2.33 | -2.25 | 0.522 | 0.546 | 0.505 | 2.11 | 2.07 | -2.53 | 0.574 | 0.589 | 0.5 | 2.67 | 2.09 | 3.04 | Fair_DGA | 8398.1 | 15850.8 | 1.856 | 0.566 | 3.41 | 0.589 | 3.04 | 0.5259 | 0.8931 | 0.9047 | 0.9764 | 1 | 0.7936 | 0.8379 | 0.7999 | 0.7999 | Fair | 1 | 1 | DGA | 0 |  | C2H2
168 | 1481.7 | 861.9 | 138.3 | 178.9 | 31.9 | 1180.2 | 7617 | 34.9 | 43 | 103.6 | 102.4 | 90.6 | 110.1 | 44.4 | 28.7 | 2903.7 | 2610.4 | 2849.7 | 3482.9 | 3179.9 | 3538.6 | 1.199 | 1.218 | 1.242 | 0.893 | 0.904 | 0.911 | 7.8 | 8.45 | -8.82 | 0.807 | 0.919 | 0.829 | 7.79 | 6.34 | 6.97 | 0.788 | 0.809 | 0.916 | 7.83 | 7.82 | 7.86 | 0.939 | 0.869 | 0.831 | 6.19 | -8.17 | 5.57 | Very Poor_Mixed | 2610.4 | 3179.9 | 1.199 | 0.911 | 8.82 | 0.939 | 8.17 | 0.1339 | 0.6494 | 0.2214 | 0.4461 | 1 | 0.1478 | 0.2095 | 0.3743 | 0.3743 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
169 | 100 | 133.7 | 68.3 | 51 | 3.4 | 350 | 2500 | 58.3 | 22.2 | 77.6 | 76.4 | 70.6 | 82 | 35 | 13.8 | 8631.3 | 8272.5 | 9014 | 16038.4 | 15465.8 | 16800.1 | 1.858 | 1.87 | 1.864 | 0.572 | 0.5 | 0.553 | 3.44 | -2 | -2.7 | 0.5 | 0.54 | 0.522 | 2.17 | 2 | 2 | 0.521 | 0.5 | 0.547 | -2 | 2.01 | 2 | 0.517 | 0.5 | 0.5 | -2 | 2 | 2.25 | Good_Mixed | 8272.5 | 15465.8 | 1.858 | 0.572 | 3.44 | 0.547 | 2.25 | 0.8959 | 0.9238 | 0.9233 | 0.9244 | 1 | 0.8422 | 0.916 | 0.9161 | 0.9161 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
170 | 1654.1 | 982.4 | 137.1 | 191.4 | 34.3 | 1305.9 | 8645.6 | 33.6 | 47.3 | 104.1 | 107 | 96.1 | 118 | 44.2 | 32.9 | 1255.8 | 2042 | 2391.3 | 1318.6 | 2377.6 | 2809.1 | 1.05 | 1.164 | 1.175 | 0.913 | 0.907 | 0.916 | 9.51 | 8.64 | 8.31 | 0.767 | 0.893 | 0.734 | 8.09 | 7.1 | 7.32 | 0.886 | 0.868 | 0.832 | -7 | -9.82 | 7.39 | 0.808 | 0.854 | 0.741 | -8.57 | 4.76 | 6.01 | Very Poor_Mixed | 1255.8 | 1318.6 | 1.05 | 0.916 | 9.51 | 0.893 | 9.82 | 0.0614 | 0.6081 | 0.124 | 0.2865 | 1 | 0.1178 | 0.2384 | 0.3345 | 0.3345 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
171 | 949.2 | 498.1 | 103.3 | 116 | 15.5 | 828.4 | 5631.8 | 45.2 | 33.2 | 93.3 | 92.8 | 82.9 | 100.3 | 40.2 | 25.7 | 5668 | 5529.1 | 6060.3 | 8811.3 | 8573.7 | 9139.1 | 1.555 | 1.551 | 1.508 | 0.732 | 0.707 | 0.695 | 5.69 | 5.17 | 4.95 | 0.661 | 0.635 | 0.681 | -4.67 | 5.66 | 4.92 | 0.663 | 0.708 | 0.665 | 6.18 | 3.64 | 4.56 | 0.7 | 0.67 | 0.734 | 6.45 | 5.23 | 5.9 | Poor_Mixed | 5529.1 | 8573.7 | 1.508 | 0.732 | 5.69 | 0.734 | 6.45 | 0.4498 | 0.7556 | 0.4644 | 0.5549 | 1 | 0.4637 | 0.4576 | 0.5846 | 0.5846 | Poor | 0 | 1 | DGA | 0 |  | C2H2
172 | 149.2 | 120 | 65 | 55.2 | 1 | 350 | 2500 | 59.1 | 20.2 | 81.3 | 78.7 | 74.3 | 84.6 | 36.1 | 10 | 9153.1 | 9735.1 | 8626.9 | 17229.4 | 19402.8 | 16288.1 | 1.882 | 1.993 | 1.888 | 0.657 | 0.61 | 0.676 | -4.33 | -4.52 | 4.44 | 0.539 | 0.559 | 0.539 | -2 | 2.35 | -2.08 | 0.5 | 0.5 | 0.528 | 2.28 | 2 | 2 | 0.515 | 0.5 | 0.5 | 2.54 | -2.29 | -2.33 | Fair_Winding_TD_Cap | 8626.9 | 16288.1 | 1.882 | 0.676 | 4.52 | 0.559 | 2.54 | 0.9803 | 0.984 | 0.8149 | 1 | 1 | 0.5748 | 0.8959 | 0.8964 | 0.8964 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
173 | 295 | 244.2 | 69.7 | 73.8 | 2.2 | 399.1 | 3324.8 | 57.7 | 23.2 | 81.3 | 79.7 | 74 | 86.6 | 35.7 | 14.1 | 9038.9 | 10000 | 9042.2 | 17445.2 | 19479 | 18084.3 | 1.93 | 1.948 | 2 | 0.708 | 0.74 | 0.736 | 6.25 | 5.44 | 5.7 | 0.558 | 0.572 | 0.522 | 2.21 | 2.34 | 2.05 | 0.526 | 0.536 | 0.516 | -2.8 | 2.42 | 2.84 | 0.529 | 0.53 | 0.55 | -2.46 | 2.02 | 2.82 | Poor_Winding_TD_Cap | 9038.9 | 17445.2 | 1.93 | 0.74 | 6.25 | 0.572 | 2.84 | 0.8326 | 0.9027 | 0.8 | 0.9169 | 1 | 0.4194 | 0.8074 | 0.8064 | 0.8064 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
174 | 148.3 | 201.1 | 66.5 | 61.4 | 2.8 | 391.8 | 2681.2 | 56.6 | 20.5 | 75.2 | 79.5 | 70.2 | 81.2 | 35 | 12.2 | 9884.2 | 9753.6 | 10000 | 19513.7 | 19036.2 | 19684.6 | 1.974 | 1.952 | 1.968 | 0.505 | 0.557 | 0.5 | 2.16 | 2.65 | -2.77 | 0.547 | 0.549 | 0.513 | -2.5 | -2 | 3.02 | 0.502 | 0.511 | 0.5 | 2 | 2.43 | 2.13 | 0.5 | 0.521 | 0.5 | 2.51 | 2.1 | -2 | Good_Mixed | 9753.6 | 19036.2 | 1.952 | 0.557 | 2.77 | 0.549 | 3.02 | 0.8627 | 0.9709 | 0.9315 | 0.9618 | 1 | 0.8952 | 0.9006 | 0.9209 | 0.9209 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
175 | 930.7 | 533 | 104.3 | 128.6 | 16.9 | 858.1 | 5467.4 | 46.6 | 33.4 | 89.8 | 92 | 83.4 | 98.4 | 40.7 | 23.6 | 6001.2 | 6228 | 5017.7 | 9141.4 | 10029.6 | 7125.2 | 1.523 | 1.61 | 1.42 | 0.716 | 0.782 | 0.745 | -5.47 | -5.39 | 6.4 | 0.713 | 0.654 | 0.618 | 5.46 | 5.18 | 4.48 | 0.685 | 0.688 | 0.69 | 5.3 | 4.64 | -5.46 | 0.691 | 0.688 | 0.657 | 4.92 | 3.9 | -5.14 | Poor_Mixed | 5017.7 | 7125.2 | 1.42 | 0.782 | 6.4 | 0.713 | 5.46 | 0.4233 | 0.7532 | 0.4952 | 0.628 | 1 | 0.4053 | 0.4726 | 0.5789 | 0.5789 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
176 | 1554.7 | 967.2 | 140 | 189.8 | 32 | 1271.3 | 8026.9 | 36.4 | 44.2 | 107.6 | 107.8 | 93.4 | 115.8 | 44.6 | 33 | 2938.7 | 3556.1 | 1795.2 | 3366.4 | 4267.4 | 2092.4 | 1.146 | 1.2 | 1.166 | 0.958 | 0.931 | 0.906 | 9.3 | -9.06 | 9.2 | 0.795 | 0.736 | 0.76 | 7.2 | 5.89 | 5.62 | 0.755 | 0.789 | 0.882 | 7.4 | 6.39 | -8.18 | 0.917 | 0.812 | 0.872 | 7.24 | 6.62 | -5.91 | Very Poor_Mixed | 1795.2 | 2092.4 | 1.146 | 0.958 | 9.3 | 0.917 | 8.18 | 0.0911 | 0.6376 | 0.1234 | 0.2826 | 1 | 0.0858 | 0.2651 | 0.3455 | 0.3455 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
177 | 1522.5 | 835.6 | 130.5 | 178.1 | 27.6 | 1191.2 | 7686.8 | 35.9 | 44.2 | 104.2 | 107.1 | 92.4 | 115.2 | 43 | 30.1 | 2404 | 1110.6 | 771.4 | 2774.9 | 1231.7 | 1200 | 1.154 | 1.109 | 1.556 | 0.977 | 0.958 | 0.908 | 9.58 | -9.32 | 8.42 | 0.811 | 0.781 | 0.8 | -9.32 | 6.97 | 5.44 | 0.849 | 0.932 | 0.815 | 6.68 | 7.9 | 6.73 | 0.684 | 0.842 | 0.798 | 8.15 | -6.46 | 5.99 | Very Poor_Mixed | 771.4 | 1200 | 1.109 | 0.977 | 9.58 | 0.932 | 9.32 | 0.1585 | 0.6376 | 0.1661 | 0.3938 | 1 | 0.0792 | 0.2548 | 0.3694 | 0.3694 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
178 | 1695.5 | 972.1 | 143.7 | 197 | 34.1 | 1316.9 | 8045.5 | 52.6 | 23.4 | 82.1 | 82.8 | 75.5 | 88 | 38.6 | 14.9 | 8752.8 | 8092.3 | 318.2 | 16146.3 | 14041 | 477.4 | 1.845 | 1.735 | 1.5 | 0.534 | 0.563 | 0.517 | 2.4 | 2.58 | 2.56 | 0.5 | 0.525 | 0.575 | 2 | 2.63 | 2.59 | 0.539 | 0.549 | 0.501 | 2 | -2.15 | 2.53 | 0.5 | 0.501 | 0.537 | 3.18 | 2.44 | -2.92 | Critical_DGA | 318.2 | 477.4 | 1.5 | 0.563 | 2.58 | 0.575 | 3.18 | 0.0574 | 0.8988 | 0.7338 | 0.8962 | 0.85 | 0.8445 | 0.8631 | 0.65 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
179 | 332 | 205.4 | 82.1 | 67.7 | 5.6 | 470.9 | 3596.8 | 52.4 | 26.8 | 83.4 | 82.2 | 72.3 | 86.8 | 37 | 15.6 | 8335.1 | 8809.4 | 7971.1 | 14660.3 | 15813.6 | 13877.1 | 1.759 | 1.795 | 1.741 | 0.616 | 0.623 | 0.619 | -3.79 | 4.5 | 4.2 | 0.539 | 0.606 | 0.575 | 2.38 | 2.59 | 2.29 | 0.606 | 0.549 | 0.563 | 2.21 | 2.8 | -3.12 | 0.519 | 0.581 | 0.557 | -2.84 | 2.72 | 3.5 | Fair_Mixed | 7971.1 | 13877.1 | 1.741 | 0.623 | 4.5 | 0.606 | 3.5 | 0.7607 | 0.8412 | 0.7694 | 0.8773 | 1 | 0.6207 | 0.7331 | 0.7908 | 0.7908 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
180 | 342.3 | 266.1 | 73.5 | 71.1 | 1.8 | 419.1 | 3285.9 | 54 | 70.9 | 82.7 | 83.2 | 76.8 | 90 | 37.2 | 13 | 7874 | 7518.8 | 7425.5 | 13856.1 | 13162.1 | 12251.6 | 1.76 | 1.751 | 1.65 | 0.989 | 0.976 | 0.981 | 9.38 | 9.4 | 9.59 | 0.633 | 0.714 | 0.625 | -3.74 | -4.34 | 3.35 | 0.612 | 0.616 | 0.629 | 2.04 | 3.7 | 3.52 | 0.59 | 0.638 | 0.669 | 4.09 | 4.46 | 3.68 | Critical_Winding_TD_Cap | 7425.5 | 12251.6 | 1.65 | 0.989 | 9.59 | 0.714 | 4.46 | 0.8352 | 0.5833 | 0.7145 | 0.9438 | 1 | 0.0386 | 0.5768 | 0.6667 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
181 | 332.3 | 240.3 | 76.9 | 78.1 | 7.1 | 427 | 3301.5 | 56.8 | 25.3 | 81.1 | 83.1 | 73.1 | 88.1 | 37.7 | 15.8 | 6791.6 | 7698.5 | 9202.1 | 11554.2 | 13453.9 | 17243.6 | 1.701 | 1.748 | 1.874 | 0.632 | 0.615 | 0.607 | -4.57 | 3.53 | 3.92 | 0.52 | 0.544 | 0.6 | 2.51 | 3.11 | 2.49 | 0.555 | 0.614 | 0.554 | -2.6 | 3.44 | 3 | 0.518 | 0.519 | 0.583 | 3.04 | 2.31 | 4.28 | Fair_Mixed | 6791.6 | 11554.2 | 1.701 | 0.632 | 4.57 | 0.614 | 4.28 | 0.7384 | 0.865 | 0.7633 | 0.8718 | 1 | 0.6321 | 0.7451 | 0.7909 | 0.7909 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
182 | 845.9 | 550.8 | 107.2 | 119.7 | 20.5 | 841.8 | 5849 | 44.8 | 32.4 | 88.1 | 91.6 | 80.4 | 95.2 | 39.2 | 24.6 | 5812.2 | 6685.5 | 6059 | 8990.6 | 11187.2 | 9852.9 | 1.547 | 1.673 | 1.626 | 0.758 | 0.758 | 0.8 | 6.13 | 6.22 | 6.53 | 0.7 | 0.784 | 0.661 | -4.25 | 4.7 | 4.03 | 0.71 | 0.614 | 0.608 | 4.83 | 5.93 | 3.84 | 0.675 | 0.773 | 0.678 | 5.1 | 6.46 | -4.68 | Poor_Mixed | 5812.2 | 8990.6 | 1.547 | 0.8 | 6.53 | 0.784 | 6.46 | 0.4105 | 0.7654 | 0.5541 | 0.5935 | 1 | 0.3549 | 0.4633 | 0.5726 | 0.5726 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
183 | 298.1 | 263.7 | 68.5 | 59.5 | 1.6 | 525.3 | 2825.5 | 35.4 | 44.9 | 77.2 | 79.6 | 72 | 84.3 | 36 | 11.8 | 5136.9 | 5862.6 | 5925 | 7427 | 9171.7 | 3453.8 | 1.446 | 1.564 | 0.583 | 0.637 | 0.63 | 0.643 | 4.65 | 4.25 | 4.35 | 0.571 | 0.57 | 0.553 | 3.4 | 2.69 | 2.82 | 0.517 | 0.556 | 0.557 | 3 | -3.59 | 2 | 0.53 | 0.536 | 0.548 | 2.53 | -2.3 | 3.06 | Critical_Oil | 5136.9 | 3453.8 | 0.583 | 0.643 | 4.65 | 0.571 | 3.59 | 0.8513 | 0.6309 | 0.8658 | 0.9703 | 0.8125 | 0.5863 | 0.7625 | 0.7729 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
184 | 1371.6 | 891.5 | 137.7 | 171.5 | 30 | 1169.9 | 7397.5 | 34.3 | 44 | 102.8 | 103.3 | 89 | 112.3 | 43.2 | 32.8 | 1483.5 | 1404.4 | 2139.1 | 1631.2 | 1544.8 | 2690.1 | 1.1 | 1.1 | 1.258 | 0.93 | 0.913 | 0.935 | -9 | 8.09 | 9.69 | 0.851 | 0.926 | 0.808 | 9.13 | 7.07 | -7.46 | 0.695 | 0.731 | 0.806 | 7.52 | 7.01 | 5.96 | 0.821 | 0.817 | 0.754 | 5.47 | 6.92 | 6.51 | Very Poor_Mixed | 1404.4 | 1544.8 | 1.1 | 0.935 | 9.69 | 0.926 | 9.13 | 0.1579 | 0.6396 | 0.2278 | 0.2904 | 1 | 0.1029 | 0.268 | 0.3762 | 0.3762 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
185 | 1608.2 | 915.5 | 142.4 | 187.1 | 30.2 | 1269.1 | 8046.9 | 33.9 | 46.2 | 108.4 | 107.4 | 96.7 | 117.7 | 44.5 | 35.3 | 1441.4 | 2396.6 | 789.8 | 1586 | 2776.7 | 1200 | 1.1 | 1.159 | 1.519 | 0.92 | 0.973 | 0.942 | 8.32 | 9.58 | -9.13 | 0.985 | 0.708 | 0.912 | -9.84 | -6.02 | 6.3 | 0.842 | 0.952 | 0.943 | -7.71 | 9.54 | 7.11 | 0.889 | 0.901 | 0.976 | 6.52 | 6.89 | -7.48 | Very Poor_Mixed | 789.8 | 1200 | 1.1 | 0.973 | 9.58 | 0.985 | 9.84 | 0.1013 | 0.6184 | 0.0942 | 0.1918 | 1 | 0.0858 | 0.1627 | 0.3199 | 0.3199 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
186 | 473.9 | 295.9 | 83.2 | 82.1 | 39.9 | 582.1 | 3693.9 | 31 | 47.4 | 78.9 | 78.9 | 72.5 | 83.9 | 35.4 | 13.8 | 4796.3 | 5508.3 | 5577.3 | 6973.4 | 8194.9 | 8835.6 | 1.454 | 1.488 | 1.584 | 0.68 | 0.682 | 0.648 | -5.66 | 4.63 | -4.2 | 0.538 | 0.618 | 0.562 | 3.94 | 3.04 | 3.67 | 0.605 | 0.577 | 0.613 | -3.93 | -4.36 | 3.35 | 0.642 | 0.606 | 0.635 | 3.39 | 3.18 | 4.07 | Critical_Oil | 4796.3 | 6973.4 | 1.454 | 0.682 | 5.66 | 0.642 | 4.36 | 0.5106 | 0.6072 | 0.8554 | 0.9244 | 1 | 0.5285 | 0.6316 | 0.6799 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
187 | 894.5 | 568.1 | 108.5 | 126.4 | 23.4 | 913 | 5784.6 | 46.3 | 32.7 | 90.3 | 86.1 | 83.3 | 96.7 | 38.9 | 26.2 | 4147.7 | 4279.9 | 5248.9 | 5725.8 | 6015.6 | 7660.7 | 1.38 | 1.406 | 1.459 | 0.789 | 0.768 | 0.736 | -6.91 | 6.79 | -5.79 | 0.656 | 0.661 | 0.694 | 3.85 | 3.41 | 5.41 | 0.689 | 0.717 | 0.562 | -3.65 | 3.7 | 4.43 | 0.686 | 0.68 | 0.649 | 4.41 | 4.18 | 4.75 | Poor_Mixed | 4147.7 | 5725.8 | 1.38 | 0.789 | 6.91 | 0.717 | 5.41 | 0.3733 | 0.7617 | 0.5523 | 0.5371 | 1 | 0.3506 | 0.5161 | 0.5688 | 0.5688 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
188 | 1766 | 948 | 148.3 | 197 | 55.2 | 1337.8 | 8727.7 | 54.3 | 27 | 83.3 | 84.4 | 78.1 | 91.5 | 37.7 | 16.7 | 8427.7 | 9147.6 | 9406.7 | 14781 | 16883.1 | 17996.7 | 1.754 | 1.846 | 1.913 | 0.562 | 0.538 | 0.565 | -3.13 | 2.61 | -2.95 | 0.536 | 0.646 | 0.606 | 3.68 | -4.39 | 3.19 | 0.667 | 0.549 | 0.63 | -4.01 | -3.13 | 3.79 | 0.59 | 0.574 | 0.685 | -3.96 | 3.94 | 3.3 | Critical_DGA | 8427.7 | 14781 | 1.754 | 0.565 | 3.13 | 0.685 | 4.39 | 0.0362 | 0.8382 | 0.6813 | 0.8465 | 1 | 0.7864 | 0.6183 | 0.6015 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
189 | 315.9 | 198.4 | 74.7 | 156.4 | 58.3 | 400.8 | 2893.8 | 54.9 | 23.3 | 109 | 109.3 | 96.3 | 118.7 | 46 | 10.1 | 8179.3 | 7274.1 | 7409.9 | 15278.9 | 12843.4 | 12842.7 | 1.868 | 1.766 | 1.733 | 0.587 | 0.559 | 0.554 | 3.1 | 2.87 | 3.06 | 0.615 | 0.572 | 0.591 | 3.25 | 4.18 | 3.74 | 0.569 | 0.547 | 0.532 | -3.54 | 4.52 | 3.95 | 0.586 | 0.601 | 0.636 | 3.87 | -3.85 | 3.25 | Critical_Thermal | 7274.1 | 12842.7 | 1.733 | 0.587 | 3.1 | 0.636 | 4.52 | 0.5032 | 0.9008 | 0.0667 | 0.9992 | 1 | 0.761 | 0.6534 | 0.6747 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
190 | 1536.6 | 855.9 | 139.2 | 184.6 | 30.3 | 1232 | 8019.7 | 51.9 | 28 | 82.6 | 84 | 77.6 | 87.8 | 37.2 | 17.2 | 9812.8 | 8504 | 8822.6 | 19294.6 | 15387.7 | 15636.9 | 1.966 | 1.809 | 1.772 | 0.576 | 0.561 | 0.556 | 2.85 | 3.75 | -3.06 | 0.543 | 0.581 | 0.571 | 3.32 | 2.57 | -3.28 | 0.569 | 0.516 | 0.57 | 3.49 | 2.7 | 3.07 | 0.555 | 2.334 | 0.537 | 2.75 | 2.11 | -2.77 | Critical_DGA | 8504 | 15387.7 | 1.772 | 0.576 | 3.75 | 2.334 | 3.49 | 0.1215 | 0.8235 | 0.7145 | 0.832 | 1 | 0.7505 | 0.69 | 0.6315 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
191 | 1465.2 | 826.8 | 134.2 | 160.4 | 32.5 | 1255.4 | 7711.7 | 34.9 | 47 | 104.2 | 104.4 | 92 | 112 | 44.5 | 32.8 | 1527.6 | 1599.5 | 1178.5 | 1604.4 | 1757 | 1331.5 | 1.05 | 1.098 | 1.13 | 0.929 | 0.925 | 0.924 | -8.73 | 9.43 | 9.34 | 0.915 | 0.826 | 0.858 | 8.88 | 6.37 | 8.79 | 0.932 | 0.798 | 0.751 | 7.97 | -6.87 | 6.97 | 0.798 | 0.877 | 0.717 | 6.78 | 7.54 | 6.57 | Very Poor_Mixed | 1178.5 | 1331.5 | 1.05 | 0.929 | 9.43 | 0.932 | 8.88 | 0.1456 | 0.6109 | 0.1886 | 0.2904 | 1 | 0.0906 | 0.2267 | 0.3566 | 0.3566 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
192 | 1442 | 810.1 | 129.1 | 165.7 | 28.1 | 1145.9 | 7157 | 37 | 42.9 | 95.8 | 97.8 | 86.6 | 105.9 | 41.9 | 35.9 | 3474.8 | 2615.4 | 2486.8 | 4300 | 3330.4 | 2934.2 | 1.237 | 1.273 | 1.18 | 0.861 | 0.784 | 1.208 | 7.2 | 7.58 | -8.1 | 0.798 | 0.713 | 0.829 | 6.14 | 7.16 | 5.26 | 0.716 | 0.785 | 0.848 | 5.42 | 5.67 | -6.26 | 0.836 | 0.83 | 0.795 | -5.11 | -6.26 | 4.66 | Critical_Mixed | 2486.8 | 2934.2 | 1.18 | 1.208 | 8.1 | 0.848 | 7.16 | 0.1879 | 0.6504 | 0.3561 | 0.1678 | 1 | 0.2032 | 0.3147 | 0.4141 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
193 | 447 | 312.6 | 83.7 | 79.4 | 1.1 | 1884.2 | 22919.4 | 55.7 | 22.9 | 83.4 | 83.3 | 78.1 | 88.2 | 37.7 | 17.3 | 9703.2 | 8683.6 | 9540.9 | 19406.3 | 16905.8 | 19081.8 | 2 | 1.947 | 2 | 0.99 | 0.93 | 0.946 | 9.84 | 9.17 | 8.8 | 0.671 | 0.623 | 0.617 | 3.51 | 2.93 | 3.93 | 0.591 | 0.562 | 0.592 | 2.91 | -3.18 | 4.86 | 0.636 | 0.585 | 0.556 | 3.22 | -3.29 | 4.31 | Critical_Winding_TD_Cap | 8683.6 | 16905.8 | 1.947 | 0.99 | 9.84 | 0.671 | 4.86 | 0.6392 | 0.9088 | 0.7054 | 0.8291 | 1 | 0.0658 | 0.6288 | 0.6633 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
194 | 579.8 | 416.5 | 87.2 | 83.6 | 11.9 | 629.2 | 4586.4 | 55.8 | 26.6 | 84.4 | 83.2 | 76.5 | 89.3 | 37.8 | 18.9 | 7190.5 | 8197.7 | 6870.9 | 12311.3 | 15169.9 | 11626.9 | 1.712 | 1.851 | 1.692 | 0.649 | 0.66 | 0.654 | 3.98 | 3.99 | 4.58 | 0.621 | 0.613 | 0.65 | 2.55 | 4.08 | 4.18 | 0.596 | 0.618 | 0.582 | -4.36 | 4.07 | 4.78 | 0.607 | 0.578 | 0.604 | 3.75 | 4.64 | -3.52 | Fair_Mixed | 6870.9 | 11626.9 | 1.692 | 0.66 | 4.58 | 0.65 | 4.78 | 0.5972 | 0.8443 | 0.7039 | 0.7811 | 1 | 0.5816 | 0.6029 | 0.71 | 0.71 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
195 | 1236.7 | 770.2 | 125.7 | 149.9 | 26.8 | 1034.6 | 6614.2 | 36.1 | 43.9 | 103.2 | 100.3 | 89.6 | 111.5 | 43.4 | 34.7 | 1676.5 | 101.3 | 2395.2 | 1970.5 | 128 | 2654.5 | 1.175 | 1.264 | 1.108 | 0.866 | 0.818 | 0.82 | 7.68 | 7.11 | 8.05 | 0.776 | 0.713 | 0.79 | 5.88 | 5.54 | 4.79 | 0.694 | 0.733 | 0.78 | 6.31 | 5.66 | 7.86 | 0.723 | 0.869 | 0.766 | -6.34 | -6.31 | 5.45 | Critical_Mixed | 101.3 | 128 | 1.108 | 0.866 | 8.05 | 0.869 | 7.86 | 0.2492 | 0.6406 | 0.2418 | 0.2157 | 0.85 | 0.2357 | 0.3408 | 0.4045 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
196 | 1695 | 982.4 | 148.3 | 197 | 39.8 | 1374.9 | 8461 | 59 | 22.9 | 81 | 75.2 | 72.9 | 84.9 | 36.4 | 17.7 | 8168.5 | 8148.2 | 8110.9 | 15870.4 | 15019.7 | 13640.3 | 1.943 | 1.843 | 1.682 | 0.541 | 0.571 | 0.54 | -2.88 | 2.75 | 2.13 | 0.633 | 0.625 | 0.633 | 3.56 | 4.95 | 3.43 | 0.662 | 0.62 | 0.631 | 2.96 | 4.07 | 3.26 | 0.563 | 0.618 | 0.603 | -4.04 | 3.83 | 4.27 | Critical_DGA | 8110.9 | 13640.3 | 1.682 | 0.571 | 2.88 | 0.662 | 4.95 | 0.0371 | 0.9088 | 0.867 | 0.8173 | 1 | 0.8165 | 0.5904 | 0.6265 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
197 | 1610.5 | 881.6 | 137.9 | 174.9 | 34.3 | 1283.2 | 7867.4 | 33.1 | 47.6 | 108.6 | 107.4 | 95.2 | 115.2 | 44.9 | 31.7 | 2482.9 | 1916.8 | 2783.9 | 3002 | 2229.4 | 3328.4 | 1.209 | 1.163 | 1.196 | 0.925 | 0.99 | 0.971 | 8.89 | 9.78 | -8.64 | 0.661 | 0.713 | 0.877 | 8.28 | 7.52 | -8.95 | 0.871 | 0.922 | 0.89 | 6.32 | -5.72 | 6.07 | 0.801 | 0.879 | 0.749 | 7.94 | 7.46 | -5.04 | Very Poor_Mixed | 1916.8 | 2229.4 | 1.163 | 0.99 | 9.78 | 0.922 | 8.95 | 0.1011 | 0.6053 | 0.1109 | 0.3329 | 1 | 0.0698 | 0.2537 | 0.3411 | 0.3411 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
198 | 152.5 | 188.4 | 70.6 | 65.4 | 1.5 | 386 | 3010.6 | 56.2 | 23.9 | 75.2 | 76.5 | 71.3 | 82.2 | 35.2 | 11.7 | 10000 | 10000 | 9311.5 | 19375 | 19699.9 | 18309.4 | 1.938 | 1.97 | 1.966 | 0.566 | 0.543 | 0.577 | -2.88 | 2.96 | 3.39 | 0.794 | 0.577 | 0.583 | -6.79 | 2 | 2 | 0.569 | 0.615 | 0.572 | 2.57 | 2.48 | 2.04 | 0.517 | 0.504 | 0.543 | 2.95 | 3.21 | 3.16 | Poor_Bushing_TD_Cap | 9311.5 | 18309.4 | 1.938 | 0.577 | 3.39 | 0.794 | 6.79 | 0.8928 | 0.8894 | 0.9435 | 0.9724 | 1 | 0.7637 | 0.7091 | 0.8674 | 0.8674 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
199 | 1578.3 | 975.2 | 142.6 | 197 | 28.6 | 1321.9 | 8180.5 | 35.6 | 44.7 | 102.1 | 105.3 | 92.4 | 113 | 43.4 | 31.1 | 1270.5 | 1947.8 | 1624.7 | 1389.9 | 2229.4 | 1859.6 | 1.094 | 1.145 | 1.145 | 0.894 | 0.931 | 0.879 | 8.58 | 9.39 | 8.66 | 0.922 | 0.862 | 0.709 | -8.87 | 5.95 | 6.35 | 0.882 | 0.864 | 0.8 | 4.49 | -5.27 | 5.22 | 0.808 | 0.819 | 0.766 | 7.14 | -6.53 | 5.39 | Very Poor_Mixed | 1270.5 | 1389.9 | 1.094 | 0.931 | 9.39 | 0.922 | 8.87 | 0.0888 | 0.6328 | 0.1961 | 0.3559 | 1 | 0.1225 | 0.2737 | 0.362 | 0.362 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
200 | 222.6 | 222.2 | 80.8 | 73.3 | 4.8 | 421.8 | 2902.4 | 54.7 | 80.4 | 78.2 | 76.5 | 70.5 | 81.3 | 35.6 | 16.3 | 8783.3 | 9945.2 | 8644.8 | 16098.3 | 18228.1 | 15711 | 1.833 | 1.833 | 1.817 | 0.622 | 0.625 | 0.624 | 3.23 | 4 | -3.28 | 0.599 | 0.564 | 0.635 | 2.57 | 3.02 | 3.01 | 0.99 | 0.541 | 0.547 | 9.26 | -3.11 | 3.58 | 0.586 | 0.522 | 0.586 | -3.18 | -3.88 | 3.93 | Critical_Bushing_TD_Cap | 8644.8 | 15711 | 1.817 | 0.625 | 4 | 0.99 | 9.26 | 0.7866 | 0.5833 | 0.9187 | 0.8578 | 1 | 0.6566 | 0.6223 | 0.7653 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
201 | 972 | 484.2 | 108.7 | 112.7 | 19.7 | 840.7 | 5460.8 | 45.6 | 35.2 | 89.5 | 90.3 | 82.5 | 98.5 | 40.2 | 25.1 | 6871.4 | 6233 | 5772 | 11936.7 | 9520.6 | 8954 | 1.737 | 1.527 | 1.551 | 0.748 | 0.696 | 0.751 | -5.96 | 5.92 | 5.67 | 0.652 | 0.635 | 0.701 | 5.07 | 5.5 | 4.41 | 0.61 | 0.667 | 0.673 | 5.8 | 4.79 | 4.41 | 0.7 | 0.657 | 0.592 | 5.19 | -4.87 | -4.96 | Poor_Mixed | 5772 | 8954 | 1.527 | 0.751 | 5.96 | 0.701 | 5.8 | 0.4228 | 0.7322 | 0.5167 | 0.576 | 1 | 0.4135 | 0.4994 | 0.5818 | 0.5818 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
202 | 874.8 | 544.6 | 96.7 | 109 | 16.7 | 837.4 | 5610.9 | 48.5 | 30.6 | 88.9 | 87.8 | 81.6 | 95.5 | 39.4 | 22 | 5766.2 | 5685.8 | 7265.7 | 8842.5 | 8475.8 | 12564.9 | 1.534 | 1.491 | 1.729 | 0.707 | 0.638 | 0.731 | -6.15 | 3.99 | 5.69 | 0.651 | 0.766 | 0.581 | 5.54 | -5.35 | -4.61 | 0.654 | 0.678 | 0.662 | 4.61 | 5.06 | 3.85 | 0.59 | 0.688 | 0.655 | 5.21 | 5.02 | 4.69 | Poor_Mixed | 5685.8 | 8475.8 | 1.491 | 0.731 | 6.15 | 0.766 | 5.54 | 0.4532 | 0.7881 | 0.5634 | 0.6819 | 1 | 0.4838 | 0.5008 | 0.6162 | 0.6162 | Fair | 1 | 1 | DGA | 0 |  | C2H2
203 | 996.4 | 510 | 105 | 116.9 | 18.8 | 927.7 | 4651 | 46.8 | 32.6 | 92.5 | 93.6 | 84 | 101.8 | 39.8 | 25 | 6749.2 | 5672 | 5853.4 | 10628.8 | 8848.3 | 8779.7 | 1.575 | 1.56 | 1.5 | 0.67 | 0.677 | 0.732 | 5.55 | 5.13 | 6.28 | 0.734 | 0.632 | 0.667 | 4.76 | 4.04 | 4.04 | 0.65 | 0.629 | 0.701 | 3.64 | 4.87 | 4.82 | 0.705 | 0.716 | 0.69 | 5.43 | 4.09 | 4.7 | Poor_Mixed | 5672 | 8779.7 | 1.5 | 0.732 | 6.28 | 0.734 | 5.43 | 0.4193 | 0.7629 | 0.4526 | 0.5796 | 1 | 0.4599 | 0.4849 | 0.5823 | 0.5823 | Poor | 0 | 1 | DGA | 0 |  | C2H2
204 | 185.2 | 146.5 | 65.5 | 58.7 | 1.9 | 453.5 | 3297.1 | 45.4 | 34.1 | 81.6 | 80.5 | 73.1 | 85.5 | 36.2 | 13.4 | 8382.1 | 8455.7 | 7665.7 | 15455.7 | 14902.1 | 13317.2 | 1.844 | 1.762 | 1.737 | 0.565 | 0.577 | 0.545 | -2.9 | 3.49 | 2.97 | 0.505 | 0.521 | 0.543 | -2.38 | -2.03 | 3.04 | 0.52 | 0.512 | 0.568 | 2.01 | 2.21 | 3.24 | 0.564 | 0.553 | 0.519 | 3.4 | 3.23 | 3.02 | Fair_Oil | 7665.7 | 13317.2 | 1.737 | 0.577 | 3.49 | 0.568 | 3.4 | 0.8781 | 0.7449 | 0.8012 | 0.9342 | 1 | 0.7603 | 0.8088 | 0.8478 | 0.8478 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
205 | 533.1 | 287.8 | 84.9 | 71.7 | 10.6 | 546.6 | 4086.5 | 52.1 | 28.5 | 86.5 | 84.1 | 78.2 | 92.6 | 37.4 | 18.2 | 8107.2 | 7828.4 | 7010.2 | 14451 | 13764.3 | 11933.6 | 1.782 | 1.758 | 1.702 | 0.638 | 0.712 | 0.65 | 4.31 | -5.07 | 3.85 | 0.627 | 0.643 | 0.574 | 2.65 | -2.91 | 3.17 | 0.59 | 0.572 | 0.5 | 3.36 | -3.28 | -3.73 | 0.655 | 0.59 | 0.599 | 3.83 | -4.12 | -3.91 | Fair_Mixed | 7010.2 | 11933.6 | 1.702 | 0.712 | 5.07 | 0.655 | 4.12 | 0.6591 | 0.8164 | 0.6555 | 0.8024 | 1 | 0.5571 | 0.6616 | 0.7255 | 0.7255 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
206 | 942.8 | 532.8 | 107.1 | 118.6 | 19 | 899.3 | 5813.7 | 55.1 | 23.7 | 80.8 | 81.8 | 72.9 | 86.3 | 35.9 | 14.2 | 8828.1 | 7932.3 | 9775.4 | 17491.3 | 13730.5 | 19450.6 | 1.981 | 1.731 | 1.99 | 0.5 | 0.5 | 0.5 | -2.01 | 2.45 | 2.68 | 0.559 | 0.515 | 0.555 | -2.75 | 2.53 | -2.46 | 0.532 | 0.547 | 0.508 | 2 | 2.56 | -2.34 | 0.612 | 0.531 | 0.509 | 3.06 | -2.48 | 2.52 | Poor_DGA | 7932.3 | 13730.5 | 1.731 | 0.5 | 2.68 | 0.612 | 3.06 | 0.4082 | 0.8931 | 0.7961 | 0.9144 | 1 | 0.967 | 0.803 | 0.7745 | 0.7745 | Fair | 1 | 1 | DGA | 0 |  | C2H2
207 | 956.4 | 526.8 | 110.3 | 131.5 | 18.9 | 866.9 | 6097.4 | 45 | 34.8 | 89 | 91.7 | 83.2 | 100.8 | 39.6 | 25.7 | 5295.3 | 5947.7 | 6218.4 | 8176.4 | 9634.6 | 9668.2 | 1.544 | 1.62 | 1.555 | 0.741 | 0.715 | 0.718 | 5.99 | -5.42 | 5.43 | 0.691 | 0.692 | 0.667 | 4.88 | -4.45 | 5.56 | 0.585 | 0.693 | 0.647 | 4.03 | 5.38 | -3.63 | 0.637 | 0.667 | 0.604 | 5.89 | 5.53 | 6.29 | Poor_Mixed | 5295.3 | 8176.4 | 1.544 | 0.741 | 5.99 | 0.693 | 6.29 | 0.3946 | 0.7368 | 0.4988 | 0.5549 | 1 | 0.4324 | 0.4985 | 0.575 | 0.575 | Poor | 0 | 1 | DGA | 0 |  | C2H2
208 | 864.6 | 493.4 | 103.6 | 117.1 | 19.5 | 798.1 | 5800.2 | 45.6 | 36.4 | 92.6 | 93.9 | 83.1 | 99.9 | 39.4 | 25 | 5587 | 4292.1 | 4800.9 | 8576 | 6269.8 | 7243.3 | 1.535 | 1.461 | 1.509 | 0.722 | 0.707 | 0.732 | -6.33 | 5.48 | -6.04 | 0.708 | 0.671 | 0.683 | -4.17 | 4.93 | 5.58 | 0.601 | 0.62 | 0.604 | 4.01 | -5.44 | 4.58 | 0.649 | 0.649 | 0.679 | 4.98 | 5.71 | -5.11 | Poor_Mixed | 4292.1 | 6269.8 | 1.461 | 0.732 | 6.33 | 0.708 | 5.71 | 0.4324 | 0.7186 | 0.4677 | 0.5796 | 1 | 0.4177 | 0.505 | 0.5795 | 0.5795 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
209 | 1375.7 | 823.1 | 131 | 170.6 | 26.1 | 1256.7 | 7830.4 | 37.4 | 44.9 | 102.8 | 103.7 | 93.4 | 114.3 | 44.3 | 32.3 | 3420.5 | 1360.7 | 1525 | 4433.7 | 1469 | 1878.1 | 1.296 | 1.08 | 1.232 | 0.855 | 0.879 | 0.863 | 8.65 | -8.37 | 8.17 | 0.754 | 0.826 | 0.671 | -7.85 | -5.76 | 6.67 | 0.748 | 0.852 | 0.89 | 7.6 | 5.88 | 5.76 | 0.723 | 0.88 | 0.889 | 6.47 | 7.62 | 6.15 | Very Poor_Mixed | 1360.7 | 1469 | 1.08 | 0.879 | 8.65 | 0.89 | 7.85 | 0.1747 | 0.6309 | 0.1824 | 0.3098 | 1 | 0.1721 | 0.2789 | 0.3874 | 0.3874 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
210 | 696 | 446 | 100.9 | 107 | 13.4 | 673.1 | 4937.5 | 46.4 | 35.7 | 92.9 | 89.7 | 83.4 | 100.1 | 39.6 | 24.9 | 5910 | 5138.3 | 6298.7 | 9338.6 | 7874 | 10083.9 | 1.58 | 1.532 | 1.601 | 0.749 | 0.767 | 0.813 | 5.67 | -6.05 | 6.01 | 0.645 | 0.685 | 0.707 | 4.77 | -5 | 3.86 | 0.628 | 0.609 | 0.649 | 4.15 | 3.72 | -5.04 | 0.704 | 0.665 | 0.695 | 4.49 | 5.78 | 4.25 | Poor_Mixed | 5138.3 | 7874 | 1.532 | 0.813 | 6.05 | 0.707 | 5.78 | 0.5286 | 0.7265 | 0.4887 | 0.5831 | 1 | 0.3725 | 0.5011 | 0.5997 | 0.5997 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
211 | 689.1 | 426.7 | 92.9 | 96.6 | 11.5 | 646 | 4867.6 | 48 | 30.2 | 86.4 | 91.2 | 79.5 | 94.7 | 38.1 | 20.3 | 6909.6 | 6489.9 | 6838.4 | 11784.7 | 10223 | 11158.3 | 1.706 | 1.575 | 1.632 | 0.679 | 0.64 | 0.743 | 5.49 | 4.16 | 5.28 | 0.617 | 0.669 | 0.684 | 4.41 | 3.48 | 3.73 | 0.641 | 0.662 | 0.525 | 2.59 | 3.01 | -5.04 | 0.592 | 0.687 | 0.606 | 4.04 | 4.76 | -4.05 | Poor_Mixed | 6489.9 | 10223 | 1.575 | 0.743 | 5.49 | 0.687 | 5.04 | 0.5668 | 0.7933 | 0.5836 | 0.7372 | 1 | 0.5047 | 0.5789 | 0.667 | 0.667 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
212 | 798.4 | 467.9 | 108.4 | 119.2 | 17.1 | 784.2 | 5307.6 | 45 | 36.1 | 90.1 | 88.3 | 80.2 | 95.6 | 38.9 | 25.6 | 6307.8 | 6204 | 6377 | 9814.5 | 10070 | 10558.4 | 1.556 | 1.623 | 1.656 | 0.784 | 0.729 | 0.728 | 6.02 | 5.12 | 5.64 | 0.688 | 0.712 | 0.711 | 5.43 | 4.64 | -4.22 | 0.61 | 0.684 | 0.609 | -4.01 | 5.71 | 5.28 | 0.674 | 0.689 | 0.631 | 5.7 | 4.82 | 5.09 | Poor_Mixed | 6204 | 9814.5 | 1.556 | 0.784 | 6.02 | 0.712 | 5.71 | 0.4567 | 0.722 | 0.5637 | 0.5584 | 1 | 0.4146 | 0.483 | 0.5901 | 0.5901 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
213 | 1020.2 | 619.4 | 114.4 | 133.8 | 18.2 | 915.7 | 5878.1 | 45.2 | 36.2 | 91.1 | 90.1 | 82.1 | 101.1 | 39.2 | 26.7 | 5543.2 | 5742.6 | 4748.1 | 8468.7 | 9119.5 | 7493.5 | 1.528 | 1.588 | 1.578 | 0.75 | 0.733 | 0.726 | -6.03 | 5.83 | 5.79 | 0.648 | 0.693 | 0.683 | 5.38 | 5.35 | 4.3 | 0.693 | 0.701 | 0.617 | 4.21 | 4.86 | 4.51 | 0.699 | 0.695 | 0.662 | -4.87 | 3.94 | -4.67 | Poor_Mixed | 4748.1 | 7493.5 | 1.528 | 0.75 | 6.03 | 0.701 | 5.38 | 0.3749 | 0.7208 | 0.5033 | 0.5192 | 1 | 0.4072 | 0.4815 | 0.5602 | 0.5602 | Poor | 0 | 1 | DGA | 0 |  | C2H2
214 | 897.3 | 492.6 | 102.7 | 115.7 | 17.6 | 913.6 | 5448.8 | 43.6 | 35.1 | 91.3 | 88.6 | 82.2 | 96.2 | 39.5 | 23.1 | 5428.4 | 5379.7 | 5504.8 | 7826.9 | 8603.2 | 8131.2 | 1.442 | 1.599 | 1.477 | 0.717 | 0.734 | 0.702 | 5.47 | 5.52 | 5.85 | 0.783 | 0.715 | 0.656 | 4.52 | 6.12 | 4.55 | 0.726 | 0.61 | 0.784 | 5.33 | 4.32 | 4.96 | 0.668 | 0.685 | 0.733 | 5.06 | 5 | -6.02 | Poor_Mixed | 5379.7 | 7826.9 | 1.442 | 0.734 | 5.85 | 0.784 | 6.12 | 0.433 | 0.7333 | 0.5341 | 0.645 | 1 | 0.4387 | 0.4333 | 0.5813 | 0.5813 | Poor | 0 | 1 | DGA | 0 |  | C2H2
215 | 963.7 | 541.7 | 103.9 | 112.6 | 22.4 | 865.2 | 5353.5 | 46.6 | 33.9 | 89.3 | 89.7 | 83.1 | 96.3 | 39.8 | 26 | 5691.7 | 5641.7 | 5967.8 | 8731.3 | 8681.3 | 8994.8 | 1.534 | 1.539 | 1.507 | 0.746 | 0.739 | 0.713 | -5.13 | 5.9 | 5.55 | 0.653 | 0.603 | 0.631 | 3.8 | 3.3 | -5.06 | 0.678 | 0.609 | 0.635 | 3.69 | 3.81 | 3.79 | 0.703 | 0.713 | 0.697 | 4.06 | 4.87 | -3.77 | Poor_Mixed | 5641.7 | 8681.3 | 1.507 | 0.746 | 5.9 | 0.713 | 5.06 | 0.4033 | 0.7473 | 0.5318 | 0.5442 | 1 | 0.4303 | 0.5323 | 0.587 | 0.587 | Poor | 0 | 1 | DGA | 0 |  | C2H2
216 | 1047.4 | 541.2 | 98.3 | 119.1 | 18 | 822.5 | 5710.9 | 46.3 | 33 | 93.2 | 87.3 | 82.7 | 99.3 | 39.2 | 23.5 | 5715.4 | 5273.7 | 6537.3 | 8817.7 | 7738.2 | 10444.5 | 1.543 | 1.467 | 1.598 | 0.747 | 0.725 | 0.766 | 6.01 | 5.7 | 6.34 | 0.629 | 0.723 | 0.703 | -5.46 | 4.09 | -4.46 | 0.623 | 0.682 | 0.655 | 4.79 | 5.25 | 5.1 | 0.66 | 0.667 | 0.688 | -5.11 | -4.3 | -4.56 | Poor_Mixed | 5273.7 | 7738.2 | 1.467 | 0.766 | 6.34 | 0.723 | 5.46 | 0.4217 | 0.7581 | 0.514 | 0.6314 | 1 | 0.3917 | 0.4859 | 0.5817 | 0.5817 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
217 | 800.5 | 476.8 | 98.1 | 119.3 | 18.8 | 845.9 | 5080.6 | 44.9 | 34.9 | 90.7 | 88.9 | 79.9 | 94.5 | 38.6 | 23.9 | 6548.8 | 5760.7 | 5765 | 10206.9 | 9352.6 | 8751.3 | 1.559 | 1.624 | 1.518 | 0.682 | 0.705 | 0.665 | -5.43 | 5.52 | -5.37 | 0.792 | 0.711 | 0.642 | 6.55 | -6.09 | 5.34 | 0.679 | 0.683 | 0.651 | 4.26 | 5.35 | 5.86 | 0.704 | 0.66 | 0.664 | 5.49 | 4.53 | -4.12 | Poor_Mixed | 5760.7 | 8751.3 | 1.518 | 0.705 | 5.52 | 0.792 | 6.55 | 0.4468 | 0.7356 | 0.565 | 0.6177 | 1 | 0.4796 | 0.4478 | 0.5951 | 0.5951 | Poor | 0 | 1 | DGA | 0 |  | C2H2
218 | 740.5 | 426.5 | 100.8 | 104.6 | 13.9 | 765 | 4529.6 | 56.5 | 23.4 | 77.1 | 79.3 | 71.7 | 80 | 35.5 | 14.9 | 8428.1 | 10000 | 9372.5 | 16121.6 | 19476.5 | 18200.6 | 1.913 | 1.948 | 1.942 | 0.553 | 0.57 | 0.565 | -2.98 | 3.39 | 3.74 | 0.568 | 0.541 | 0.557 | -2.75 | 2.43 | -3.34 | 0.576 | 0.505 | 0.57 | -2.69 | 2.65 | 2.55 | 0.556 | 0.548 | 0.51 | 3.04 | -2.75 | 3.32 | Fair_DGA | 8428.1 | 16121.6 | 1.913 | 0.57 | 3.74 | 0.576 | 3.34 | 0.5178 | 0.8988 | 0.896 | 0.8962 | 1 | 0.7429 | 0.7681 | 0.774 | 0.774 | Fair | 1 | 1 | DGA | 0 |  | C2H2
219 | 1476.4 | 787.4 | 128.8 | 169.6 | 29.5 | 1070.8 | 7619.8 | 34.6 | 46.2 | 106.3 | 104 | 95.1 | 115 | 43.7 | 31 | 1409.7 | 690 | 1420.9 | 1628.7 | 1200 | 1496.4 | 1.155 | 1.739 | 1.053 | 0.865 | 0.964 | 0.93 | 8.5 | 9.49 | -8.73 | 0.797 | 0.862 | 0.92 | 6.12 | 7.94 | 6.79 | 0.759 | 0.837 | 0.736 | -6.56 | 6.67 | 7.44 | 0.856 | 0.815 | 0.883 | -6.85 | -5.3 | 5.6 | Very Poor_Mixed | 690 | 1200 | 1.053 | 0.964 | 9.49 | 0.92 | 7.94 | 0.181 | 0.6184 | 0.1526 | 0.3597 | 1 | 0.1086 | 0.2538 | 0.3736 | 0.3736 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
220 | 1688.2 | 943.2 | 139.6 | 174 | 27.6 | 1226.3 | 8479 | 35.5 | 45.8 | 104.9 | 104.9 | 91.5 | 113.8 | 43.4 | 34 | 829.7 | 2244.3 | 1738.7 | 1200 | 2496.7 | 1913.6 | 1.446 | 1.112 | 1.101 | 0.924 | 0.985 | 0.926 | 8.4 | 9.67 | 9.24 | 0.877 | 0.85 | 0.89 | 6.65 | -6.61 | 6.67 | 0.816 | 0.952 | 0.866 | 9.02 | 6.61 | 8.53 | 0.767 | 0.792 | 0.772 | 5.67 | -7.61 | 7.79 | Very Poor_Mixed | 829.7 | 1200 | 1.101 | 0.985 | 9.67 | 0.952 | 9.02 | 0.1171 | 0.6222 | 0.1836 | 0.2434 | 1 | 0.0812 | 0.2203 | 0.3455 | 0.3455 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
221 | 307 | 213.9 | 74.1 | 64.9 | 1.9 | 493.7 | 2500 | 59.7 | 23.6 | 78.8 | 81.7 | 73 | 86.6 | 36.8 | 11.9 | 9653 | 9251.4 | 10000 | 19305.9 | 17798.3 | 19865.5 | 2 | 1.924 | 1.987 | 0.759 | 0.747 | 0.815 | 7.05 | 5.86 | 6.85 | 0.555 | 0.585 | 0.528 | 3.23 | -2.24 | -2.83 | 0.5 | 0.52 | 0.511 | 2 | 2.53 | -2.55 | 0.55 | 0.581 | 0.563 | 2 | 2 | -2.66 | Poor_Winding_TD_Cap | 9251.4 | 17798.3 | 1.924 | 0.815 | 7.05 | 0.585 | 3.23 | 0.8408 | 0.895 | 0.8078 | 0.9682 | 1 | 0.3382 | 0.8063 | 0.7993 | 0.7993 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
222 | 413.8 | 305.8 | 87.6 | 111.6 | 1 | 519.8 | 3502.7 | 58 | 23.3 | 97.2 | 97.4 | 87.8 | 106.5 | 42.3 | 15.1 | 8740.7 | 9578.3 | 9656 | 16450.1 | 18486.8 | 19072.1 | 1.882 | 1.93 | 1.975 | 0.581 | 0.503 | 0.624 | 3.71 | -2.46 | 3.56 | 0.535 | 0.603 | 0.56 | 2.87 | 3.16 | 3.43 | 0.555 | 0.537 | 0.559 | 3 | -2.66 | 2.98 | 0.585 | 0.584 | 0.552 | 2 | 4.02 | 2.45 | Poor_Thermal | 8740.7 | 16450.1 | 1.882 | 0.624 | 3.71 | 0.603 | 4.02 | 0.8108 | 0.9008 | 0.3371 | 0.8908 | 1 | 0.7605 | 0.7259 | 0.7862 | 0.7862 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H4
223 | 100.3 | 120 | 68.3 | 51.3 | 1.8 | 350 | 2528.5 | 55.8 | 24.9 | 75.9 | 75.3 | 72.8 | 84.1 | 35.5 | 16.1 | 9725.7 | 8687 | 9182.3 | 18553 | 16479.1 | 17570.3 | 1.908 | 1.897 | 1.913 | 0.513 | 0.56 | 0.537 | 2.05 | 2.34 | 2.8 | 0.511 | 0.5 | 0.5 | -2 | 2.38 | 2.3 | 0.512 | 0.5 | 0.5 | 2.29 | 2.28 | 2 | 0.551 | 0.512 | 0.5 | 2.73 | 2.16 | -2.36 | Fair_Age | 8687 | 16479.1 | 1.897 | 0.56 | 2.8 | 0.551 | 2.73 | 0.9347 | 0.8717 | 0.9247 | 0.8635 | 1 | 0.858 | 0.9292 | 0.9213 | 0.9213 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
224 | 1210.5 | 803.8 | 123.7 | 164.4 | 27.4 | 1117 | 7416.7 | 32.8 | 47.1 | 101.8 | 99 | 88.1 | 109.9 | 42.7 | 28.6 | 2662 | 1748.9 | 1843.3 | 3241.6 | 2120.6 | 2166.9 | 1.218 | 1.213 | 1.176 | 0.934 | 0.904 | 0.903 | 9.34 | 8.6 | 8.4 | 0.892 | 0.775 | 0.844 | -8.26 | 5.64 | 5.41 | 0.791 | 0.883 | 0.796 | -7.61 | 5.35 | 6.51 | 0.74 | 0.802 | 0.742 | 6.09 | 6.66 | -7.93 | Very Poor_Mixed | 1748.9 | 2120.6 | 1.176 | 0.934 | 9.34 | 0.892 | 8.26 | 0.2143 | 0.61 | 0.2791 | 0.4498 | 1 | 0.1187 | 0.2742 | 0.4032 | 0.4032 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
225 | 1569.1 | 901.8 | 133.7 | 182.9 | 29.9 | 1239.8 | 7426.1 | 36.8 | 42.8 | 108.1 | 105.3 | 95.2 | 116.8 | 43.3 | 32.4 | 1853.9 | 1986.9 | 2989 | 2129.8 | 2301.6 | 3911.4 | 1.149 | 1.158 | 1.309 | 0.935 | 0.946 | 0.919 | 8.78 | 8.85 | -9.14 | 0.83 | 0.918 | 0.76 | -7.86 | -7.22 | -7.17 | 0.858 | 0.829 | 0.71 | 8.77 | 8.66 | 5.85 | 0.863 | 0.747 | 0.822 | 8.21 | 6.83 | 7.52 | Very Poor_Mixed | 1853.9 | 2129.8 | 1.149 | 0.946 | 9.14 | 0.918 | 8.77 | 0.1285 | 0.6514 | 0.1288 | 0.3059 | 1 | 0.0978 | 0.2356 | 0.3546 | 0.3546 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
226 | 907.1 | 490.6 | 107.8 | 116.4 | 17.4 | 829.3 | 5163 | 48.1 | 30.8 | 90.5 | 88.3 | 80.5 | 94.9 | 39.6 | 24.5 | 5623.8 | 6708.1 | 5106.5 | 9458 | 11091.6 | 7382.3 | 1.682 | 1.653 | 1.446 | 0.742 | 0.733 | 0.737 | 6.82 | 5.68 | 5.97 | 0.686 | 0.77 | 0.595 | -5.6 | 4.33 | -6.24 | 0.669 | 0.692 | 0.638 | -5.02 | 5.11 | 5.48 | 0.611 | 0.66 | 0.662 | -3.75 | 4.78 | 5.52 | Poor_Mixed | 5106.5 | 7382.3 | 1.446 | 0.742 | 6.82 | 0.77 | 6.24 | 0.4426 | 0.7855 | 0.5582 | 0.597 | 1 | 0.3915 | 0.4841 | 0.5925 | 0.5925 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
227 | 914 | 532.4 | 105.2 | 127.8 | 22.8 | 903.1 | 5599.1 | 44.5 | 37 | 90.5 | 89.5 | 82.8 | 101 | 39.1 | 24.9 | 5352 | 6661.2 | 5417.3 | 8007.1 | 10097.8 | 7895.5 | 1.496 | 1.516 | 1.457 | 0.705 | 0.693 | 0.773 | 5.14 | 6.09 | 6.52 | 0.636 | 0.717 | 0.673 | 4.57 | 4.76 | 6.24 | 0.636 | 0.709 | 0.729 | 5.44 | 5.07 | 5.75 | 0.646 | 0.62 | 0.639 | 5.54 | 5.85 | 4.61 | Poor_Mixed | 5352 | 7895.5 | 1.457 | 0.773 | 6.52 | 0.729 | 6.24 | 0.3832 | 0.712 | 0.5079 | 0.5831 | 1 | 0.4177 | 0.4713 | 0.5645 | 0.5645 | Poor | 0 | 1 | DGA | 0 |  | C2H2
228 | 1678.9 | 856.9 | 143.8 | 180.6 | 34.3 | 1267.9 | 7927 | 34.1 | 45.4 | 107.5 | 106.8 | 93.2 | 117.6 | 44.3 | 32.5 | 1872.8 | 1246.5 | 1900.8 | 2256.5 | 1308.9 | 2118.5 | 1.205 | 1.05 | 1.115 | 0.966 | 0.941 | 0.892 | -9.84 | 9.32 | -8.78 | 0.85 | 0.714 | 0.775 | -6.15 | 7.48 | 8.84 | 0.787 | 0.878 | 0.859 | -7.01 | 8.33 | 7.58 | 0.853 | 0.782 | 0.944 | 7.74 | 7.06 | 6.5 | Very Poor_Mixed | 1246.5 | 1308.9 | 1.05 | 0.966 | 9.84 | 0.944 | 8.84 | 0.0904 | 0.6261 | 0.1237 | 0.302 | 1 | 0.0788 | 0.2297 | 0.3376 | 0.3376 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
229 | 440.1 | 334.6 | 83.9 | 84.6 | 2.7 | 2816.4 | 17290.4 | 53.9 | 25.7 | 80.2 | 79.7 | 72.4 | 84.3 | 36.8 | 13.3 | 1070.8 | 840.5 | 690 | 1092.2 | 870.3 | 703.8 | 1.02 | 1.035 | 1.02 | 0.743 | 0.648 | 0.741 | 5.04 | 4.7 | -5.81 | 0.571 | 0.569 | 0.585 | -4.18 | 2.61 | -3.3 | 0.553 | 0.595 | 0.566 | 3.23 | 4.28 | -3.44 | 0.593 | 0.575 | 0.602 | -4.28 | 3.66 | 3.02 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.743 | 5.81 | 0.602 | 4.28 | 0.5712 | 0.8584 | 0.8288 | 0.9367 | 0.85 | 0.4711 | 0.6678 | 0.6977 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation; IR_Min_10min<1000 Mohm: critical insulation resistance | CO
230 | 1758.7 | 982.4 | 148.3 | 196.7 | 34.3 | 1379 | 8214.7 | 54.6 | 57.2 | 85.3 | 83.2 | 78.3 | 91.4 | 39.2 | 12.8 | 9558 | 8280.8 | 9768.4 | 18697.2 | 14767.5 | 18946.5 | 1.956 | 1.783 | 1.94 | 0.515 | 0.623 | 0.599 | 2.9 | 3.98 | 3.4 | 0.569 | 0.55 | 0.546 | 2.07 | 3.67 | 2.7 | 0.52 | 0.594 | 0.523 | -2.96 | 2.77 | 2 | 0.593 | 0.506 | 0.584 | 2.91 | 3.76 | 3.6 | Critical_DGA | 8280.8 | 14767.5 | 1.783 | 0.623 | 3.98 | 0.594 | 3.76 | 0.0386 | 0.5833 | 0.6657 | 0.9484 | 1 | 0.7271 | 0.7543 | 0.5912 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
231 | 249.6 | 271.5 | 71.2 | 63.7 | 35.5 | 484.1 | 3328 | 53.5 | 26.6 | 79.4 | 78.4 | 74.5 | 86.7 | 36.7 | 16.3 | 8949.1 | 7772 | 8665.9 | 17149.8 | 13543.2 | 16088.4 | 1.916 | 1.743 | 1.857 | 0.629 | 0.62 | 0.567 | -3.56 | 3.54 | 3.12 | 0.5 | 0.624 | 0.533 | 3.96 | 2.73 | 2.67 | 0.648 | 0.58 | 0.595 | -2.32 | -4.5 | 3.72 | 0.933 | 0.558 | 0.582 | 9.07 | 4.01 | 3.6 | Critical_Bushing_TD_Cap | 7772 | 13543.2 | 1.743 | 0.629 | 3.56 | 0.933 | 9.07 | 0.5829 | 0.8443 | 0.819 | 0.8578 | 1 | 0.6857 | 0.6264 | 0.7406 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
232 | 465 | 373.8 | 89.2 | 87.9 | 11.4 | 647.2 | 4161.5 | 47.9 | 31.2 | 87.5 | 84.3 | 81.2 | 92.8 | 39.1 | 22.3 | 5958.8 | 5182.9 | 5960.2 | 8981.6 | 7824 | 9336.2 | 1.507 | 1.51 | 1.566 | 0.693 | 0.708 | 0.713 | 5.33 | 5.34 | 4.95 | 0.611 | 0.67 | 0.618 | 3.58 | 3.35 | -4.96 | 0.629 | 0.572 | 0.575 | 5.09 | -4.2 | -2.48 | 0.636 | 0.585 | 0.65 | 3.08 | -3.79 | 3.61 | Poor_Mixed | 5182.9 | 7824 | 1.507 | 0.713 | 5.34 | 0.67 | 5.09 | 0.611 | 0.7804 | 0.616 | 0.6719 | 1 | 0.4732 | 0.6002 | 0.6759 | 0.6759 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
233 | 828.4 | 447.1 | 102.3 | 117 | 19.4 | 832.9 | 4960.6 | 46.3 | 34.5 | 92 | 89.6 | 79.7 | 97.8 | 39.5 | 23.6 | 4929.5 | 5707.8 | 5758.3 | 6797.6 | 8947.1 | 8768.4 | 1.379 | 1.568 | 1.523 | 0.709 | 0.666 | 0.68 | 4.92 | -4.93 | -5.15 | 0.593 | 0.701 | 0.713 | 4.71 | 4 | 4.8 | 0.672 | 0.606 | 0.671 | 5.38 | 5.41 | 5.35 | 0.688 | 0.578 | 0.657 | -4.21 | -4.89 | -4.42 | Poor_Mixed | 4929.5 | 6797.6 | 1.379 | 0.709 | 5.15 | 0.713 | 5.41 | 0.4464 | 0.7403 | 0.5312 | 0.628 | 1 | 0.5036 | 0.5103 | 0.6073 | 0.6073 | Fair | 1 | 1 | DGA | 0 |  | C2H2
234 | 1455.8 | 945.5 | 142.1 | 167.7 | 30.1 | 1236.6 | 7972.7 | 32.6 | 47.1 | 105 | 103.9 | 93.3 | 111.4 | 44.1 | 31.4 | 1914.1 | 1328.9 | 2800.3 | 2093.3 | 1506.4 | 3564.8 | 1.094 | 1.134 | 1.273 | 0.866 | 0.914 | 0.966 | 8.2 | 8.63 | 9.18 | 0.785 | 0.805 | 0.945 | 5.76 | 8.06 | 5.26 | 0.776 | 0.853 | 0.811 | 6.66 | 7.91 | -6.51 | 0.83 | 0.776 | 0.86 | 8.98 | -7.51 | 7.74 | Very Poor_Mixed | 1328.9 | 1506.4 | 1.094 | 0.966 | 9.18 | 0.945 | 8.98 | 0.1304 | 0.61 | 0.1855 | 0.3444 | 1 | 0.1236 | 0.2374 | 0.3616 | 0.3616 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
235 | 597.7 | 367.1 | 92.9 | 95.4 | 2.3 | 636.7 | 4161.8 | 30.6 | 49.4 | 81.6 | 79.5 | 74.9 | 86.3 | 37.2 | 13.6 | 4113.3 | 52.9 | 4486.6 | 5560.7 | 94.5 | 6526.5 | 1.352 | 1.786 | 1.455 | 0.661 | 0.68 | 0.663 | 3.87 | -5.2 | -5.06 | 0.609 | 0.592 | 0.532 | 3.9 | 4.59 | 3.65 | 0.572 | 0.656 | 0.561 | 2.8 | 3.08 | 4.03 | 0.558 | 0.567 | 0.556 | 3.47 | -3.59 | 3.51 | Critical_Oil | 52.9 | 94.5 | 1.352 | 0.68 | 5.2 | 0.656 | 4.59 | 0.7052 | 0.5888 | 0.7864 | 0.9294 | 0.85 | 0.5373 | 0.6703 | 0.7039 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
236 | 222.4 | 240.1 | 72.1 | 57.9 | 2.3 | 446.8 | 3144.9 | 45.3 | 34.9 | 77.1 | 78 | 73.4 | 85 | 36.6 | 10 | 8019.3 | 7630.4 | 7744.2 | 14207.3 | 13026.1 | 13609.7 | 1.772 | 1.707 | 1.757 | 0.57 | 0.503 | 0.566 | 2.94 | 2.7 | 3.72 | 0.516 | 0.53 | 0.519 | 2 | 2 | -2.8 | 0.5 | 0.54 | 0.545 | -2.73 | -2.17 | 2.22 | 0.525 | 0.526 | 0.5 | 2 | 2.18 | 2.3 | Poor_Oil | 7630.4 | 13026.1 | 1.707 | 0.57 | 3.72 | 0.545 | 2.8 | 0.8516 | 0.7356 | 0.8632 | 1 | 1 | 0.7973 | 0.8709 | 0.8659 | 0.8659 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
237 | 1441.9 | 797.9 | 133.6 | 161.4 | 31.9 | 1200.2 | 7147.9 | 35.2 | 43.8 | 106.5 | 103 | 95.5 | 115.8 | 44.7 | 31.6 | 2226.6 | 2446.1 | 2455.4 | 2722.8 | 3114.1 | 2735.4 | 1.223 | 1.273 | 1.114 | 0.979 | 0.938 | 0.942 | -9.27 | 9.25 | -9.08 | 0.705 | 0.689 | 0.743 | 7.69 | 7.45 | 4.91 | 0.782 | 0.684 | 0.773 | 6.67 | 8.42 | 6.25 | 0.815 | 0.798 | 0.756 | 6.6 | -5.31 | 6.9 | Very Poor_Mixed | 2226.6 | 2722.8 | 1.114 | 0.979 | 9.27 | 0.815 | 8.42 | 0.1659 | 0.6415 | 0.1436 | 0.3368 | 1 | 0.0707 | 0.3296 | 0.3789 | 0.3789 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
238 | 893.2 | 529.5 | 107.7 | 120.8 | 16.4 | 819.8 | 5602.5 | 46.5 | 32.9 | 91.2 | 90.8 | 83.2 | 98.2 | 40.4 | 23.9 | 5102.2 | 5795.3 | 5965.2 | 7579.1 | 8649 | 9329.3 | 1.485 | 1.492 | 1.564 | 0.659 | 0.716 | 0.712 | -4.83 | 4.49 | 6.35 | 0.698 | 0.713 | 0.714 | 4 | 3.51 | 6.31 | 0.718 | 0.563 | 0.63 | 4.14 | 5.03 | 5.85 | 0.757 | 0.715 | 0.672 | 4.83 | 4.81 | -3.99 | Poor_Mixed | 5102.2 | 7579.1 | 1.485 | 0.716 | 6.35 | 0.757 | 6.31 | 0.4382 | 0.7593 | 0.498 | 0.6177 | 1 | 0.482 | 0.473 | 0.594 | 0.594 | Poor | 0 | 1 | DGA | 0 |  | C2H2
239 | 326.3 | 316.6 | 82.1 | 83.6 | 40.3 | 567.2 | 3186.1 | 52.9 | 24.5 | 77.6 | 80.9 | 74.3 | 82 | 37 | 13.4 | 690 | 690 | 1235.2 | 722.4 | 734.7 | 1302.4 | 1.047 | 1.065 | 1.054 | 0.718 | 0.762 | 0.714 | 5.85 | 5.77 | -5.9 | 0.573 | 0.563 | 0.564 | 3.21 | 3.12 | 2.83 | 0.584 | 0.533 | 0.574 | 3.09 | -2.6 | 3.58 | 0.609 | 0.606 | 0.512 | 3.5 | 2.55 | 3.28 | Critical_IR_PI | 690 | 722.4 | 1.047 | 0.762 | 5.9 | 0.609 | 3.58 | 0.5263 | 0.8786 | 0.8375 | 0.9342 | 0.85 | 0.4142 | 0.7123 | 0.6897 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
240 | 1512.6 | 772.2 | 136.4 | 172 | 30 | 1119.7 | 7908.8 | 37.5 | 44.4 | 104.8 | 104.6 | 91.9 | 113.3 | 43.7 | 32.6 | 3072.2 | 2266.6 | 2618 | 3543 | 2683.1 | 3093.8 | 1.153 | 1.184 | 1.182 | 0.924 | 0.964 | 0.893 | 9.41 | 8.6 | -8.27 | 0.694 | 0.798 | 0.848 | -7.87 | 6.75 | 7.67 | 0.809 | 0.926 | 0.753 | 5.51 | -7.65 | 9.28 | 0.95 | 0.828 | 0.789 | 8.8 | -6.6 | 5.92 | Very Poor_Mixed | 2266.6 | 2683.1 | 1.153 | 0.964 | 9.41 | 0.95 | 9.28 | 0.1605 | 0.6357 | 0.1839 | 0.2982 | 1 | 0.1107 | 0.2384 | 0.3681 | 0.3681 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
241 | 378.3 | 268.4 | 81.3 | 93.1 | 38.3 | 615 | 3918.6 | 55.9 | 21.5 | 79.9 | 79.7 | 74.9 | 85.5 | 35.2 | 11.9 | 9438.2 | 8506.7 | 8917.4 | 17832.2 | 15720.8 | 17162.9 | 1.889 | 1.848 | 1.925 | 0.615 | 0.661 | 0.636 | 3.57 | 4.12 | 4.21 | 0.57 | 0.516 | 0.94 | 2 | 3.4 | 9.31 | 0.588 | 0.533 | 0.599 | 3.67 | 2.54 | -2.41 | 0.649 | 0.617 | 0.517 | 2.67 | 3.16 | 3.18 | Critical_Bushing_TD_Cap | 8506.7 | 15720.8 | 1.848 | 0.661 | 4.21 | 0.94 | 9.31 | 0.5047 | 0.9406 | 0.8123 | 0.9682 | 1 | 0.6131 | 0.6484 | 0.7313 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
242 | 845.5 | 483.2 | 105.8 | 104.4 | 20.1 | 886.6 | 5640.5 | 45.6 | 34.2 | 92.3 | 89.1 | 84.6 | 98.6 | 39.9 | 26.5 | 5791 | 5859.7 | 6451.7 | 8673.4 | 8211.4 | 10308 | 1.498 | 1.401 | 1.598 | 0.772 | 0.772 | 0.688 | 5.95 | 6.15 | 5.43 | 0.676 | 0.75 | 0.701 | 5.87 | -6.08 | 4.8 | 0.748 | 0.604 | 0.754 | -4.15 | 4.89 | -5.05 | 0.619 | 0.673 | 0.645 | 4.85 | 4.01 | 4.71 | Poor_Mixed | 5791 | 8211.4 | 1.401 | 0.772 | 6.15 | 0.754 | 6.08 | 0.4334 | 0.7438 | 0.4947 | 0.5264 | 1 | 0.404 | 0.4646 | 0.5736 | 0.5736 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
243 | 534.5 | 395.1 | 90.9 | 96 | 2.5 | 757.4 | 4217.9 | 32.5 | 49.4 | 85.1 | 85.1 | 79.7 | 89.9 | 38.3 | 21.3 | 4222.5 | 4473.3 | 494.8 | 5769 | 6378.7 | 533.3 | 1.366 | 1.426 | 1.078 | 0.654 | 0.647 | 0.671 | 4.22 | 4.71 | -5.06 | 0.582 | 0.624 | 0.526 | 3.16 | 2.4 | 3.95 | 0.544 | 0.598 | 0.561 | 2.11 | -3.26 | -2.28 | 0.551 | 0.609 | 0.553 | 3.17 | 2.68 | 3.41 | Critical_Oil | 494.8 | 533.3 | 1.078 | 0.671 | 5.06 | 0.624 | 3.95 | 0.6866 | 0.5888 | 0.6563 | 0.7049 | 0.85 | 0.5503 | 0.7127 | 0.6845 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
244 | 935.8 | 472.7 | 105 | 118.6 | 14 | 815.4 | 5006.9 | 45.5 | 32.3 | 91 | 89.2 | 81.6 | 97.4 | 39.6 | 24.4 | 6970.2 | 5462.1 | 6332.8 | 11495.5 | 8284.1 | 9646.5 | 1.649 | 1.517 | 1.523 | 0.713 | 0.733 | 0.748 | 4.98 | 5 | 6.01 | 0.759 | 0.707 | 0.66 | 4.3 | 5.33 | 4.13 | 0.713 | 0.669 | 0.71 | 4.08 | -5.56 | 4.81 | 0.689 | 0.611 | 0.68 | 4.81 | -3.56 | -4.93 | Poor_Mixed | 5462.1 | 8284.1 | 1.517 | 0.748 | 6.01 | 0.759 | 5.56 | 0.4684 | 0.7666 | 0.5292 | 0.6005 | 1 | 0.4427 | 0.4708 | 0.5988 | 0.5988 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
245 | 984.2 | 496 | 107.9 | 118.7 | 15 | 813.6 | 5395.2 | 47.2 | 30.6 | 88.9 | 90.8 | 83.1 | 99.5 | 40.7 | 24.3 | 5152.2 | 5693 | 6482.6 | 7519 | 8661.2 | 10886 | 1.459 | 1.521 | 1.679 | 0.714 | 0.765 | 0.72 | 5.66 | 6.23 | 5.33 | 0.594 | 0.637 | 0.631 | 4.4 | 5.18 | 5.04 | 0.665 | 0.674 | 0.681 | 5.06 | -4.77 | -3.51 | 0.628 | 0.697 | 0.682 | 4.63 | 4.37 | 5.7 | Poor_Mixed | 5152.2 | 7519 | 1.459 | 0.765 | 6.23 | 0.697 | 5.7 | 0.4491 | 0.7881 | 0.5054 | 0.6039 | 1 | 0.4184 | 0.5085 | 0.5977 | 0.5977 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
246 | 1645.3 | 912.3 | 139.2 | 181.7 | 31.6 | 1290.3 | 7781 | 32.8 | 45.3 | 104.8 | 106.2 | 94 | 115.7 | 43.9 | 32.7 | 2108.9 | 1888.9 | 1130.3 | 2517.3 | 2048.8 | 1233.3 | 1.194 | 1.085 | 1.091 | 0.973 | 0.916 | 0.974 | 9.6 | 8.68 | 9.7 | 0.784 | 0.732 | 0.926 | 7.39 | 7.31 | -7.76 | 0.754 | 0.911 | 0.752 | 5.48 | 7.82 | 6.38 | 0.651 | 0.915 | 0.812 | 6.83 | 6.87 | 5.95 | Very Poor_Mixed | 1130.3 | 1233.3 | 1.085 | 0.974 | 9.7 | 0.926 | 7.82 | 0.1008 | 0.627 | 0.1498 | 0.2943 | 1 | 0.0637 | 0.2724 | 0.3481 | 0.3481 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
247 | 196.3 | 278.4 | 81.5 | 76.7 | 1.4 | 530 | 3369 | 55.4 | 25 | 77.4 | 75.3 | 70 | 81.6 | 35.7 | 12.5 | 4718.2 | 3897.2 | 4232.9 | 6774.6 | 5489.3 | 5842 | 1.436 | 1.409 | 1.38 | 0.62 | 0.647 | 0.656 | 4.29 | 5.28 | 4.13 | 0.517 | 0.563 | 0.576 | 2.62 | -2.95 | 2.1 | 0.543 | 0.592 | 0.582 | 3.08 | -3.72 | 2.59 | 0.565 | 0.565 | 0.599 | -2.62 | -2.31 | 2.41 | Poor_IR_PI | 3897.2 | 5489.3 | 1.38 | 0.656 | 5.28 | 0.599 | 3.72 | 0.8334 | 0.87 | 0.9489 | 0.9552 | 1 | 0.5735 | 0.7314 | 0.8273 | 0.8273 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
248 | 1562 | 950.8 | 142.4 | 190.3 | 32.8 | 1379 | 8725 | 31.7 | 45.7 | 103.8 | 103.6 | 91.2 | 112.1 | 44.6 | 32.4 | 1649.3 | 1856.9 | 2112.4 | 2036.7 | 2054.7 | 2220.4 | 1.235 | 1.107 | 1.051 | 0.94 | 0.956 | 0.925 | 8.47 | 9.42 | 8.85 | 0.834 | 0.899 | 0.894 | 5.84 | 6.73 | 8.01 | 0.832 | 0.804 | 0.905 | 7.94 | 7.18 | 6.23 | 0.888 | 0.942 | 0.795 | 8.13 | -7.89 | 8.31 | Very Poor_Mixed | 1649.3 | 2036.7 | 1.051 | 0.956 | 9.42 | 0.942 | 8.31 | 0.0656 | 0.6232 | 0.1986 | 0.3059 | 1 | 0.0936 | 0.1944 | 0.3344 | 0.3344 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
249 | 1533.7 | 909.5 | 142.3 | 181.1 | 34.3 | 1219.4 | 7984.8 | 32.5 | 47 | 108 | 107 | 95.6 | 114.8 | 44.4 | 33.3 | 2651.2 | 2129 | 2391.8 | 3229.1 | 2584.4 | 2593.4 | 1.218 | 1.214 | 1.084 | 0.961 | 0.909 | 0.925 | 9.57 | 9.27 | -9.11 | 0.987 | 0.866 | 0.768 | 6.62 | 8.06 | 7.31 | 0.923 | 0.712 | 0.829 | 6.44 | -6.72 | 6.56 | 0.84 | 0.841 | 0.735 | 8.85 | -6.03 | -8.28 | Very Poor_Mixed | 2129 | 2584.4 | 1.084 | 0.961 | 9.57 | 0.987 | 8.85 | 0.1004 | 0.6109 | 0.1198 | 0.2709 | 1 | 0.0793 | 0.2318 | 0.3368 | 0.3368 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
250 | 362.1 | 253 | 72 | 59.2 | 1 | 496.2 | 3541.8 | 21.9 | 21.7 | 79.5 | 83.2 | 75 | 88.5 | 36.4 | 18.2 | 6829.1 | 7891.3 | 7266.3 | 11873.1 | 14019.2 | 13133.5 | 1.739 | 1.777 | 1.807 | 0.962 | 0.918 | 0.907 | 9.05 | -9.02 | -8.34 | 0.54 | 0.515 | 0.531 | 2.49 | -2.61 | 2.29 | 0.52 | 0.5 | 0.528 | 2 | 2 | -2.36 | 0.518 | 0.548 | 0.54 | 2 | -2.6 | 2.1 | Critical_Winding_TD_Cap | 6829.1 | 11873.1 | 1.739 | 0.962 | 9.05 | 0.548 | 2.61 | 0.8972 | 0.3522 | 0.7661 | 0.8024 | 1 | 0.107 | 0.8518 | 0.7116 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
251 | 811.6 | 559.8 | 107.7 | 126.5 | 16 | 871.1 | 5204.5 | 44.6 | 35 | 92.6 | 89.8 | 83.8 | 97.3 | 40.5 | 25.1 | 5844.1 | 5353.9 | 5825.9 | 9111.2 | 8439.9 | 8485.1 | 1.559 | 1.576 | 1.456 | 0.727 | 0.739 | 0.755 | 5.7 | 5.65 | 5.95 | 0.697 | 0.706 | 0.747 | 5.57 | 3.77 | 5.18 | 0.714 | 0.668 | 0.733 | 6.77 | 5.4 | 3.73 | 0.616 | 0.677 | 0.646 | -5.28 | 4.92 | 5.83 | Poor_Mixed | 5353.9 | 8439.9 | 1.456 | 0.755 | 5.95 | 0.747 | 6.77 | 0.4362 | 0.7345 | 0.4957 | 0.576 | 1 | 0.4102 | 0.4503 | 0.574 | 0.574 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
252 | 668.6 | 475.1 | 103.9 | 112.1 | 17.1 | 797.2 | 5642.1 | 46.2 | 34.9 | 91.7 | 92 | 81.4 | 100.6 | 40.2 | 24.3 | 5872.9 | 6378.9 | 6746.9 | 9283.2 | 9818 | 11665.1 | 1.581 | 1.539 | 1.729 | 0.771 | 0.772 | 0.739 | -5.87 | 6.16 | 5.21 | 0.719 | 0.656 | 0.717 | 5.12 | 5.17 | 4.66 | 0.671 | 0.627 | 0.7 | 2.9 | -3.91 | 5.11 | 0.696 | 0.705 | 0.658 | 5.91 | 3.85 | -5.24 | Poor_Mixed | 5872.9 | 9283.2 | 1.539 | 0.772 | 6.16 | 0.719 | 5.91 | 0.4716 | 0.7356 | 0.4877 | 0.6039 | 1 | 0.3943 | 0.4756 | 0.5859 | 0.5859 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
253 | 825.4 | 626.4 | 104.5 | 116.7 | 17.4 | 863.5 | 5781 | 57.4 | 23.7 | 78.1 | 75 | 71.1 | 83 | 35 | 11.9 | 8895.2 | 9412.1 | 9928.2 | 17014.3 | 17717 | 19397.9 | 1.913 | 1.882 | 1.954 | 0.554 | 0.555 | 0.555 | 2.12 | 3.62 | 2.84 | 0.53 | 0.507 | 0.5 | -2.1 | 2.46 | -2.22 | 0.512 | 0.547 | 0.535 | 2.13 | 2.69 | -2 | 0.534 | 0.558 | 0.506 | -2.42 | -2.63 | 2.29 | Poor_DGA | 8895.2 | 17014.3 | 1.882 | 0.555 | 3.62 | 0.558 | 2.69 | 0.4253 | 0.8931 | 0.9302 | 0.9682 | 1 | 0.7911 | 0.8564 | 0.7798 | 0.7798 | Fair | 1 | 1 | DGA | 0 |  | C2H2
254 | 448.3 | 246.5 | 74.7 | 127.6 | 3.1 | 469.8 | 3120.4 | 56.7 | 23.1 | 92.5 | 90 | 84 | 98.2 | 40.6 | 10 | 8685.2 | 8627.2 | 8860.8 | 16992.7 | 16194.1 | 16781 | 1.957 | 1.877 | 1.894 | 0.5 | 0.5 | 0.542 | 2.21 | 2.25 | 3.43 | 0.551 | 0.531 | 0.5 | 2.73 | 2.37 | 2.04 | 0.542 | 0.533 | 0.537 | -3.04 | 2.39 | 2.23 | 0.518 | 0.545 | 0.567 | 2.6 | 2.83 | 2.81 | Poor_Thermal | 8627.2 | 16194.1 | 1.877 | 0.542 | 3.43 | 0.567 | 3.04 | 0.7264 | 0.9047 | 0.4886 | 1 | 1 | 0.9086 | 0.8115 | 0.8223 | 0.8223 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
255 | 1495.6 | 902.2 | 138.1 | 176.8 | 25 | 1221.1 | 8538.1 | 34.4 | 44.5 | 101 | 106.9 | 92.8 | 115 | 43.5 | 31 | 3044.6 | 1547.3 | 1910.7 | 3784.2 | 1778.4 | 2119 | 1.243 | 1.149 | 1.109 | 0.89 | 0.893 | 0.87 | 8.09 | 7.57 | 8.36 | 0.811 | 0.86 | 0.767 | 5.67 | -7.05 | 6.1 | 0.812 | 0.803 | 0.758 | -6.51 | 6.7 | 8.27 | 0.776 | 0.741 | 0.906 | -8.72 | 7.14 | 7.31 | Very Poor_Mixed | 1547.3 | 1778.4 | 1.109 | 0.893 | 8.36 | 0.906 | 8.72 | 0.1469 | 0.6347 | 0.1806 | 0.3597 | 1 | 0.1787 | 0.2623 | 0.3812 | 0.3812 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
256 | 292.9 | 235.5 | 75.5 | 64.1 | 4.5 | 453.8 | 3650.9 | 56.3 | 23.7 | 79.8 | 78.6 | 74.2 | 84.1 | 36.6 | 10.3 | 8707.9 | 8630.9 | 8583 | 17388.6 | 15899.6 | 16664 | 1.997 | 1.842 | 1.942 | 0.76 | 0.815 | 0.806 | 6.37 | 6.42 | 6.3 | 0.547 | 0.6 | 0.528 | 2.19 | 2.46 | 2.68 | 0.571 | 0.557 | 0.5 | 2 | -2.79 | 2.41 | 0.539 | 0.542 | 0.539 | 2 | 3.02 | -2.79 | Poor_Winding_TD_Cap | 8583 | 15899.6 | 1.842 | 0.815 | 6.42 | 0.6 | 3.02 | 0.7875 | 0.8931 | 0.8294 | 0.9968 | 1 | 0.3337 | 0.7928 | 0.7863 | 0.7863 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
257 | 128.8 | 191.8 | 70.3 | 55.5 | 3.7 | 366.4 | 3484.8 | 60 | 21.8 | 75.9 | 75.9 | 70 | 80 | 35.6 | 12.6 | 10000 | 7738.6 | 9891.7 | 20000 | 14221.7 | 19658.2 | 2 | 1.838 | 1.987 | 0.5 | 0.546 | 0.537 | 2 | 2.21 | 2.12 | 0.5 | 0.536 | 0.545 | 2.48 | -2.27 | 2.93 | 0.535 | 0.518 | 0.558 | 2 | 2.63 | -2 | 0.52 | 0.5 | 0.552 | 3.17 | 2.53 | 2.46 | Good_Mixed | 7738.6 | 14221.7 | 1.838 | 0.546 | 2.21 | 0.558 | 3.17 | 0.858 | 0.9331 | 0.9658 | 0.953 | 1 | 0.9085 | 0.8407 | 0.9092 | 0.9092 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
258 | 100 | 172.4 | 71.9 | 53.8 | 1.2 | 423.2 | 3491.6 | 60 | 20 | 77.2 | 77.6 | 71.5 | 82.8 | 35 | 11.6 | 10000 | 9995.6 | 8395.3 | 19284.8 | 19991.2 | 16051.2 | 1.928 | 2 | 1.912 | 0.525 | 0.542 | 0.555 | 2 | 2 | 2.23 | 0.5 | 0.513 | 0.524 | 2 | 2 | 2 | 0.506 | 0.531 | 0.517 | -2.01 | 2 | 2.58 | 0.5 | 0.501 | 0.5 | 2 | 2.11 | 2 | Good_Mixed | 8395.3 | 16051.2 | 1.912 | 0.555 | 2.23 | 0.531 | 2.58 | 0.9261 | 1 | 0.9008 | 0.9744 | 1 | 0.8749 | 0.9312 | 0.9404 | 0.9404 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
259 | 965.4 | 607.2 | 106.6 | 118.3 | 18.3 | 861.4 | 6344.3 | 55.5 | 22.4 | 75 | 76.7 | 73.2 | 82.8 | 35.8 | 13.2 | 8209.3 | 7724.3 | 7323 | 14625.1 | 13338.5 | 12886.5 | 1.782 | 1.727 | 1.76 | 0.581 | 0.505 | 0.558 | 3 | 2.84 | 3.03 | 0.582 | 0.601 | 0.59 | 3.55 | 3.2 | 3.85 | 0.583 | 0.572 | 0.575 | 3.34 | 4.29 | 3.31 | 0.536 | 0.572 | 0.555 | -2.67 | 2.35 | 2.27 | Poor_DGA | 7323 | 12886.5 | 1.727 | 0.581 | 3.03 | 0.601 | 4.29 | 0.4017 | 0.9193 | 0.9238 | 0.939 | 1 | 0.8035 | 0.6931 | 0.7473 | 0.7473 | Fair | 1 | 1 | DGA | 0 |  | C2H2
260 | 913.9 | 578.6 | 106.6 | 121.4 | 17.8 | 885.2 | 5508.3 | 45.2 | 33.6 | 86.8 | 90 | 80.6 | 95.6 | 38.5 | 22.6 | 5397.1 | 5305.8 | 6064.2 | 8518.5 | 7664.7 | 9861.6 | 1.578 | 1.445 | 1.626 | 0.737 | 0.726 | 0.753 | 5.53 | -5.7 | -5.45 | 0.606 | 0.707 | 0.642 | -5.17 | 4.24 | -3.89 | 0.674 | 0.628 | 0.619 | 4.38 | 4.78 | 5.94 | 0.632 | 0.66 | 0.713 | 4.83 | 4.44 | 3.98 | Poor_Mixed | 5305.8 | 7664.7 | 1.445 | 0.753 | 5.7 | 0.713 | 5.94 | 0.4153 | 0.7509 | 0.5745 | 0.6619 | 1 | 0.4231 | 0.5142 | 0.5963 | 0.5963 | Poor | 0 | 1 | DGA | 0 |  | C2H2
261 | 389.7 | 270 | 80.1 | 65.2 | 77.9 | 507.3 | 3577.8 | 32.9 | 48.4 | 78.8 | 75.1 | 71.6 | 83.1 | 36.5 | 17 | 4353.7 | 4488 | 5664.1 | 6507.1 | 6393.3 | 8924 | 1.495 | 1.425 | 1.576 | 0.621 | 0.64 | 0.667 | 4.06 | -4.28 | 5.71 | 0.59 | 0.548 | 0.593 | -2.85 | 2.77 | 2.11 | 0.591 | 0.508 | 0.611 | -3.17 | 3.17 | 3.43 | 0.6 | 0.644 | 0.531 | -3.5 | 2.61 | 3.57 | Critical_Oil | 4353.7 | 6393.3 | 1.425 | 0.667 | 5.71 | 0.644 | 3.57 | 0.5568 | 0.5979 | 0.9086 | 0.8378 | 1 | 0.5655 | 0.7003 | 0.7089 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
262 | 418.7 | 277.9 | 82.8 | 68.9 | 1 | 553.8 | 3534.7 | 54.3 | 27.7 | 81.7 | 80.3 | 74.8 | 87.1 | 36.8 | 13.7 | 8512 | 7870.3 | 352.2 | 16002 | 13474.8 | 411.9 | 1.88 | 1.712 | 1.17 | 0.57 | 0.543 | 0.528 | -3.13 | 2.46 | 2.82 | 0.514 | 0.58 | 0.611 | 3.96 | 3.15 | 3.11 | 0.984 | 0.576 | 0.626 | 8.75 | -4.08 | 3.45 | 0.513 | 0.575 | 0.579 | 3.11 | 2 | 3.99 | Critical_Bushing_TD_Cap | 352.2 | 411.9 | 1.17 | 0.57 | 3.13 | 0.984 | 8.75 | 0.8597 | 0.8279 | 0.7774 | 0.9269 | 0.85 | 0.8072 | 0.6288 | 0.8005 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
263 | 465 | 356.7 | 97.6 | 94.9 | 14.3 | 641.6 | 4686.3 | 55 | 25.7 | 75.8 | 79.5 | 72 | 82.1 | 35.9 | 14.8 | 9212.8 | 8866.3 | 9319.5 | 16987.6 | 17117.3 | 17880.3 | 1.844 | 1.931 | 1.919 | 0.537 | 0.585 | 0.557 | 2.96 | -2 | 3.15 | 0.541 | 0.5 | 0.5 | 2 | 2 | 2 | 0.511 | 0.531 | 0.532 | 2 | -2.29 | 2 | 0.5 | 0.509 | 0.582 | 2 | -2.27 | 2.21 | Fair_DGA | 8866.3 | 16987.6 | 1.844 | 0.585 | 3.15 | 0.582 | 2.29 | 0.5736 | 0.8584 | 0.8948 | 0.8988 | 1 | 0.7971 | 0.8931 | 0.8132 | 0.8132 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
264 | 505 | 257.4 | 83.9 | 153.3 | 2.1 | 643.6 | 4475.7 | 51.9 | 28.9 | 108.6 | 114.1 | 96.6 | 119.2 | 44.9 | 15.3 | 7747.3 | 7242.1 | 6899.6 | 12924.2 | 12872.8 | 11903.5 | 1.668 | 1.777 | 1.725 | 0.554 | 0.598 | 0.588 | -2.7 | -3.86 | -3.17 | 0.625 | 0.544 | 0.614 | 3.03 | 3.92 | 3.05 | 0.544 | 0.573 | 0.692 | 2.93 | 2 | 4.13 | 0.565 | 0.601 | 0.626 | 2.9 | -3.46 | 3.29 | Critical_Thermal | 6899.6 | 11903.5 | 1.668 | 0.598 | 3.86 | 0.692 | 4.13 | 0.6779 | 0.8109 | 0.0692 | 0.8855 | 1 | 0.7284 | 0.6581 | 0.6984 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | C2H4
265 | 507.8 | 280.4 | 84.3 | 85.9 | 1.9 | 616.8 | 3858.7 | 52.3 | 88.4 | 78.6 | 82.1 | 73.4 | 86.6 | 37.3 | 14.6 | 8443.1 | 8146 | 8360.1 | 15384.7 | 14214.4 | 16119.7 | 1.822 | 1.745 | 1.928 | 0.6 | 0.544 | 0.575 | -3.51 | 4.06 | -3.71 | 0.539 | 0.523 | 0.605 | -3.67 | 3.74 | 3.32 | 0.987 | 0.52 | 0.625 | 9.84 | 4.77 | -3.42 | 0.543 | 0.552 | 0.554 | 3.79 | 4.44 | 2.93 | Critical_Bushing_TD_Cap | 8146 | 14214.4 | 1.745 | 0.6 | 4.06 | 0.987 | 9.84 | 0.7557 | 0.5833 | 0.8005 | 0.904 | 1 | 0.7052 | 0.6304 | 0.7564 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
266 | 905.6 | 509.6 | 107.7 | 120.6 | 18.6 | 838.7 | 5842 | 47.3 | 33.1 | 91.1 | 90.5 | 80.7 | 95 | 39.9 | 25.7 | 5583.3 | 4060.9 | 6703.6 | 8563 | 5828.1 | 11191 | 1.534 | 1.435 | 1.669 | 0.713 | 0.66 | 0.732 | 5.52 | 4.36 | 6.05 | 0.678 | 0.582 | 0.645 | 4.68 | 5.11 | -3.8 | 0.699 | 0.599 | 0.642 | 5.03 | -5.57 | 5.03 | 0.656 | 0.762 | 0.764 | 5.28 | 4.44 | 4.97 | Poor_Mixed | 4060.9 | 5828.1 | 1.435 | 0.732 | 6.05 | 0.764 | 5.57 | 0.4208 | 0.7568 | 0.5359 | 0.5549 | 1 | 0.4716 | 0.4877 | 0.5912 | 0.5912 | Poor | 0 | 1 | DGA | 0 |  | C2H2
267 | 1583.2 | 973.1 | 144.3 | 179 | 33 | 1275.6 | 8118.9 | 31.2 | 48.7 | 108.3 | 106.3 | 94.3 | 115.8 | 44.5 | 35.4 | 1541.7 | 1808.7 | 1481.1 | 1830.2 | 2290 | 1592.9 | 1.187 | 1.266 | 1.075 | 0.934 | 0.953 | 0.948 | -8.93 | 9.58 | 8.97 | 0.808 | 0.716 | 0.924 | 7.44 | 7.99 | -8.91 | 0.898 | 0.922 | 0.823 | 7.67 | 9.36 | 7.38 | 0.822 | 0.91 | 0.819 | 8.88 | 9.84 | 6.07 | Very Poor_Mixed | 1481.1 | 1592.9 | 1.075 | 0.953 | 9.58 | 0.924 | 9.84 | 0.0878 | 0.5952 | 0.1235 | 0.1878 | 1 | 0.078 | 0.1851 | 0.3194 | 0.3194 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
268 | 1317.5 | 686.2 | 127.9 | 152.6 | 62.3 | 1163.3 | 7192.4 | 39.2 | 42.3 | 101.8 | 103.6 | 91.5 | 107.9 | 42.9 | 36.1 | 2548.1 | 2554.8 | 1901.9 | 3223.1 | 3237.3 | 2244.5 | 1.265 | 1.267 | 1.18 | 0.919 | 0.922 | 0.859 | 9.04 | 9.08 | 8.4 | 0.791 | 0.782 | 0.859 | 6.32 | 5.86 | 6.62 | 0.673 | 0.786 | 0.697 | 5.03 | 5.02 | 6.85 | 0.76 | 0.661 | 0.84 | 5.19 | 5.8 | 8.1 | Critical_Mixed | 1901.9 | 2244.5 | 1.18 | 0.922 | 9.08 | 0.859 | 8.1 | 0.1894 | 0.6564 | 0.2415 | 0.1598 | 1 | 0.1254 | 0.34 | 0.397 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
269 | 977.6 | 503.4 | 104.6 | 127.4 | 17.4 | 900.8 | 5282.8 | 43.9 | 35.1 | 90.6 | 93.2 | 81.5 | 99 | 39.5 | 24.6 | 6994.8 | 5858.4 | 6296.2 | 11518.4 | 8982.1 | 9997.3 | 1.647 | 1.533 | 1.588 | 0.764 | 0.763 | 0.674 | 5.9 | 5.85 | -5.76 | 0.723 | 0.655 | 0.678 | 4.71 | 5.54 | 4.94 | 0.691 | 0.634 | 0.763 | 5.53 | 5.07 | 5.79 | 0.706 | 0.64 | 0.605 | -4.88 | 4.17 | -5.71 | Poor_Mixed | 5858.4 | 8982.1 | 1.533 | 0.764 | 5.9 | 0.763 | 5.79 | 0.4174 | 0.7333 | 0.4991 | 0.5935 | 1 | 0.4134 | 0.4657 | 0.5736 | 0.5736 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
270 | 300.9 | 177.2 | 71.7 | 57.9 | 1 | 441.6 | 2688.5 | 53.1 | 25.4 | 75 | 79 | 71.9 | 80.5 | 35 | 14.2 | 9076.2 | 9821 | 9213 | 17173.9 | 19335.5 | 17742.9 | 1.892 | 1.969 | 1.926 | 0.746 | 0.753 | 0.775 | 5.43 | -5.3 | -5.99 | 0.5 | 0.5 | 0.5 | -2.64 | 2.13 | 2.23 | 0.527 | 0.568 | 0.5 | 2.67 | 2 | 2 | 0.531 | 0.511 | 0.5 | -2.42 | 2 | 2.17 | Poor_Winding_TD_Cap | 9076.2 | 17173.9 | 1.892 | 0.775 | 5.99 | 0.568 | 2.67 | 0.9285 | 0.8633 | 0.9264 | 0.9144 | 1 | 0.406 | 0.9152 | 0.8556 | 0.8556 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
271 | 1554.5 | 785.9 | 133.8 | 165.5 | 34.3 | 1221.8 | 8360.2 | 36.4 | 42.1 | 103.3 | 102.8 | 93.5 | 112.8 | 44.3 | 32.6 | 2347.8 | 1754.9 | 1567 | 2569.4 | 2051.5 | 1719.1 | 1.094 | 1.169 | 1.097 | 0.883 | 0.861 | 0.831 | 7.91 | -7.93 | 7.92 | 0.909 | 0.883 | 0.717 | 7.23 | -8.12 | 6.92 | 0.8 | 0.817 | 0.895 | 8.64 | 5.29 | 7.35 | 0.731 | 0.749 | 0.93 | -5.37 | -6.78 | 7.66 | Very Poor_Mixed | 1567 | 1719.1 | 1.094 | 0.883 | 7.93 | 0.93 | 8.64 | 0.1271 | 0.6584 | 0.1916 | 0.2982 | 1 | 0.2021 | 0.2445 | 0.3772 | 0.3772 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
272 | 451.5 | 164.4 | 72.5 | 97.2 | 1 | 554.9 | 3217.5 | 56.3 | 22.9 | 91.7 | 92 | 80.9 | 98.1 | 39.7 | 14.5 | 7859 | 8942.2 | 10000 | 14225.2 | 16443.1 | 20000 | 1.81 | 1.839 | 2 | 0.637 | 0.617 | 0.603 | 3.97 | 2.88 | -4.02 | 0.578 | 0.562 | 0.566 | -3.29 | -2.48 | 2.92 | 0.562 | 0.545 | 0.614 | -2.94 | -2.45 | 3.34 | 0.521 | 0.562 | 0.601 | -2.68 | 2.35 | 2.17 | Poor_Thermal | 7859 | 14225.2 | 1.81 | 0.637 | 4.02 | 0.614 | 3.34 | 0.8453 | 0.9088 | 0.5067 | 0.9067 | 1 | 0.6552 | 0.728 | 0.7992 | 0.7992 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H4
273 | 109.3 | 126.7 | 65 | 54.2 | 1 | 350 | 2500 | 60 | 20.8 | 77.5 | 75.3 | 73.1 | 81.3 | 35.9 | 13.9 | 9122.3 | 10000 | 9742.5 | 17583.1 | 18256.7 | 19484.9 | 1.927 | 1.826 | 2 | 0.5 | 0.51 | 0.559 | -2 | -2 | 3.24 | 0.567 | 0.571 | 0.533 | -2.93 | 3.57 | 2.76 | 0.606 | 0.557 | 0.577 | 3.01 | 3.4 | 3.11 | 0.565 | 0.552 | 0.51 | 2.5 | 2.91 | 2.53 | Good_Mixed | 9122.3 | 17583.1 | 1.826 | 0.559 | 3.24 | 0.606 | 3.57 | 0.9864 | 0.9605 | 0.916 | 0.9219 | 1 | 0.9017 | 0.7341 | 0.9179 | 0.9179 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
274 | 407 | 302.2 | 87.7 | 73.4 | 52.2 | 539.3 | 3878.1 | 60 | 22.2 | 79.3 | 78.8 | 72.2 | 83 | 36.4 | 19.1 | 7441.9 | 8412.4 | 7479.2 | 12605.7 | 14813.1 | 12838.5 | 1.694 | 1.761 | 1.717 | 0.581 | 0.606 | 0.509 | 3.25 | -3.23 | 2.75 | 0.589 | 0.919 | 0.647 | 2.69 | 9.45 | 3.75 | 0.519 | 0.589 | 0.597 | 3.63 | 2.48 | 2.84 | 0.538 | 0.553 | 0.527 | 3.53 | 3.3 | 3.83 | Critical_Bushing_TD_Cap | 7441.9 | 12605.7 | 1.694 | 0.606 | 3.25 | 0.919 | 9.45 | 0.5284 | 0.9238 | 0.8553 | 0.7749 | 1 | 0.7695 | 0.6367 | 0.7496 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
275 | 388.4 | 290.3 | 76.4 | 78.7 | 2.7 | 538.8 | 3441.7 | 58.5 | 22.6 | 80.5 | 78 | 72.8 | 84.7 | 35.4 | 13.7 | 9765.8 | 8587.5 | 8494.1 | 19531.6 | 15890.7 | 15055 | 2 | 1.85 | 1.772 | 0.813 | 0.759 | 0.744 | 6.78 | 6.47 | -5.87 | 0.508 | 0.518 | 0.534 | 2 | -2 | 2 | 0.557 | 0.536 | 0.527 | 2 | 2.01 | 2.58 | 0.511 | 0.579 | 0.517 | 2.98 | 2.57 | 2.02 | Poor_Winding_TD_Cap | 8494.1 | 15055 | 1.772 | 0.813 | 6.78 | 0.579 | 2.98 | 0.7723 | 0.915 | 0.8432 | 0.9269 | 1 | 0.351 | 0.8397 | 0.7938 | 0.7938 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
276 | 654.1 | 360.6 | 95.3 | 94 | 4.2 | 698.6 | 4010.3 | 35.2 | 44.7 | 81.4 | 83.3 | 75.5 | 89.5 | 38.4 | 12.2 | 5535.9 | 5969.7 | 6011.4 | 8312 | 8811.2 | 8802 | 1.501 | 1.476 | 1.464 | 1.355 | 0.651 | 0.691 | -5.57 | -4.91 | 4.24 | 0.559 | 0.589 | 0.629 | -3.06 | 3.45 | 2.51 | 0.561 | 0.587 | 0.588 | 3.09 | -3.58 | 3.78 | 0.61 | 0.544 | 0.612 | 3.11 | 2.32 | 3.51 | Critical_Oil | 5535.9 | 8312 | 1.464 | 1.355 | 5.57 | 0.629 | 3.78 | 0.6571 | 0.6328 | 0.7293 | 0.9618 | 1 | 0.4382 | 0.6736 | 0.7038 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | Moisture_PPM
277 | 1534.2 | 863.8 | 137.5 | 175.4 | 27.9 | 1277.2 | 8006.7 | 32.9 | 45.2 | 106.9 | 104.3 | 91.5 | 114.4 | 44.7 | 31.7 | 2232.2 | 781.6 | 1514.5 | 2787.7 | 1200 | 1834.7 | 1.249 | 1.535 | 1.211 | 0.91 | 0.931 | 0.939 | 8.95 | 8.89 | 8.67 | 0.871 | 0.76 | 0.884 | 6.4 | 8.1 | 8.44 | 0.826 | 0.858 | 0.769 | 8.53 | 6.24 | -8.45 | 0.807 | 0.766 | 0.81 | 7.86 | -7.99 | -8.21 | Very Poor_Mixed | 781.6 | 1200 | 1.211 | 0.939 | 8.95 | 0.884 | 8.53 | 0.1363 | 0.628 | 0.1635 | 0.3329 | 1 | 0.1067 | 0.2251 | 0.3579 | 0.3579 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
278 | 160.1 | 120 | 68.6 | 51.9 | 2.3 | 355.9 | 2518.4 | 54.1 | 23 | 77.4 | 79.1 | 70 | 81.2 | 36.5 | 11.5 | 9852.8 | 9840.4 | 9869.2 | 19295.8 | 18787.2 | 18241.8 | 1.958 | 1.909 | 1.848 | 0.625 | 0.634 | 0.574 | -4.02 | 4.02 | -4.01 | 0.55 | 0.517 | 0.508 | -2.66 | 2.45 | 2.22 | 0.506 | 0.515 | 0.544 | 2.58 | 3.37 | 2 | 0.569 | 0.555 | 0.551 | 2 | -2.81 | 2.35 | Fair_Winding_TD_Cap | 9840.4 | 18241.8 | 1.848 | 0.634 | 4.02 | 0.569 | 3.37 | 0.9083 | 0.9067 | 0.9041 | 0.9764 | 1 | 0.6406 | 0.818 | 0.872 | 0.872 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
279 | 795.4 | 514.2 | 108.1 | 119.1 | 17.7 | 887.6 | 5972.7 | 45.6 | 33.2 | 89.8 | 87.6 | 84.8 | 98.1 | 38.4 | 25.2 | 6089.3 | 4557.4 | 6684.3 | 9770.8 | 6766.5 | 11010.5 | 1.605 | 1.485 | 1.647 | 0.716 | 0.68 | 0.721 | 5.9 | 4.75 | 6.01 | 0.693 | 0.7 | 0.652 | 3.39 | 4.72 | 5.22 | 0.677 | 0.598 | 0.634 | 4.15 | 5.34 | -3.12 | 0.572 | 0.654 | 0.72 | 3.94 | -4.58 | -3.68 | Poor_Mixed | 4557.4 | 6766.5 | 1.485 | 0.721 | 6.01 | 0.72 | 5.34 | 0.4283 | 0.7556 | 0.5317 | 0.5725 | 1 | 0.4534 | 0.5289 | 0.5982 | 0.5982 | Poor | 0 | 1 | DGA | 0 |  | C2H2
280 | 520.2 | 276 | 81.2 | 74.9 | 1 | 550.9 | 3872.6 | 35.3 | 47.8 | 77.9 | 77 | 73.3 | 84.4 | 35.4 | 13.3 | 5917.8 | 5152.7 | 5749 | 8927.4 | 7476 | 9384.8 | 1.509 | 1.451 | 1.632 | 0.633 | 0.686 | 0.705 | -4.11 | -4.53 | -5.57 | 0.551 | 0.563 | 0.549 | 2.61 | -3.51 | -15.19 | 0.626 | 0.564 | 0.5 | -3.05 | 3.15 | -2.26 | 0.54 | 0.517 | 0.53 | -3.24 | 2.98 | -3.73 | Critical_Oil | 5152.7 | 7476 | 1.451 | 0.705 | 5.57 | 0.626 | 15.19 | 0.8421 | 0.6035 | 0.8747 | 0.9367 | 1 | 0.5301 | 0.736 | 0.7839 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
281 | 1607.6 | 952.9 | 140.2 | 177 | 33.9 | 1193.5 | 7806.6 | 33.5 | 46.7 | 102.5 | 109.3 | 94.9 | 112.2 | 44.3 | 30.4 | 1386 | 1929.7 | 1847.9 | 1706 | 2214.4 | 2189.5 | 1.231 | 1.148 | 1.185 | 0.902 | 0.876 | 0.859 | 8.58 | 7.68 | 7.56 | 0.737 | 0.844 | 0.785 | 7.65 | 8.45 | -7.06 | 0.832 | 0.716 | 0.742 | -7.99 | 5.48 | 8.03 | 0.749 | 0.885 | 0.757 | 5.97 | 7 | 8.17 | Very Poor_Mixed | 1386 | 1706 | 1.148 | 0.902 | 8.58 | 0.885 | 8.45 | 0.1024 | 0.6137 | 0.1555 | 0.3825 | 1 | 0.1861 | 0.2748 | 0.3694 | 0.3694 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
282 | 100 | 153.1 | 70.7 | 68.6 | 1 | 384.4 | 2729.4 | 56.7 | 22.3 | 78.5 | 75 | 70 | 83.8 | 36.1 | 15 | 10000 | 9685.4 | 9977.6 | 20000 | 19299.8 | 18759.2 | 2 | 1.993 | 1.88 | 0.515 | 0.539 | 0.544 | 2.21 | -3.2 | 2.36 | 0.52 | 0.523 | 0.558 | 2.43 | 3.23 | 2.28 | 0.52 | 0.524 | 0.515 | 2.9 | 2.25 | 2.16 | 0.535 | 0.601 | 0.562 | 3.12 | -2.2 | 2.97 | Good_Mixed | 9685.4 | 18759.2 | 1.88 | 0.544 | 3.2 | 0.601 | 3.23 | 0.9496 | 0.9215 | 0.9322 | 0.8935 | 1 | 0.8491 | 0.7974 | 0.9083 | 0.9083 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
283 | 356.3 | 246.6 | 73.3 | 73.5 | 2 | 500.6 | 3763.7 | 54.1 | 25 | 78.2 | 78.1 | 73.1 | 81.5 | 35.6 | 13.4 | 8716.7 | 8563.9 | 10000 | 7132.5 | 16249.7 | 19866.6 | 0.818 | 1.897 | 1.987 | 0.965 | 0.966 | 0.971 | 9.49 | 9.13 | 9.84 | 0.518 | 0.569 | 0.532 | 2.99 | -2 | 2.78 | 0.517 | 0.58 | 0.531 | 2.9 | 2.61 | 3.21 | 0.52 | 0.55 | 0.558 | 3 | 2.54 | -2.47 | Critical_Winding_TD_Cap | 8563.9 | 7132.5 | 0.818 | 0.971 | 9.84 | 0.58 | 3.21 | 0.8098 | 0.87 | 0.8757 | 0.9342 | 0.8187 | 0.0468 | 0.7854 | 0.7201 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_HV
284 | 1614.8 | 923.1 | 138.5 | 180.4 | 29.7 | 1291.2 | 7869.4 | 32.5 | 47.5 | 107.2 | 109.3 | 94.8 | 119 | 45.4 | 31.9 | 711.1 | 690 | 1105.2 | 1200 | 1200 | 1200 | 1.688 | 1.739 | 1.086 | 0.974 | 0.939 | 0.962 | 9.46 | 9.36 | 9.54 | 0.753 | 0.907 | 0.934 | 7.77 | 6.98 | -8.66 | 0.965 | 0.984 | 0.708 | 7.68 | 7.56 | 5.24 | 0.745 | 0.864 | 0.796 | -8.85 | -7.36 | 7.29 | Very Poor_Mixed | 690 | 1200 | 1.086 | 0.974 | 9.54 | 0.984 | 8.85 | 0.1109 | 0.6062 | 0.0877 | 0.3252 | 1 | 0.0544 | 0.2085 | 0.3307 | 0.3307 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
285 | 1676.2 | 903.7 | 140.8 | 189.7 | 33.5 | 1241.8 | 8482.3 | 35.8 | 44 | 103.9 | 109.3 | 92.7 | 115.1 | 43.7 | 30.9 | 2123.8 | 1722.9 | 1876.2 | 2548.1 | 1989.7 | 2038.2 | 1.2 | 1.155 | 1.086 | 0.952 | 0.899 | 0.852 | 9.28 | 8.25 | 7.98 | 0.886 | 0.79 | 0.758 | -6.22 | -6.48 | 8.34 | 0.851 | 0.781 | 0.74 | 7.58 | 7.54 | 7.99 | 0.806 | 0.867 | 0.862 | -7.19 | 6.62 | 8.06 | Very Poor_Mixed | 1722.9 | 1989.7 | 1.086 | 0.952 | 9.28 | 0.886 | 8.34 | 0.0795 | 0.6396 | 0.1497 | 0.3635 | 1 | 0.1421 | 0.2415 | 0.3531 | 0.3531 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
286 | 890.6 | 531.1 | 99.4 | 126.6 | 18.4 | 859 | 5122.8 | 45.4 | 33.9 | 93.3 | 89.4 | 81.9 | 99.4 | 41.6 | 25.6 | 5352.4 | 4971.4 | 5738.9 | 8395.1 | 7659.1 | 9401 | 1.568 | 1.541 | 1.638 | 0.681 | 0.695 | 0.757 | 5.01 | -5.35 | 5.93 | 0.601 | 0.635 | 0.69 | 3.95 | 3.57 | 3.5 | 0.693 | 0.701 | 0.635 | 3.9 | 4.73 | 3.7 | 0.659 | 0.641 | 0.593 | -3.91 | -5.06 | -5.05 | Poor_Mixed | 4971.4 | 7659.1 | 1.541 | 0.757 | 5.93 | 0.701 | 5.06 | 0.4261 | 0.7473 | 0.4881 | 0.5584 | 1 | 0.4558 | 0.5378 | 0.5935 | 0.5935 | Poor | 0 | 1 | DGA | 0 |  | C2H2
287 | 409.3 | 308.8 | 70.6 | 71.7 | 1.7 | 434.2 | 3033.3 | 57.8 | 23.4 | 80.3 | 78.4 | 74 | 83.3 | 36.6 | 10 | 7361.7 | 7897.5 | 9043.6 | 12981.9 | 13361 | 17305.8 | 1.763 | 1.692 | 1.914 | 0.566 | 0.599 | 0.578 | 3.25 | -3.26 | 2.91 | 0.553 | 0.572 | 0.723 | 3.17 | 2.69 | -5.22 | 0.594 | 0.547 | 0.537 | 3.38 | 2.16 | 2 | 0.531 | 0.56 | 0.532 | 3.59 | 2.66 | 2.28 | Poor_Bushing_TD_Cap | 7361.7 | 12981.9 | 1.692 | 0.599 | 3.26 | 0.723 | 5.22 | 0.8272 | 0.8988 | 0.8326 | 1 | 1 | 0.7324 | 0.7181 | 0.8397 | 0.8397 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
288 | 984.1 | 570.2 | 104.4 | 127.1 | 20.2 | 914.4 | 5901.9 | 47.1 | 32.4 | 92 | 96.5 | 83.9 | 100.4 | 39 | 26.6 | 5449.5 | 5828 | 5154.8 | 8007.6 | 9222.3 | 7912.5 | 1.469 | 1.582 | 1.535 | 0.791 | 0.737 | 0.738 | 5.93 | 5.4 | 5.89 | 0.696 | 0.691 | 0.617 | 3.57 | 4.24 | 5.17 | 0.725 | 0.746 | 0.675 | -4.54 | 5.83 | 3.88 | 0.599 | 0.68 | 0.669 | 4.79 | -4.44 | 5.15 | Poor_Mixed | 5154.8 | 7912.5 | 1.469 | 0.791 | 5.93 | 0.746 | 5.83 | 0.3847 | 0.7654 | 0.4505 | 0.5228 | 1 | 0.3993 | 0.4849 | 0.5624 | 0.5624 | Poor | 0 | 1 | DGA | 0 |  | C2H2
289 | 100 | 120 | 65 | 50 | 1 | 406.3 | 2646.7 | 57.8 | 23.4 | 80 | 75 | 73.9 | 83.9 | 36.8 | 14 | 6177.1 | 5921.1 | 5795.1 | 9601 | 9622.8 | 9495.3 | 1.554 | 1.625 | 1.639 | 0.596 | 0.554 | 0.599 | 3.87 | 3.94 | -4.05 | 0.504 | 0.53 | 0.55 | -3.34 | 2.09 | 2 | 0.553 | 0.53 | 0.578 | -2.81 | 2.55 | -2.19 | 0.61 | 0.505 | 0.564 | 2.85 | 2.22 | -2 | Fair_IR_PI | 5795.1 | 9495.3 | 1.554 | 0.599 | 4.05 | 0.61 | 3.34 | 0.9861 | 0.8988 | 0.8755 | 0.9194 | 1 | 0.6791 | 0.7965 | 0.8863 | 0.8863 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
290 | 847.2 | 554.5 | 104.6 | 124.9 | 23.3 | 905.6 | 5743.1 | 45.1 | 33.2 | 90 | 88.9 | 79.6 | 97.8 | 40.4 | 25.2 | 6289.2 | 5498.5 | 6584.4 | 10523.6 | 8721.8 | 10837.3 | 1.673 | 1.586 | 1.646 | 0.756 | 0.707 | 0.753 | 5.66 | 5.62 | 5.51 | 0.702 | 0.641 | 0.661 | 4.54 | 5.23 | -4.28 | 0.733 | 0.668 | 0.63 | 3.48 | -5.03 | 4.98 | 0.666 | 0.68 | 0.68 | -4.26 | -4.47 | 3.95 | Poor_Mixed | 5498.5 | 8721.8 | 1.586 | 0.756 | 5.66 | 0.733 | 5.23 | 0.3847 | 0.7556 | 0.5438 | 0.5725 | 1 | 0.4213 | 0.4936 | 0.5777 | 0.5777 | Poor | 0 | 1 | DGA | 0 |  | C2H2
291 | 382.9 | 203.1 | 78.6 | 71 | 2.5 | 493.1 | 3367.1 | 53.7 | 27.4 | 77.4 | 80.2 | 73.4 | 84.1 | 36.4 | 16.7 | 2724.4 | 1412.8 | 2555.1 | 3231.7 | 1577.5 | 3002.6 | 1.186 | 1.117 | 1.175 | 0.65 | 0.666 | 0.723 | 5.04 | 4.31 | 5.73 | 0.546 | 0.524 | 0.629 | 2.64 | 2.58 | 2.79 | 0.543 | 0.582 | 0.523 | 2.44 | 2.59 | 2 | 0.526 | 0.551 | 0.541 | 11.71 | 2.01 | 2.5 | Critical_IR_PI | 1412.8 | 1577.5 | 1.117 | 0.723 | 5.73 | 0.629 | 11.71 | 0.8036 | 0.8323 | 0.8453 | 0.8465 | 1 | 0.5084 | 0.7489 | 0.7936 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_R_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
292 | 495.4 | 298.9 | 84 | 142.2 | 1.8 | 557.8 | 3562.4 | 55.9 | 26.6 | 109.3 | 108.7 | 106.5 | 119.2 | 44.8 | 13.8 | 9019.8 | 8227.2 | 8631.5 | 17084.1 | 14615.4 | 15878.9 | 1.894 | 1.776 | 1.84 | 0.615 | 0.561 | 0.593 | 4.29 | 3.35 | -3.59 | 0.549 | 0.546 | 0.519 | 3.85 | 2.59 | -2.93 | 0.57 | 0.57 | 0.573 | 3.59 | 3.21 | 2 | 0.543 | 0.525 | 0.501 | 2.7 | 3.15 | 2.93 | Critical_Thermal | 8227.2 | 14615.4 | 1.776 | 0.615 | 4.29 | 0.573 | 3.85 | 0.7124 | 0.8443 | 0.0548 | 0.9244 | 1 | 0.6837 | 0.7724 | 0.7259 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | C2H4
293 | 1499.7 | 837.7 | 138.4 | 182 | 32.8 | 1282.1 | 7862.2 | 34.6 | 44.4 | 106.8 | 108.1 | 93.1 | 114 | 44.5 | 30.8 | 1863.2 | 1892.8 | 3579.7 | 2313.7 | 2132.5 | 4578.4 | 1.242 | 1.127 | 1.279 | 0.901 | 0.92 | 0.909 | 8.29 | -9.29 | -7.9 | 0.858 | 0.726 | 0.85 | 6.05 | 5.99 | 8.39 | 0.832 | 0.927 | 0.759 | 6.44 | 6.8 | -5.31 | 0.747 | 0.838 | 0.748 | -5.9 | 6.15 | -7.82 | Very Poor_Mixed | 1863.2 | 2132.5 | 1.127 | 0.92 | 9.29 | 0.927 | 8.39 | 0.1142 | 0.6357 | 0.1375 | 0.3673 | 1 | 0.1358 | 0.2751 | 0.3655 | 0.3655 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
294 | 166 | 148.7 | 69.4 | 59.1 | 1 | 384.2 | 2799.6 | 50.8 | 29.2 | 76.5 | 75.7 | 71.1 | 80.9 | 35 | 11.9 | 7980.6 | 9508.6 | 8775.1 | 14050.2 | 18025 | 16265.8 | 1.761 | 1.896 | 1.854 | 0.557 | 0.553 | 0.5 | 2.89 | 2.71 | 2.44 | 0.5 | 0.53 | 0.5 | 2 | -2.24 | 2 | 0.525 | 0.5 | 0.503 | 2.79 | -2 | 2.51 | 0.502 | 0.512 | 0.5 | 2.09 | 2.05 | -2.41 | Fair_Oil | 7980.6 | 14050.2 | 1.761 | 0.557 | 2.89 | 0.53 | 2.79 | 0.9557 | 0.8067 | 0.9445 | 0.9682 | 1 | 0.8482 | 0.9346 | 0.9255 | 0.9255 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
295 | 810.4 | 587.7 | 100.9 | 117.1 | 13 | 811.2 | 5866.2 | 47.2 | 32.2 | 91 | 94.9 | 83.3 | 100.6 | 39.5 | 23.6 | 5323.4 | 6815.5 | 5957.2 | 7891.8 | 11000.6 | 9213.4 | 1.482 | 1.614 | 1.547 | 0.719 | 0.756 | 0.704 | 5.39 | 5.83 | 5.94 | 0.619 | 0.67 | 0.693 | 4.44 | 4.95 | -4.83 | 0.679 | 0.763 | 0.721 | 4.79 | 4.17 | -3.82 | 0.666 | 0.615 | 0.694 | 4.54 | 4.79 | -4.2 | Poor_Mixed | 5323.4 | 7891.8 | 1.482 | 0.756 | 5.94 | 0.763 | 4.95 | 0.4688 | 0.7678 | 0.4664 | 0.628 | 1 | 0.4253 | 0.4857 | 0.5943 | 0.5943 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
296 | 1329.5 | 773.3 | 131.1 | 170.3 | 29.4 | 1121.2 | 7545.4 | 33 | 47.2 | 99.8 | 97.8 | 90 | 106.5 | 42.2 | 29.3 | 985.1 | 2844.1 | 3285.1 | 1200 | 3539.8 | 3979.6 | 1.218 | 1.245 | 1.211 | 0.897 | 0.919 | 0.918 | 8.01 | 8.88 | 9.2 | 0.865 | 0.868 | 0.779 | 7.12 | 5.8 | 6.89 | 0.762 | 0.945 | 0.83 | 7.02 | -7.78 | 6.13 | 0.9 | 0.784 | 0.798 | 5.25 | 7.48 | 5.33 | Very Poor_Mixed | 985.1 | 1200 | 1.211 | 0.919 | 9.2 | 0.945 | 7.78 | 0.1865 | 0.609 | 0.3071 | 0.4238 | 1 | 0.1245 | 0.2489 | 0.3939 | 0.3939 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
297 | 630.6 | 424 | 89.8 | 88.8 | 3.5 | 694.9 | 4848.4 | 53.5 | 27.6 | 77.4 | 115.3 | 73.3 | 84.3 | 36.1 | 19.5 | 7344.9 | 7608.1 | 7398.6 | 12859.4 | 13297.4 | 12699.9 | 1.751 | 1.748 | 1.717 | 0.982 | 0.963 | 0.985 | 9.6 | 9.69 | 9.84 | 0.629 | 0.615 | 0.645 | 3.43 | 3.77 | 3.7 | 0.504 | 0.58 | 0.646 | 4.32 | 3.75 | 4.73 | 0.578 | 0.595 | 0.555 | 4.65 | 3.83 | 4.36 | Critical_Winding_TD_Cap | 7344.9 | 12699.9 | 1.717 | 0.985 | 9.84 | 0.646 | 4.73 | 0.6659 | 0.8293 | 0.6564 | 0.7625 | 1 | 0.0295 | 0.6324 | 0.6477 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | WTI_LV
298 | 240.1 | 120 | 70.7 | 50.1 | 1 | 384.1 | 2521.5 | 59.3 | 20 | 76.2 | 77.7 | 72.7 | 84.3 | 35.5 | 12 | 10000 | 9739.3 | 10000 | 19090.4 | 18794.3 | 20000 | 1.909 | 1.93 | 2 | 0.5 | 0.555 | 0.5 | 2 | -2.62 | 2.06 | 0.5 | 0.518 | 0.519 | -2.62 | -2 | -2.6 | 0.529 | 0.547 | 0.559 | 2.61 | 2 | 2.09 | 0.523 | 0.523 | 0.551 | 2 | -2.11 | 2.2 | Good_Mixed | 9739.3 | 18794.3 | 1.909 | 0.555 | 2.62 | 0.559 | 2.62 | 0.9708 | 1 | 0.8912 | 0.9661 | 1 | 0.9325 | 0.8459 | 0.9429 | 0.9429 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
299 | 100 | 120 | 65 | 58.6 | 3.4 | 350 | 2865.7 | 60 | 20 | 77.3 | 75.4 | 70 | 82.3 | 35.5 | 11.3 | 10000 | 9206.4 | 9103.1 | 20000 | 17058.6 | 17323.7 | 2 | 1.853 | 1.903 | 0.526 | 0.5 | 0.608 | 2.5 | 2 | 2.9 | 0.545 | 0.5 | 0.5 | 2.34 | 2 | 2.7 | 0.5 | 0.5 | 0.5 | 2 | -2.36 | 2 | 0.569 | 0.505 | 0.5 | 2 | 2 | 2.05 | Good_Mixed | 9103.1 | 17058.6 | 1.853 | 0.608 | 2.9 | 0.569 | 2.7 | 0.8828 | 1 | 0.9456 | 0.9802 | 1 | 0.8597 | 0.9362 | 0.9332 | 0.9332 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
300 | 190.7 | 151.8 | 71 | 55.3 | 1.4 | 427.2 | 2871.1 | 56.1 | 23.1 | 81.4 | 77.1 | 73.7 | 86.8 | 37.3 | 10.6 | 6184.5 | 5772.9 | 5161.5 | 9140.9 | 8956.3 | 8035.7 | 1.478 | 1.551 | 1.557 | 0.593 | 0.594 | 0.587 | -4.28 | 3.26 | 3.08 | 0.56 | 0.544 | 0.528 | 2.39 | 2 | 2.78 | 0.5 | 0.553 | 0.526 | 2.63 | 2.35 | -2.51 | 0.571 | 0.554 | 0.537 | -2.34 | -2.55 | 2.58 | Fair_IR_PI | 5161.5 | 8035.7 | 1.478 | 0.594 | 4.28 | 0.571 | 2.78 | 0.9062 | 0.9047 | 0.8178 | 0.9925 | 1 | 0.6932 | 0.8038 | 0.8683 | 0.8683 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
301 | 372.5 | 314 | 78.9 | 76.7 | 1.6 | 546.2 | 3219.4 | 56.5 | 22.9 | 78.1 | 78.7 | 73.8 | 85.8 | 36.2 | 12.4 | 9230.8 | 9311.1 | 7961.4 | 17475.1 | 17999.8 | 14791.9 | 1.893 | 1.933 | 1.858 | 0.763 | 0.779 | 0.749 | 5.95 | 6.99 | -6.81 | 0.537 | 0.595 | 0.55 | 3.22 | 2.76 | 2.15 | 0.554 | 0.565 | 0.511 | -2.15 | 2.07 | -2.64 | 0.516 | 0.519 | 0.507 | 2.43 | -3.07 | 2.57 | Poor_Winding_TD_Cap | 7961.4 | 14791.9 | 1.858 | 0.779 | 6.99 | 0.595 | 3.22 | 0.8034 | 0.9088 | 0.8409 | 0.9575 | 1 | 0.3462 | 0.8042 | 0.7951 | 0.7951 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
302 | 868.2 | 613.1 | 107 | 116.3 | 17.2 | 953 | 5604.8 | 49.2 | 31 | 92.7 | 92.2 | 82.4 | 99.3 | 40.4 | 24.9 | 5124.6 | 5502.2 | 5507.5 | 7544.9 | 8204.8 | 8811 | 1.472 | 1.491 | 1.6 | 0.72 | 0.79 | 0.82 | 6.01 | 6.41 | -7.57 | 0.676 | 0.674 | 0.661 | 3.5 | 5.57 | 5.59 | 0.687 | 0.687 | 0.669 | -5.53 | 4.86 | 4.2 | 0.681 | 0.647 | 0.678 | 5.05 | 5.55 | 4.72 | Poor_Mixed | 5124.6 | 7544.9 | 1.472 | 0.82 | 7.57 | 0.687 | 5.59 | 0.4143 | 0.7829 | 0.4789 | 0.5831 | 1 | 0.3324 | 0.4749 | 0.5666 | 0.5666 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
303 | 1474.3 | 838 | 132.9 | 168.9 | 28.5 | 1244.1 | 7354.6 | 33.5 | 46.2 | 99.8 | 101.5 | 91.4 | 109.6 | 43.2 | 31.1 | 3629.8 | 2187.5 | 2436.7 | 4862.2 | 2657.1 | 2694.7 | 1.34 | 1.215 | 1.106 | 0.922 | 0.948 | 0.944 | -8.78 | 8.89 | 8.22 | 0.838 | 0.903 | 0.838 | -7.81 | -7.6 | 7.94 | 0.903 | 0.895 | 0.726 | -6.66 | 6.13 | 5.64 | 0.878 | 0.718 | 0.888 | 8.41 | -7.23 | 8.13 | Very Poor_Mixed | 2187.5 | 2657.1 | 1.106 | 0.948 | 8.89 | 0.903 | 8.41 | 0.1615 | 0.6184 | 0.2549 | 0.3559 | 1 | 0.1095 | 0.2195 | 0.3727 | 0.3727 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
304 | 749.4 | 411.7 | 86.2 | 99.8 | 12.7 | 718.6 | 4872.5 | 50.2 | 31.8 | 87.4 | 87 | 76.7 | 90.2 | 38 | 20.1 | 7293.6 | 7591.4 | 7155.8 | 12928.2 | 13463.1 | 12887.6 | 1.773 | 1.773 | 1.801 | 0.698 | 0.689 | 0.676 | -5.44 | 5.01 | 4.83 | 0.603 | 0.566 | 0.599 | -4.05 | 4.35 | -3.11 | 0.63 | 0.631 | 0.622 | -3.4 | 3.91 | 4.04 | 0.661 | 0.635 | 0.528 | 4.37 | 3.03 | 3.57 | Fair_Mixed | 7155.8 | 12887.6 | 1.773 | 0.698 | 5.44 | 0.661 | 4.37 | 0.5455 | 0.7728 | 0.6474 | 0.7436 | 1 | 0.4956 | 0.6156 | 0.6712 | 0.6712 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
305 | 145.5 | 162.6 | 69.5 | 63.4 | 1 | 353.9 | 3004.4 | 60 | 21.3 | 80.6 | 76 | 70 | 82.8 | 35.2 | 13 | 9941.6 | 9775.1 | 9782 | 19883.2 | 18978.6 | 19384.2 | 2 | 1.942 | 1.982 | 0.514 | 0.5 | 0.521 | 2 | 2 | -2.06 | 0.521 | 0.515 | 0.5 | -2.26 | 2.37 | 2.09 | 0.5 | 0.556 | 0.505 | 2.02 | 2.05 | 2.2 | 0.511 | 0.501 | 0.531 | -2.71 | 2.77 | 2.06 | Good_Mixed | 9775.1 | 18978.6 | 1.942 | 0.521 | 2.06 | 0.556 | 2.77 | 0.956 | 0.9458 | 0.9048 | 0.9438 | 1 | 0.95 | 0.8975 | 0.9447 | 0.9447 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
306 | 838.4 | 492 | 104.1 | 128 | 17.1 | 794.4 | 5444.6 | 47.2 | 32.6 | 93 | 89.2 | 83.7 | 98.7 | 39.2 | 23.5 | 5896.6 | 6388.1 | 5558.9 | 9373.9 | 10157 | 8241.7 | 1.59 | 1.59 | 1.483 | 0.69 | 0.697 | 0.675 | 5.09 | 4.99 | 4.4 | 0.696 | 0.692 | 0.726 | 4.8 | 6.84 | 6.16 | 0.63 | 0.688 | 0.728 | 4.78 | 4.17 | 4.65 | 0.655 | 0.798 | 0.722 | 4.62 | 5.21 | -4.46 | Poor_Mixed | 5558.9 | 8241.7 | 1.483 | 0.697 | 5.09 | 0.798 | 6.84 | 0.4428 | 0.7629 | 0.499 | 0.6314 | 1 | 0.5112 | 0.4363 | 0.5938 | 0.5938 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
307 | 113.2 | 186.7 | 70.5 | 57.8 | 2.1 | 474.5 | 3072.3 | 58 | 20.6 | 76.5 | 75.7 | 70.9 | 84.2 | 36.1 | 13.9 | 9732.6 | 10000 | 8274.3 | 18961 | 19718.3 | 14529 | 1.948 | 1.972 | 1.756 | 0.778 | 0.762 | 0.843 | -6.75 | 5.86 | -7.38 | 0.541 | 0.543 | 0.525 | 2.32 | 2.51 | 2.09 | 0.555 | 0.509 | 0.611 | -2.72 | 2.65 | -2.62 | 0.554 | 0.569 | 0.612 | -2.01 | 2 | 3.57 | Poor_Winding_TD_Cap | 8274.3 | 14529 | 1.756 | 0.843 | 7.38 | 0.612 | 3.57 | 0.8729 | 0.9672 | 0.9257 | 0.9219 | 1 | 0.3177 | 0.7664 | 0.8154 | 0.8154 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
308 | 1631.5 | 982.4 | 148.3 | 185.4 | 29.2 | 1345.6 | 8697.7 | 34.3 | 48.2 | 106.3 | 107.7 | 94.9 | 117.4 | 44.5 | 34.7 | 1637.3 | 909.1 | 908.3 | 1895.2 | 1200 | 1200 | 1.158 | 1.32 | 1.321 | 0.914 | 0.956 | 0.885 | -9.05 | 8.61 | 8.85 | 0.986 | 0.883 | 0.99 | 6.32 | 9.61 | 9.14 | 0.885 | 0.893 | 0.868 | -8.88 | -4.79 | 7.6 | 0.935 | 0.898 | 0.876 | 9.2 | -6.03 | 9.49 | Very Poor_Mixed | 908.3 | 1200 | 1.158 | 0.956 | 9.05 | 0.99 | 9.61 | 0.0768 | 0.5998 | 0.1154 | 0.2157 | 1 | 0.1127 | 0.1377 | 0.3141 | 0.3141 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
309 | 561.6 | 330.7 | 86.5 | 82.2 | 4.2 | 648.8 | 3546.7 | 19.8 | 20.8 | 79.2 | 80.2 | 70 | 83.7 | 36.2 | 16.7 | 8499.7 | 9224.8 | 7282.7 | 14937.4 | 16643.5 | 11927 | 1.757 | 1.804 | 1.638 | 0.99 | 0.965 | 0.99 | -9.65 | 9.84 | 9.32 | 0.5 | 0.591 | 0.554 | 2.88 | -2.77 | -3.36 | 0.512 | 0.527 | 0.518 | 2.26 | 2.89 | 2.07 | 0.594 | 0.534 | 0.515 | 3.94 | 2.45 | -2.61 | Critical_Winding_TD_Cap | 7282.7 | 11927 | 1.638 | 0.99 | 9.84 | 0.594 | 3.94 | 0.6979 | 0.3772 | 0.8659 | 0.8465 | 1 | 0.0316 | 0.8026 | 0.6575 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
310 | 158.3 | 156.2 | 69.5 | 63.8 | 1 | 352.7 | 2990 | 53.6 | 27.9 | 78.4 | 80.5 | 74.2 | 83.8 | 35.8 | 13.2 | 7270.7 | 7069.2 | 7932.8 | 12107.7 | 12754.1 | 14506.1 | 1.665 | 1.804 | 1.829 | 0.587 | 0.554 | 0.585 | 3.6 | 3.74 | -3.82 | 0.559 | 0.641 | 0.538 | 2.63 | 3.93 | -3.17 | 1.658 | 0.59 | 0.561 | 3.81 | 2.82 | 2.94 | 0.99 | 0.582 | 0.633 | 9.39 | 2.14 | 4.02 | Critical_Bushing_TD_Cap | 7069.2 | 12107.7 | 1.665 | 0.587 | 3.82 | 1.658 | 9.39 | 0.9552 | 0.825 | 0.8306 | 0.939 | 1 | 0.7031 | 0.5552 | 0.8262 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
311 | 899.1 | 520.6 | 100.2 | 114.2 | 15.2 | 831.5 | 5706.8 | 48.4 | 31.6 | 88.5 | 94 | 81.6 | 97.3 | 39.1 | 25.3 | 6433.3 | 5486.6 | 6091.5 | 10602.8 | 8600.9 | 9776.5 | 1.648 | 1.568 | 1.605 | 0.701 | 0.753 | 0.7 | 4.4 | 6.19 | 6.08 | 0.66 | 0.693 | 0.72 | -5.05 | -4.72 | 4.71 | 0.656 | 0.713 | 0.641 | 4.48 | -4.32 | 4.67 | 0.682 | 0.648 | 0.725 | 5.08 | 5.09 | 3.34 | Poor_Mixed | 5486.6 | 8600.9 | 1.568 | 0.753 | 6.19 | 0.725 | 5.09 | 0.456 | 0.7753 | 0.5184 | 0.569 | 1 | 0.4427 | 0.478 | 0.5954 | 0.5954 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
312 | 180.1 | 176.8 | 73 | 59.2 | 1.5 | 398.4 | 3121 | 59.2 | 22.7 | 81 | 78.4 | 74.1 | 85.1 | 36.8 | 13.2 | 8992.8 | 10000 | 8356.6 | 17607.7 | 19736.6 | 15622.9 | 1.958 | 1.974 | 1.87 | 0.526 | 0.549 | 0.509 | 2.1 | 2.04 | 2 | 0.544 | 0.514 | 0.557 | 3.42 | 2.34 | -3.08 | 0.556 | 0.513 | 0.605 | 2.22 | 3.32 | -2.31 | 0.83 | 0.522 | 0.543 | -5.97 | 3.32 | 2.84 | Poor_Bushing_TD_Cap | 8356.6 | 15622.9 | 1.87 | 0.549 | 2.1 | 0.83 | 5.97 | 0.8959 | 0.9129 | 0.8158 | 0.939 | 1 | 0.9039 | 0.72 | 0.8782 | 0.8782 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
313 | 483.7 | 299.2 | 82.3 | 74.1 | 7.4 | 514.1 | 3582.7 | 56.8 | 24.3 | 75 | 76.7 | 71 | 80.3 | 35.1 | 10 | 9277.1 | 9138.8 | 8220.1 | 17138.9 | 18089.1 | 14950.4 | 1.847 | 1.979 | 1.819 | 0.538 | 0.546 | 0.554 | 2.11 | 2.82 | 3.22 | 0.5 | 0.5 | 0.549 | 2.59 | -2.36 | -2 | 0.522 | 0.509 | 0.5 | 2 | 2.12 | 2 | 0.516 | 0.5 | 0.519 | 2.79 | 2 | 2.15 | Fair_DGA | 8220.1 | 14950.4 | 1.819 | 0.554 | 3.22 | 0.549 | 2.79 | 0.6997 | 0.8821 | 0.9592 | 1 | 1 | 0.8146 | 0.9165 | 0.8657 | 0.8657 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
314 | 950.4 | 547.3 | 105.3 | 126 | 20.7 | 877 | 4803.1 | 43.8 | 33.8 | 88 | 88.8 | 80.4 | 97.3 | 39.6 | 22.8 | 5676.3 | 6486.1 | 5395.9 | 8855.2 | 10152.1 | 8932.8 | 1.56 | 1.565 | 1.655 | 0.739 | 0.74 | 0.705 | 5.56 | 5.31 | 4.96 | 0.708 | 0.714 | 0.654 | 4.28 | -4.48 | 4.34 | 0.633 | 0.664 | 0.643 | -5.32 | 5 | -3.61 | 0.645 | 0.597 | 0.645 | 4.6 | 4.54 | 3.72 | Poor_Mixed | 5395.9 | 8855.2 | 1.56 | 0.74 | 5.56 | 0.714 | 5.32 | 0.4032 | 0.7485 | 0.5603 | 0.6552 | 1 | 0.4484 | 0.5182 | 0.5955 | 0.5955 | Poor | 0 | 1 | DGA | 0 |  | C2H2
315 | 724.4 | 406.7 | 98.9 | 110 | 12.6 | 704.7 | 4807.3 | 55.6 | 24.8 | 76 | 76.8 | 71.7 | 80 | 35.5 | 16.1 | 9157.5 | 9661.1 | 8481.3 | 17138.7 | 18483.8 | 15607.6 | 1.872 | 1.913 | 1.84 | 0.502 | 0.512 | 0.566 | 2.58 | 2.91 | 2.68 | 0.5 | 0.5 | 0.56 | 2.43 | 2.28 | 2.36 | 0.5 | 0.507 | 0.513 | 2.31 | 2.18 | 2.32 | 0.5 | 0.524 | 0.505 | -2.12 | 2.15 | 2 | Fair_DGA | 8481.3 | 15607.6 | 1.84 | 0.566 | 2.91 | 0.56 | 2.43 | 0.5322 | 0.8734 | 0.9338 | 0.8635 | 1 | 0.8614 | 0.9196 | 0.8205 | 0.8205 | Good | 1 | 1 | DGA | 0 |  | C2H2
316 | 330.4 | 146.1 | 70.4 | 57.7 | 3.3 | 556.6 | 3792.9 | 60 | 21.3 | 78.6 | 75.5 | 71.6 | 82 | 36.6 | 15.4 | 4917.2 | 2742.1 | 3717.9 | 7254.9 | 3539.7 | 4763.9 | 1.475 | 1.291 | 1.281 | 0.684 | 0.625 | 0.667 | 4.97 | 4.36 | -4.89 | 0.562 | 0.525 | 0.571 | 3.35 | 2.64 | 2.2 | 0.518 | 0.605 | 0.545 | 2 | 2.31 | 2.74 | 0.553 | 0.522 | 0.565 | 2 | 2.97 | -2.64 | Poor_IR_PI | 2742.1 | 3539.7 | 1.281 | 0.684 | 4.97 | 0.605 | 3.35 | 0.8103 | 0.9458 | 0.9083 | 0.8828 | 1 | 0.5451 | 0.7735 | 0.8266 | 0.8266 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
317 | 338.7 | 280.6 | 73.2 | 70.3 | 4.5 | 430.6 | 3347.4 | 58.8 | 21.2 | 79.1 | 77.4 | 73.7 | 86.2 | 36.9 | 13.2 | 10000 | 9539 | 9574.9 | 20000 | 18997 | 18621.6 | 2 | 1.992 | 1.945 | 0.539 | 0.604 | 0.513 | 2.41 | -2.6 | 2.54 | 0.5 | 0.593 | 0.501 | 2.29 | 2.35 | 2.69 | 0.579 | 0.6 | 0.512 | -2.04 | 2.99 | 2.5 | 0.746 | 0.5 | 0.579 | 5.49 | -2.76 | 2.96 | Poor_Bushing_TD_Cap | 9539 | 18621.6 | 1.945 | 0.604 | 2.6 | 0.746 | 5.49 | 0.7768 | 0.9486 | 0.8396 | 0.939 | 1 | 0.8266 | 0.767 | 0.8527 | 0.8527 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
318 | 798 | 472.4 | 103.9 | 118 | 21.2 | 798.6 | 5179.5 | 48.8 | 32.3 | 89.3 | 92.5 | 79.7 | 96.9 | 39.1 | 23.7 | 6557.5 | 6463.7 | 7310.9 | 10468.9 | 11008.8 | 12133.1 | 1.596 | 1.703 | 1.66 | 0.691 | 0.685 | 0.662 | 5.55 | 4.87 | 5.33 | 0.759 | 0.767 | 0.661 | -4.58 | 4.37 | 5.54 | 0.688 | 0.697 | 0.66 | 3.98 | 4.51 | -4.06 | 0.682 | 0.655 | 0.696 | -5.42 | 4.15 | -3.85 | Poor_Mixed | 6463.7 | 10468.9 | 1.596 | 0.691 | 5.55 | 0.767 | 5.54 | 0.4356 | 0.7666 | 0.537 | 0.6246 | 1 | 0.4948 | 0.4659 | 0.5989 | 0.5989 | Poor | 0 | 1 | DGA | 0 |  | C2H2
319 | 1621.8 | 943.7 | 140.7 | 175.6 | 29.9 | 1327.5 | 8274 | 33.2 | 44.7 | 101.5 | 105.2 | 92.1 | 110.6 | 43.7 | 33 | 2349.7 | 1288.6 | 1836.7 | 2861 | 1448.6 | 2173.1 | 1.218 | 1.124 | 1.183 | 0.912 | 0.905 | 0.98 | 8.45 | -8.73 | 9.54 | 0.801 | 0.674 | 0.836 | 6.88 | 5.11 | 6.91 | 0.815 | 0.911 | 0.756 | 6.44 | 5.01 | 8.76 | 0.952 | 0.867 | 0.902 | -5.28 | -7.43 | 6.93 | Very Poor_Mixed | 1288.6 | 1448.6 | 1.124 | 0.98 | 9.54 | 0.952 | 8.76 | 0.1002 | 0.6328 | 0.2116 | 0.2826 | 1 | 0.0997 | 0.2537 | 0.3559 | 0.3559 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
320 | 356.6 | 260.8 | 83.2 | 94.8 | 7.5 | 510.5 | 4469.5 | 52.6 | 28.9 | 83.6 | 87.4 | 77.2 | 91.9 | 37.5 | 16.5 | 7876.9 | 7659.3 | 8044.3 | 14166.2 | 13190 | 14467.1 | 1.798 | 1.722 | 1.798 | 0.597 | 0.643 | 0.577 | 4.06 | 3.25 | -3.68 | 0.569 | 0.601 | 0.618 | 3.65 | 3.07 | 4.24 | 0.588 | 0.604 | 0.567 | 3.83 | -2.52 | -3.72 | 0.586 | 0.564 | 0.571 | 2.6 | -2 | 2.92 | Fair_Mixed | 7659.3 | 13190 | 1.722 | 0.643 | 4.06 | 0.618 | 4.24 | 0.6833 | 0.8109 | 0.6629 | 0.8522 | 1 | 0.669 | 0.6748 | 0.7521 | 0.7521 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
321 | 354.2 | 261.4 | 75.7 | 74.7 | 6.6 | 540.9 | 3666.5 | 52.8 | 27.6 | 81.2 | 80.4 | 74.4 | 88.1 | 37 | 14.2 | 6504.1 | 7581.5 | 8164.9 | 11072.8 | 13594.2 | 14664.5 | 1.702 | 1.793 | 1.796 | 0.642 | 0.595 | 0.61 | 3.25 | 3.81 | 4.12 | 0.568 | 0.542 | 0.576 | -2.9 | 3.84 | -2.87 | 0.582 | 0.506 | 0.584 | 3.22 | -2.02 | -2.58 | 0.501 | 0.576 | 0.575 | 2.92 | 2.94 | 2.32 | Fair_Mixed | 6504.1 | 11072.8 | 1.702 | 0.642 | 4.12 | 0.584 | 3.84 | 0.7233 | 0.8293 | 0.7777 | 0.9144 | 1 | 0.6524 | 0.7563 | 0.7913 | 0.7913 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
322 | 1554.5 | 888.7 | 136.5 | 164.8 | 32.1 | 1184 | 7379.9 | 32.7 | 46.6 | 102.4 | 104 | 93.7 | 112.3 | 44.4 | 30.3 | 3089.7 | 1250.3 | 2141.9 | 3728 | 1394.5 | 2510 | 1.207 | 1.115 | 1.172 | 0.851 | 0.94 | 0.988 | 8.34 | 9.25 | 9.33 | 0.907 | 0.843 | 0.772 | 6.36 | 9.07 | 6.77 | 0.861 | 0.677 | 0.828 | 8.9 | 6 | 7.33 | 0.887 | 0.865 | 0.867 | 6.84 | 5.76 | 8.59 | Very Poor_Mixed | 1250.3 | 1394.5 | 1.115 | 0.988 | 9.33 | 0.907 | 9.07 | 0.1407 | 0.6147 | 0.1906 | 0.3863 | 1 | 0.1012 | 0.2278 | 0.3625 | 0.3625 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
323 | 100 | 120 | 65 | 50 | 1 | 352.2 | 2721.5 | 56.7 | 21.9 | 75 | 76.7 | 71.6 | 80.4 | 36.2 | 10 | 9739.1 | 9914.8 | 9905 | 18032.8 | 19829.6 | 19370.2 | 1.852 | 2 | 1.956 | 0.546 | 0.591 | 0.538 | -3.05 | 3.93 | 2.53 | 0.515 | 0.624 | 0.5 | 3.18 | 5.34 | -2.53 | 0.5 | 0.504 | 0.5 | 2.31 | 2.71 | -2.08 | 0.5 | 0.55 | 0.524 | 2.9 | -3.35 | 2 | Fair_Bushing_TD_Cap | 9739.1 | 18032.8 | 1.852 | 0.591 | 3.93 | 0.624 | 5.34 | 0.9983 | 0.9307 | 0.9481 | 1 | 1 | 0.7659 | 0.861 | 0.9283 | 0.9283 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
324 | 1188.5 | 686.6 | 119.5 | 143.7 | 30.2 | 1026.6 | 6306 | 55.6 | 22.8 | 81.6 | 82.6 | 75.6 | 88.5 | 37.1 | 14.7 | 8396.7 | 9076.1 | 8238.5 | 15607.9 | 17447.8 | 15489.7 | 1.859 | 1.922 | 1.88 | 0.623 | 0.618 | 0.584 | 3.85 | 3.41 | 2.62 | 0.533 | 0.514 | 0.518 | 2.37 | 2.19 | -3.28 | 0.556 | 0.524 | 0.527 | 2.31 | 2.9 | 2.22 | 0.514 | 0.505 | 0.521 | 2.65 | -3.13 | 3.42 | Poor_DGA | 8238.5 | 15489.7 | 1.859 | 0.623 | 3.85 | 0.556 | 3.42 | 0.2606 | 0.9108 | 0.7448 | 0.9014 | 1 | 0.6891 | 0.8327 | 0.7004 | 0.7004 | Fair | 1 | 1 | DGA | 0 |  | C2H2
325 | 670.5 | 341.1 | 82.8 | 97.3 | 10.7 | 675.3 | 4765.5 | 50.3 | 28.1 | 86.9 | 86.5 | 79 | 93 | 38.6 | 19.5 | 7450.6 | 7550 | 6913.2 | 12841.5 | 12784.3 | 11699.5 | 1.724 | 1.693 | 1.692 | 0.639 | 0.681 | 0.637 | -3.98 | 4.72 | 4.06 | 0.673 | 0.6 | 0.612 | 3.83 | 3.99 | 3.39 | 0.652 | 0.614 | 0.582 | 4.65 | 3.38 | 3.4 | 0.637 | 0.587 | 0.593 | 3.81 | 3.29 | -4.11 | Fair_Mixed | 6913.2 | 11699.5 | 1.692 | 0.681 | 4.72 | 0.673 | 4.65 | 0.5878 | 0.8221 | 0.6208 | 0.7625 | 1 | 0.58 | 0.599 | 0.6948 | 0.6948 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
326 | 544.3 | 266.4 | 76.4 | 72.7 | 2 | 496.5 | 3360.9 | 57.1 | 22.1 | 76.5 | 75.4 | 72.3 | 84.7 | 35 | 13.7 | 8016.7 | 8241.4 | 8963.9 | 15581.5 | 14569.2 | 16233.2 | 1.944 | 1.768 | 1.811 | 0.585 | 0.509 | 0.572 | 3.24 | -2.59 | 3.27 | 0.514 | 0.587 | 0.585 | 2.74 | 2.93 | 2.94 | 0.774 | 0.501 | 0.576 | 5.79 | 3.07 | 3.28 | 0.54 | 0.545 | 0.54 | 2.53 | 2.92 | 2.74 | Poor_Bushing_TD_Cap | 8016.7 | 14569.2 | 1.768 | 0.585 | 3.27 | 0.774 | 5.79 | 0.7936 | 0.926 | 0.9186 | 0.9269 | 1 | 0.7855 | 0.7203 | 0.8473 | 0.8473 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
327 | 1045.9 | 501.2 | 106.6 | 125 | 19.6 | 902.5 | 5603 | 45.1 | 35.6 | 92.8 | 90.6 | 82.7 | 100.2 | 40 | 25.3 | 5927.4 | 5122.3 | 6523.5 | 9137.6 | 7776.6 | 10796.1 | 1.542 | 1.518 | 1.655 | 0.759 | 0.735 | 0.78 | 5.7 | 5.79 | 5.54 | 0.6 | 0.681 | 0.643 | 4.25 | 4.69 | 5.18 | 0.595 | 0.688 | 0.653 | -4.03 | 3.7 | -4.95 | 0.646 | 0.623 | 0.644 | 5.26 | 4.23 | 3.97 | Poor_Mixed | 5122.3 | 7776.6 | 1.518 | 0.78 | 5.79 | 0.688 | 5.26 | 0.3963 | 0.7276 | 0.4848 | 0.569 | 1 | 0.4003 | 0.5356 | 0.5758 | 0.5758 | Poor | 0 | 1 | DGA | 0 |  | C2H2
328 | 1766 | 946.1 | 144.1 | 185.3 | 34 | 1343.9 | 8511.7 | 33.6 | 47.3 | 106.5 | 103.6 | 94 | 114.5 | 43.8 | 32.6 | 1069.9 | 1814.4 | 1785.3 | 1200 | 2092.1 | 2093.5 | 1.122 | 1.153 | 1.173 | 0.872 | 0.927 | 0.924 | 7.95 | -8.9 | 8.45 | 0.739 | 0.822 | 0.847 | 6.9 | -7.06 | 8.45 | 0.893 | 0.872 | 0.84 | 7.91 | -7.73 | 6.65 | 0.832 | 0.782 | 0.801 | 7.79 | 9.84 | -7.57 | Very Poor_Mixed | 1069.9 | 1200 | 1.122 | 0.927 | 8.9 | 0.893 | 9.84 | 0.0558 | 0.6081 | 0.1616 | 0.2982 | 1 | 0.1406 | 0.2182 | 0.337 | 0.337 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
329 | 1167.1 | 583.2 | 108.3 | 121.8 | 19.2 | 882.5 | 5789.2 | 57 | 21.1 | 75 | 78.1 | 72.6 | 84.2 | 35.7 | 10.9 | 9256.8 | 9643.1 | 10000 | 17663.2 | 18841.4 | 19140.8 | 1.908 | 1.954 | 1.914 | 0.528 | 0.52 | 0.5 | 2.13 | 2.24 | -2.7 | 0.528 | 0.54 | 0.545 | 3.21 | -2.44 | 3.76 | 0.557 | 0.534 | 0.534 | -3.1 | -2.25 | 2.62 | 0.544 | 0.51 | 0.554 | 2.87 | 2 | 2.77 | Poor_DGA | 9256.8 | 17663.2 | 1.908 | 0.528 | 2.7 | 0.557 | 3.76 | 0.3825 | 0.9514 | 0.9076 | 0.9875 | 1 | 0.9104 | 0.7881 | 0.7793 | 0.7793 | Fair | 1 | 1 | DGA | 0 |  | C2H2
330 | 950.1 | 588.8 | 113.2 | 132.9 | 17.3 | 968.1 | 6127.8 | 56.5 | 23.1 | 78.5 | 77.9 | 70 | 82.9 | 36 | 11.3 | 9740.3 | 8879.3 | 9336.4 | 18803 | 16327.8 | 17902.6 | 1.93 | 1.839 | 1.918 | 0.548 | 0.616 | 0.649 | 3.55 | -3.54 | -4.08 | 0.565 | 0.579 | 0.634 | -3.02 | 4.44 | 3.97 | 0.549 | 0.55 | 0.613 | 2.88 | 2.65 | 2.75 | 0.527 | 0.528 | 0.551 | 3.1 | -3.16 | 2.38 | Poor_DGA | 8879.3 | 16327.8 | 1.839 | 0.649 | 4.08 | 0.634 | 4.44 | 0.382 | 0.9047 | 0.8986 | 0.9802 | 1 | 0.6698 | 0.7149 | 0.7254 | 0.7254 | Fair | 1 | 1 | DGA | 0 |  | C2H2
331 | 1583.9 | 925 | 141.9 | 182.7 | 34.3 | 1286.3 | 8589.8 | 32.9 | 46 | 106.7 | 104.7 | 93.4 | 114 | 44.4 | 30.5 | 1317.2 | 1664 | 1584.9 | 1431.5 | 1895 | 1734.1 | 1.087 | 1.139 | 1.094 | 0.911 | 0.912 | 0.984 | 8.46 | 8.6 | -9.12 | 0.895 | 0.946 | 0.838 | -8.22 | -6.92 | 8.71 | 0.808 | 0.801 | 0.821 | 7.03 | -6.75 | 5.22 | 0.873 | 0.955 | 0.895 | 9.58 | -6.68 | -8.24 | Very Poor_Mixed | 1317.2 | 1431.5 | 1.087 | 0.984 | 9.12 | 0.955 | 9.58 | 0.0788 | 0.6203 | 0.1558 | 0.3787 | 1 | 0.1065 | 0.1874 | 0.3373 | 0.3373 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
332 | 891.9 | 526.4 | 106.2 | 113.6 | 18.7 | 859.1 | 5632.2 | 59.8 | 21.2 | 79.6 | 79.9 | 73 | 83.9 | 36.7 | 11.5 | 9382.5 | 10000 | 9612.4 | 17978.6 | 20000 | 19224.8 | 1.916 | 2 | 2 | 0.568 | 0.588 | 0.55 | 2.49 | 3.83 | 2.68 | 0.531 | 0.536 | 0.531 | 2.89 | 2.26 | 2.59 | 0.563 | 0.526 | 0.513 | 3.26 | 2.29 | -2.86 | 0.503 | 0.517 | 0.571 | 2 | 3.06 | 3.36 | Poor_DGA | 9382.5 | 17978.6 | 1.916 | 0.588 | 3.83 | 0.571 | 3.36 | 0.4271 | 0.9486 | 0.8297 | 0.9764 | 1 | 0.7606 | 0.8117 | 0.765 | 0.765 | Fair | 1 | 1 | DGA | 0 |  | C2H2
333 | 1249.4 | 737.9 | 125.3 | 152.7 | 20.8 | 916.4 | 6615.2 | 55.1 | 23.2 | 82.3 | 80.1 | 75.5 | 89.5 | 38 | 13 | 9923.6 | 9328.8 | 9842.3 | 19262 | 18000 | 19583.6 | 1.941 | 1.93 | 1.99 | 0.546 | 0.548 | 0.526 | 2.24 | 3.49 | 2.36 | 0.572 | 0.538 | 0.539 | -2.55 | 2.14 | -2.83 | 0.552 | 0.549 | 0.527 | 2.88 | 2.64 | 2.39 | 0.573 | 0.561 | 0.585 | 3.16 | -2.15 | 2.65 | Poor_DGA | 9328.8 | 18000 | 1.93 | 0.548 | 3.49 | 0.585 | 3.16 | 0.2954 | 0.9027 | 0.7504 | 0.9438 | 1 | 0.8272 | 0.758 | 0.7167 | 0.7167 | Fair | 1 | 1 | DGA | 0 |  | C2H2
334 | 1644.2 | 859.5 | 139.4 | 180.3 | 34.3 | 1299.9 | 8131.1 | 31.7 | 47.7 | 108.2 | 105 | 93.1 | 114.8 | 44.5 | 33 | 2712.8 | 1206.9 | 1649.1 | 3354.7 | 1268.2 | 1782.4 | 1.237 | 1.051 | 1.081 | 0.94 | 0.936 | 0.983 | 9.5 | 9.38 | -9.16 | 0.805 | 0.809 | 0.821 | 6.13 | 6.94 | 7.58 | 0.866 | 0.8 | 0.945 | 5.51 | -9.1 | 6.12 | 0.738 | 0.894 | 0.793 | -5.64 | 5.73 | 6.38 | Very Poor_Mixed | 1206.9 | 1268.2 | 1.051 | 0.983 | 9.5 | 0.945 | 9.1 | 0.0902 | 0.6044 | 0.1429 | 0.2826 | 1 | 0.0634 | 0.2541 | 0.3381 | 0.3381 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
335 | 192.9 | 162.4 | 76 | 59.2 | 3.4 | 350 | 2500 | 59.1 | 22.9 | 75 | 75.7 | 70 | 81.7 | 36.2 | 13.8 | 9606.5 | 9515.6 | 9362.3 | 18919.6 | 18220.3 | 18194.3 | 1.969 | 1.915 | 1.943 | 0.542 | 0.537 | 0.584 | 2 | 2.1 | -2.97 | 0.5 | 0.527 | 0.522 | 2.64 | -2.19 | 2.04 | 0.5 | 0.565 | 0.543 | -2 | 2.48 | 2.18 | 0.508 | 0.509 | 0.5 | 2.46 | -2.47 | 2.44 | Good_Mixed | 9362.3 | 18194.3 | 1.915 | 0.584 | 2.97 | 0.565 | 2.64 | 0.8601 | 0.9088 | 0.9734 | 0.9244 | 1 | 0.8314 | 0.8866 | 0.9036 | 0.9036 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
336 | 869 | 592.9 | 113.6 | 126.1 | 17.4 | 836.8 | 5914.9 | 46.4 | 34.8 | 91.7 | 91.8 | 86 | 102.3 | 39.8 | 24.8 | 5708.7 | 6241.8 | 6100.7 | 8800.8 | 10053.8 | 9459.6 | 1.542 | 1.611 | 1.551 | 0.763 | 0.795 | 0.776 | 6.39 | -6.17 | 5.98 | 0.665 | 0.663 | 0.689 | -3.89 | 4.01 | 3.81 | 0.612 | 0.663 | 0.69 | 4.18 | -4.09 | 4.64 | 0.678 | 0.676 | 0.686 | 3.76 | 2.69 | 4.01 | Poor_Mixed | 5708.7 | 8800.8 | 1.542 | 0.795 | 6.39 | 0.69 | 4.64 | 0.4117 | 0.7368 | 0.4544 | 0.5865 | 1 | 0.356 | 0.5211 | 0.5697 | 0.5697 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
337 | 942.8 | 578.9 | 109 | 127.8 | 20.7 | 886.9 | 5759.9 | 44.7 | 33.5 | 93 | 88.7 | 84.3 | 99.3 | 40.1 | 24.9 | 4377.3 | 5237.6 | 4998.5 | 5785.7 | 7683.4 | 7070.6 | 1.322 | 1.467 | 1.415 | 0.719 | 0.714 | 0.76 | 6.86 | -5.27 | 5.78 | 0.771 | 0.69 | 0.657 | 4.26 | -4.4 | -5.21 | 0.688 | 0.634 | 0.674 | 5.45 | -3.35 | -4.03 | 0.597 | 0.706 | 0.723 | 4.24 | 6.01 | -5.37 | Poor_Mixed | 4377.3 | 5785.7 | 1.322 | 0.76 | 6.86 | 0.771 | 6.01 | 0.3849 | 0.752 | 0.49 | 0.5831 | 1 | 0.4078 | 0.4768 | 0.5675 | 0.5675 | Poor | 0 | 1 | DGA | 0 |  | C2H2
338 | 873.9 | 490.1 | 96.8 | 109.9 | 19.9 | 824.3 | 4880.1 | 58 | 23.7 | 77.4 | 75 | 70 | 80.9 | 35.9 | 13.3 | 10000 | 10000 | 8761.3 | 19617 | 19634.1 | 16425.2 | 1.962 | 1.963 | 1.875 | 0.598 | 0.566 | 0.551 | -2.82 | 2.68 | 2.77 | 0.518 | 0.5 | 0.526 | 2.6 | 2.19 | 2.1 | 0.517 | 0.522 | 0.523 | 2 | 2 | 2.66 | 0.5 | 0.521 | 0.5 | 3.2 | 2.44 | 2.13 | Poor_DGA | 8761.3 | 16425.2 | 1.875 | 0.598 | 2.82 | 0.526 | 3.2 | 0.4478 | 0.8931 | 0.9586 | 0.9367 | 1 | 0.7719 | 0.895 | 0.791 | 0.791 | Fair | 1 | 1 | DGA | 0 |  | C2H2
339 | 249.6 | 179.2 | 73.5 | 59.1 | 1.9 | 512.3 | 2500 | 50.8 | 26.4 | 85.6 | 88.6 | 78.1 | 94.1 | 37.5 | 19.2 | 1070.7 | 690 | 1173.2 | 1151.9 | 703.8 | 1196.7 | 1.076 | 1.02 | 1.02 | 0.739 | 0.68 | 0.686 | -5.29 | -5.35 | 5.09 | 0.614 | 0.533 | 0.575 | 2.69 | 2.72 | 2.12 | 0.512 | 0.536 | 0.527 | -2.98 | 3.39 | 2.5 | 0.538 | 0.559 | 2.41 | 2 | 3.28 | 2.98 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.739 | 5.35 | 2.41 | 3.39 | 0.8569 | 0.8474 | 0.6226 | 0.7718 | 0.925 | 0.4744 | 0.7134 | 0.7596 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_TV_B_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
340 | 987.4 | 486.1 | 110 | 121.8 | 20.9 | 803 | 5438.2 | 46.1 | 35.6 | 91.1 | 88.3 | 82.6 | 98.2 | 39.5 | 24.4 | 5990.7 | 6721.3 | 6191.2 | 9212.4 | 10461.8 | 9001.3 | 1.538 | 1.557 | 1.454 | 0.774 | 0.72 | 0.734 | 5.9 | 5.94 | 4.91 | 0.733 | 0.632 | 0.701 | 5.37 | 4.52 | 5.83 | 0.685 | 0.598 | 0.652 | 4.88 | 4.66 | 5.13 | 0.611 | 0.625 | 0.723 | 3.64 | -4.2 | 3.49 | Poor_Mixed | 5990.7 | 9001.3 | 1.454 | 0.774 | 5.94 | 0.733 | 5.83 | 0.4095 | 0.7276 | 0.5249 | 0.6005 | 1 | 0.4189 | 0.5044 | 0.5816 | 0.5816 | Poor | 0 | 1 | DGA | 0 |  | C2H2
341 | 316.3 | 160.9 | 73.1 | 60.9 | 1.8 | 505.1 | 3277 | 53.8 | 23.6 | 79.6 | 78.7 | 70 | 84.8 | 35.9 | 10.3 | 6044.1 | 5884 | 6823 | 9874.5 | 9657.7 | 11346.5 | 1.634 | 1.641 | 1.663 | 0.551 | 0.577 | 0.597 | -2.31 | 3.06 | -3.57 | 0.5 | 0.512 | 0.518 | 2 | 2.34 | 2.79 | 0.542 | 0.5 | 0.552 | 2.19 | 2.17 | -2 | 0.516 | 0.597 | 0.518 | -2.7 | 2.07 | 2.26 | Fair_IR_PI | 5884 | 9657.7 | 1.634 | 0.597 | 3.57 | 0.597 | 2.79 | 0.8506 | 0.895 | 0.8717 | 0.9968 | 1 | 0.7534 | 0.8607 | 0.8775 | 0.8775 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
342 | 146.4 | 180.7 | 69 | 61.4 | 1 | 471.2 | 3147.5 | 50.9 | 27.7 | 77.1 | 75 | 72.3 | 80 | 35.7 | 12.7 | 8892.2 | 8869.8 | 8756.9 | 16811 | 17067.2 | 16041.4 | 1.891 | 1.924 | 1.832 | 0.529 | 0.544 | 0.588 | 2 | 3.14 | 2.77 | 0.5 | 0.548 | 0.531 | -2.42 | -2.01 | 2 | 0.527 | 0.504 | 0.534 | 3.07 | 3.01 | 2.62 | 0.5 | 0.537 | 0.524 | 2 | 2.66 | 3.11 | Fair_Oil | 8756.9 | 16041.4 | 1.832 | 0.588 | 3.14 | 0.548 | 3.11 | 0.9328 | 0.8279 | 0.9415 | 0.9507 | 1 | 0.8124 | 0.8576 | 0.9023 | 0.9023 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
343 | 250.7 | 158.6 | 65 | 53.4 | 1.3 | 350 | 2500 | 60 | 20 | 75 | 77.2 | 72.9 | 83.3 | 35 | 13.3 | 10000 | 9892.2 | 9041.7 | 20000 | 19750.2 | 17658.8 | 2 | 1.997 | 1.953 | 0.511 | 0.502 | 0.5 | 2.15 | -2 | 2.52 | 0.542 | 0.557 | 0.506 | 3.12 | 2 | 2 | 0.525 | 0.533 | 0.5 | 2 | 2.39 | 2 | 0.501 | 0.52 | 0.507 | -2.34 | 2.46 | 2.14 | Good_Mixed | 9041.7 | 17658.8 | 1.953 | 0.511 | 2.52 | 0.557 | 3.12 | 0.9296 | 1 | 0.9213 | 0.9367 | 1 | 0.955 | 0.8768 | 0.9429 | 0.9429 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
344 | 500.4 | 309 | 87.6 | 87.6 | 3.8 | 572.9 | 4250.6 | 52.8 | 27.7 | 84.2 | 86.5 | 76.4 | 92 | 38 | 17.9 | 8764.9 | 8182.2 | 8085.1 | 15384 | 15293.5 | 15295.2 | 1.755 | 1.869 | 1.892 | 0.551 | 0.558 | 0.569 | -3.31 | 2.8 | 14.07 | 0.532 | 0.6 | 0.624 | -3.04 | 3.97 | -4.49 | 0.595 | 0.531 | 0.561 | 3.76 | -3.5 | 3.54 | 0.6 | 0.955 | 0.536 | 2.87 | -9.23 | 2.88 | Critical_Bushing_TD_Cap | 8085.1 | 15293.5 | 1.755 | 0.569 | 14.07 | 0.955 | 9.23 | 0.7103 | 0.8279 | 0.6671 | 0.8114 | 1 | 0.6413 | 0.6177 | 0.7452 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
345 | 1567.7 | 788.1 | 131 | 175.6 | 27.4 | 1204.5 | 7039.5 | 32.9 | 44.4 | 102.5 | 103.8 | 93.6 | 113.7 | 43.1 | 31.7 | 3237.3 | 3028.8 | 2766.8 | 4214.9 | 3854.6 | 3268.4 | 1.302 | 1.273 | 1.181 | 0.946 | 0.859 | 0.884 | 9.01 | 7.4 | 8.16 | 0.829 | 0.72 | 0.894 | 6.48 | 5.2 | 8.14 | 0.869 | 0.826 | 0.826 | 9.15 | 7.66 | 5.55 | 0.835 | 0.741 | 0.897 | 5.32 | 8.07 | -8.88 | Very Poor_Mixed | 2766.8 | 3268.4 | 1.181 | 0.946 | 9.01 | 0.897 | 9.15 | 0.1696 | 0.6357 | 0.1941 | 0.3329 | 1 | 0.1614 | 0.2389 | 0.3803 | 0.3803 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
346 | 375.3 | 227.7 | 80.3 | 154 | 1.9 | 401.3 | 3291.2 | 58.1 | 23.2 | 109.1 | 108.3 | 109.2 | 118.5 | 45.9 | 13.8 | 9412.5 | 9215.6 | 8226.2 | 17319.4 | 17088.8 | 15655.2 | 1.84 | 1.854 | 1.903 | 0.583 | 0.549 | 0.523 | 2.99 | 2.54 | 2 | 0.633 | 0.636 | 0.642 | 3.46 | 3.47 | -2.44 | 0.598 | 0.623 | 0.635 | 3.84 | 3.73 | -3.16 | 0.541 | 0.621 | 0.564 | 3.48 | 4.06 | -3.38 | Critical_Thermal | 8226.2 | 15655.2 | 1.84 | 0.583 | 2.99 | 0.642 | 4.06 | 0.7479 | 0.9027 | 0.0533 | 0.9244 | 1 | 0.8249 | 0.6239 | 0.7346 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | C2H4
347 | 348 | 189.7 | 71.4 | 69 | 64 | 521.5 | 3176.2 | 54.8 | 27.8 | 83.8 | 83.9 | 78.5 | 91.6 | 37.5 | 15 | 7783.8 | 7400.1 | 7130 | 13097.1 | 12583.7 | 12331.5 | 1.683 | 1.7 | 1.73 | 0.935 | 0.969 | 0.963 | 8.3 | 9.05 | 9.72 | 0.55 | 0.568 | 0.516 | -3.32 | 2.43 | 2.89 | 0.557 | 0.53 | 0.53 | 3.18 | 3.06 | -2.76 | 0.557 | 0.529 | 0.569 | 2 | 3.12 | 2.66 | Critical_Winding_TD_Cap | 7130 | 12331.5 | 1.683 | 0.969 | 9.72 | 0.569 | 3.32 | 0.5708 | 0.8264 | 0.6791 | 0.8935 | 1 | 0.0779 | 0.7706 | 0.6641 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
348 | 1004 | 521.1 | 104.6 | 129.1 | 20 | 820.5 | 5472.4 | 44.8 | 35.3 | 89.1 | 87.7 | 80.3 | 98.2 | 39.2 | 26 | 6415.8 | 5589.9 | 5626 | 10542.8 | 8580.8 | 8388.9 | 1.643 | 1.535 | 1.491 | 0.744 | 0.779 | 0.774 | 6.77 | 6.69 | 6.41 | 0.71 | 0.747 | 0.613 | 5.49 | 4.28 | 3.13 | 0.669 | 0.723 | 0.773 | 4.46 | 5.3 | 4.76 | 0.628 | 0.644 | 0.661 | -4.74 | -4.65 | 3.83 | Poor_Mixed | 5589.9 | 8388.9 | 1.491 | 0.779 | 6.77 | 0.773 | 5.49 | 0.4039 | 0.731 | 0.559 | 0.5442 | 1 | 0.3423 | 0.4804 | 0.5662 | 0.5662 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
349 | 411.3 | 310.9 | 81.3 | 81.2 | 7.8 | 593.3 | 3574.1 | 53.1 | 27.1 | 83.4 | 85.5 | 77.1 | 87.9 | 36.6 | 17.4 | 7160.4 | 7323.1 | 7984.3 | 12160.4 | 12169.3 | 14258.7 | 1.698 | 1.662 | 1.786 | 0.563 | 0.653 | 0.565 | 3.34 | 4.33 | 2.34 | 0.605 | 0.589 | 0.533 | 3.15 | -3.47 | 3.36 | 0.548 | 0.601 | 0.557 | 3.98 | -3.04 | 3.52 | 0.59 | 0.579 | 0.53 | 3.36 | 3.61 | 3.64 | Fair_Mixed | 7160.4 | 12160.4 | 1.662 | 0.653 | 4.33 | 0.605 | 3.98 | 0.6809 | 0.8367 | 0.7035 | 0.8262 | 1 | 0.7095 | 0.6905 | 0.7659 | 0.7659 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
350 | 1256.8 | 740.1 | 127 | 152.7 | 26.1 | 1031.8 | 6653 | 39.4 | 41.1 | 101.1 | 102.9 | 89.9 | 110.9 | 41.7 | 33.1 | 2746.2 | 3077 | 3559.7 | 3528.2 | 4032.7 | 4476.2 | 1.285 | 1.311 | 1.257 | 0.82 | 0.765 | 0.879 | 7.72 | -6.75 | 7.4 | 0.859 | 0.752 | 0.799 | 6.79 | 6.05 | -7.97 | 0.728 | 0.693 | 0.742 | 14.69 | 5.6 | 7.12 | 0.829 | 0.871 | 0.842 | 4.94 | 5.15 | -5.45 | Critical_Mixed | 2746.2 | 3528.2 | 1.257 | 0.879 | 7.72 | 0.871 | 14.69 | 0.2509 | 0.6685 | 0.2519 | 0.2787 | 1 | 0.2636 | 0.2937 | 0.4318 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
351 | 890.8 | 568.2 | 103.2 | 123.3 | 23 | 832.9 | 5876.8 | 46.4 | 33.2 | 87.3 | 90 | 81.5 | 95.1 | 40 | 27.5 | 5381.8 | 5973 | 7018.9 | 8384.9 | 9688.5 | 11371.5 | 1.558 | 1.622 | 1.62 | 0.76 | 0.75 | 0.723 | 6 | 5.89 | 4.96 | 0.765 | 0.761 | 0.659 | 4.42 | -4.82 | 5.2 | 0.655 | 0.644 | 0.637 | 5.28 | 4.79 | 4.92 | 0.656 | 0.714 | 0.647 | -4.85 | 4.61 | 4.5 | Poor_Mixed | 5381.8 | 8384.9 | 1.558 | 0.76 | 6 | 0.765 | 5.28 | 0.3913 | 0.7556 | 0.5583 | 0.4902 | 1 | 0.4154 | 0.4715 | 0.5719 | 0.5719 | Poor | 0 | 1 | DGA | 0 |  | C2H2
352 | 154.7 | 178 | 75.2 | 77.3 | 1.8 | 456.5 | 2842.3 | 55.9 | 25 | 84.4 | 79.1 | 75.7 | 90.1 | 37.5 | 11.4 | 9347 | 7731.2 | 8046.6 | 17545.4 | 12944.7 | 14743.4 | 1.877 | 1.674 | 1.832 | 0.94 | 0.974 | 0.981 | 9.62 | 9.01 | 9.25 | 0.533 | 0.642 | 0.589 | 3.97 | -2.68 | 3.05 | 0.545 | 0.535 | 1.432 | 2.84 | 3.24 | 2.64 | 0.542 | 0.572 | 0.513 | 2.69 | -2 | 3.03 | Critical_Winding_TD_Cap | 7731.2 | 12944.7 | 1.674 | 0.981 | 9.62 | 1.432 | 3.97 | 0.8522 | 0.87 | 0.7416 | 0.9783 | 1 | 0.058 | 0.6893 | 0.7327 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_TV_TanDelta_pct
353 | 400.9 | 301.1 | 82.7 | 78.7 | 1.6 | 516.2 | 3489.5 | 25.5 | 25.8 | 83.1 | 84.2 | 77.8 | 89.4 | 37 | 16.4 | 840.8 | 1857 | 1008.4 | 857.6 | 1999.5 | 1028.6 | 1.02 | 1.077 | 1.02 | 0.74 | 0.703 | 0.746 | 5.58 | 4.85 | 5.51 | 0.512 | 0.548 | 0.511 | 2.2 | -2.91 | 3.17 | 0.5 | 0.5 | 0.515 | 3.07 | -2.51 | -2.1 | 0.513 | 0.578 | 0.537 | 2.38 | -3.45 | -2.47 | Critical_IR_PI | 840.8 | 857.6 | 1.02 | 0.746 | 5.58 | 0.578 | 3.45 | 0.8002 | 0.2735 | 0.7008 | 0.855 | 0.925 | 0.4451 | 0.8497 | 0.709 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
354 | 100 | 133.6 | 68.7 | 55.5 | 1 | 372.9 | 2668.9 | 60 | 21 | 79.3 | 78.4 | 72.6 | 85.1 | 36.3 | 13.7 | 9501.7 | 9731.1 | 9420.6 | 18165.2 | 19462.2 | 18105.9 | 1.912 | 2 | 1.922 | 0.552 | 0.5 | 0.545 | 2.69 | 2 | -2.67 | 0.542 | 0.505 | 0.54 | 2 | -2.64 | 2.48 | 0.531 | 0.517 | 0.5 | -2.32 | -2 | 2.15 | 0.517 | 0.505 | 0.5 | 2.32 | 2.37 | 2.02 | Good_Mixed | 9420.6 | 18105.9 | 1.912 | 0.552 | 2.69 | 0.542 | 2.64 | 0.976 | 0.9543 | 0.8455 | 0.9269 | 1 | 0.8739 | 0.8897 | 0.9319 | 0.9319 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
355 | 732.2 | 337.6 | 95.8 | 99.4 | 12.3 | 712.8 | 4288.4 | 51.1 | 25.5 | 85.2 | 88 | 76.7 | 91.2 | 37.7 | 19.1 | 5944.4 | 6899.3 | 6412 | 10068.7 | 11556.1 | 10306.2 | 1.694 | 1.675 | 1.607 | 0.706 | 0.596 | 0.671 | -5.29 | 3.89 | 4.88 | 0.615 | 0.646 | 0.638 | 4.05 | 4.61 | 3.35 | 0.581 | 0.619 | 0.594 | 4.15 | 3.57 | 2.97 | 0.618 | 0.569 | 0.68 | 4.05 | 4.73 | 3.2 | Fair_Mixed | 5944.4 | 10068.7 | 1.607 | 0.706 | 5.29 | 0.68 | 4.73 | 0.5586 | 0.8617 | 0.6528 | 0.7749 | 1 | 0.5519 | 0.5946 | 0.6914 | 0.6914 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
356 | 904.8 | 590.6 | 115.7 | 127.4 | 18.4 | 982.4 | 6290.8 | 53.6 | 24.3 | 76.7 | 81.3 | 71.8 | 83 | 35.1 | 17.3 | 8813.1 | 7707.4 | 9775.5 | 16228.8 | 13324.5 | 19551.1 | 1.841 | 1.729 | 2 | 0.556 | 0.55 | 0.552 | -2.81 | 2.44 | -2.68 | 0.5 | 0.516 | 0.507 | 2 | -2.36 | 2.9 | 0.506 | 0.548 | 0.5 | 2 | 2.09 | 2 | 0.5 | 0.5 | 0.519 | 2 | -2 | -2.51 | Poor_DGA | 7707.4 | 13324.5 | 1.729 | 0.556 | 2.81 | 0.548 | 2.9 | 0.3783 | 0.8821 | 0.8687 | 0.8291 | 1 | 0.8069 | 0.9265 | 0.7685 | 0.7685 | Fair | 1 | 1 | DGA | 0 |  | C2H2
357 | 793.7 | 528.3 | 101.3 | 117.4 | 15.5 | 701.2 | 5349.4 | 58.9 | 23.5 | 80.1 | 79.2 | 72.3 | 84.2 | 36.4 | 14 | 9871.4 | 10000 | 9153.6 | 18837.7 | 19592.3 | 17629.2 | 1.908 | 1.959 | 1.926 | 0.61 | 0.536 | 0.567 | 3.16 | 2.5 | 2.59 | 0.5 | 0.527 | 0.502 | 2 | -2.21 | 2.43 | 0.516 | 0.593 | 0.544 | 2.91 | 2.35 | 2.94 | 0.531 | 0.533 | 0.518 | -3.03 | 2.78 | 2.77 | Poor_DGA | 9153.6 | 17629.2 | 1.908 | 0.61 | 3.16 | 0.593 | 3.03 | 0.478 | 0.8969 | 0.8376 | 0.9194 | 1 | 0.7762 | 0.8345 | 0.7757 | 0.7757 | Fair | 1 | 1 | DGA | 0 |  | C2H2
358 | 337.3 | 301.5 | 71 | 73.4 | 3 | 468.9 | 3676.4 | 57.1 | 21.8 | 75.2 | 76.2 | 71.3 | 81.8 | 35.9 | 12.7 | 9782.6 | 9612.7 | 8981.4 | 19273.8 | 18727.7 | 16450.9 | 1.97 | 1.948 | 1.832 | 0.801 | 0.844 | 0.848 | -6.35 | 6.9 | 7.09 | 0.552 | 0.567 | 0.5 | -3.09 | 3.23 | -2.58 | 0.506 | 0.566 | 0.528 | 3.06 | 2.81 | 2.42 | 0.568 | 0.5 | 0.585 | 2.48 | 3.3 | 3.1 | Poor_Winding_TD_Cap | 8981.4 | 16450.9 | 1.832 | 0.848 | 7.09 | 0.585 | 3.3 | 0.7884 | 0.9331 | 0.9462 | 0.9507 | 1 | 0.2823 | 0.7967 | 0.7942 | 0.7942 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
359 | 1435.5 | 839.6 | 137.9 | 178.9 | 30.3 | 1200.9 | 7363.8 | 34.1 | 45.7 | 105.4 | 107.2 | 93.5 | 115.4 | 43.8 | 32.1 | 1717.1 | 1551.4 | 2227.7 | 1948.3 | 1786.6 | 2656.1 | 1.135 | 1.152 | 1.192 | 0.947 | 0.937 | 0.945 | -9.73 | 9.39 | 9.18 | 0.932 | 0.865 | 0.803 | 7.53 | 7.29 | 8.43 | 0.807 | 0.74 | 0.931 | 6.5 | -7.01 | 8.16 | 0.854 | 0.798 | 0.912 | 6.29 | 8.46 | 7.56 | Very Poor_Mixed | 1551.4 | 1786.6 | 1.135 | 0.947 | 9.73 | 0.932 | 8.46 | 0.1481 | 0.6232 | 0.146 | 0.3175 | 1 | 0.0657 | 0.2069 | 0.3487 | 0.3487 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
360 | 1654.4 | 876.5 | 135.4 | 190.3 | 30.2 | 1228.2 | 7933.6 | 33.1 | 47.6 | 106.2 | 109.3 | 93 | 117.9 | 44.5 | 33.8 | 1409 | 1507.8 | 1661.5 | 1479.4 | 1698.8 | 1882.6 | 1.05 | 1.127 | 1.133 | 0.974 | 0.987 | 0.99 | 9.31 | -9.84 | 9.73 | 0.9 | 0.88 | 0.885 | 7.33 | 5.29 | 8.35 | 0.884 | 0.925 | 0.73 | 8.83 | 7.6 | 8.88 | 0.93 | 0.803 | 0.836 | 7.51 | 6.68 | 8.19 | Very Poor_Mixed | 1409 | 1479.4 | 1.05 | 0.99 | 9.84 | 0.93 | 8.88 | 0.1112 | 0.6053 | 0.1154 | 0.2513 | 1 | 0.0291 | 0.1889 | 0.3226 | 0.3226 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
361 | 805.8 | 504.5 | 96.5 | 118.2 | 14.3 | 785.1 | 5324 | 49.3 | 32.2 | 88.6 | 92.4 | 79.3 | 97.4 | 38.9 | 22.2 | 5868 | 5882.4 | 5756.1 | 9226.1 | 9372.2 | 9167.3 | 1.572 | 1.593 | 1.593 | 0.659 | 0.753 | 0.719 | -5.01 | 5.59 | 6.31 | 0.603 | 0.618 | 0.623 | -4.16 | 4.77 | 3.93 | 0.586 | 0.663 | 0.651 | 3.77 | 4.51 | -4.7 | 0.747 | 0.705 | 0.674 | 3.3 | 4.19 | 4.71 | Poor_Mixed | 5756.1 | 9167.3 | 1.572 | 0.753 | 6.31 | 0.747 | 4.77 | 0.48 | 0.7678 | 0.5437 | 0.6753 | 1 | 0.4455 | 0.5331 | 0.6186 | 0.6186 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
362 | 810.3 | 444.9 | 111 | 110.3 | 16.8 | 850.4 | 4979.4 | 45 | 32.7 | 92.6 | 91 | 81.1 | 99 | 39.7 | 25 | 5035.6 | 5854.6 | 6356.1 | 8443.7 | 8947.7 | 10151.1 | 1.677 | 1.528 | 1.597 | 0.745 | 0.794 | 0.759 | 5.37 | -6.22 | -5.7 | 0.787 | 0.603 | 0.808 | 4.9 | 6.65 | 3.8 | 0.667 | 0.662 | 0.693 | 5.2 | 4.54 | 5.05 | 0.688 | 0.744 | 0.726 | 5.14 | 5.9 | 4.69 | Poor_Mixed | 5035.6 | 8443.7 | 1.528 | 0.794 | 6.22 | 0.808 | 6.65 | 0.4621 | 0.7617 | 0.5016 | 0.5796 | 1 | 0.389 | 0.4322 | 0.5783 | 0.5783 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
363 | 842.6 | 548.1 | 99.9 | 119.3 | 20 | 738.5 | 5800.9 | 45.5 | 36.5 | 91.8 | 91.1 | 83 | 102 | 40 | 25.8 | 4441.5 | 5681.9 | 4207.3 | 6381.4 | 8135.3 | 5683 | 1.437 | 1.432 | 1.351 | 0.739 | 0.734 | 0.747 | 6.22 | 5.22 | -5.48 | 0.727 | 0.605 | 0.694 | 3.64 | 4.55 | 4.21 | 0.653 | 0.703 | 0.62 | 3.65 | 4.73 | 4.31 | 0.631 | 0.633 | 0.605 | 4.29 | 4.57 | 4.39 | Poor_Mixed | 4207.3 | 5683 | 1.351 | 0.747 | 6.22 | 0.727 | 4.73 | 0.4332 | 0.7175 | 0.477 | 0.5513 | 1 | 0.4176 | 0.5304 | 0.5836 | 0.5836 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
364 | 381.6 | 343.3 | 82.1 | 89.4 | 5.2 | 595.5 | 4055.1 | 59.6 | 20.8 | 75 | 75.2 | 71.4 | 82.8 | 35.5 | 13.6 | 9779.1 | 9010.4 | 240.5 | 18589.3 | 17167.3 | 279.7 | 1.901 | 1.905 | 1.163 | 0.937 | 0.983 | 0.962 | 9.44 | 9.84 | 9.2 | 0.587 | 0.561 | 0.545 | 2.44 | 2.28 | 2.57 | 0.585 | 0.633 | 0.64 | -4.07 | 3.05 | -3.02 | 0.592 | 0.594 | 0.611 | 3.32 | -3.92 | -3.55 | Critical_Winding_TD_Cap | 240.5 | 279.7 | 1.163 | 0.983 | 9.84 | 0.64 | 4.07 | 0.6961 | 0.9605 | 0.9619 | 0.9294 | 0.85 | 0.051 | 0.6626 | 0.6943 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
365 | 280.3 | 220.6 | 65 | 56.7 | 1 | 350 | 2904.4 | 58 | 22.1 | 76.5 | 75 | 71.5 | 82 | 36 | 12.1 | 9855.1 | 10000 | 9689.6 | 19710.2 | 20000 | 18180.2 | 2 | 2 | 1.876 | 0.531 | 0.535 | 0.515 | 2 | -2.7 | 2.49 | 0.557 | 0.531 | 0.5 | 2.09 | 2.66 | -2.21 | 0.544 | 0.533 | 0.533 | 2.46 | 2.21 | 2 | 0.523 | 0.545 | 0.59 | 2.85 | -2.82 | 2.07 | Good_Mixed | 9689.6 | 18180.2 | 1.876 | 0.535 | 2.7 | 0.59 | 2.85 | 0.9494 | 0.926 | 0.9444 | 0.964 | 1 | 0.8744 | 0.8148 | 0.9202 | 0.9202 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
366 | 1515.9 | 873.5 | 138.8 | 171.6 | 34.3 | 1293.5 | 8081.8 | 32.7 | 48.3 | 109.3 | 109.3 | 97 | 118.1 | 44.6 | 33.7 | 1962.1 | 2209.5 | 1637.7 | 2076.6 | 2639.7 | 1809.6 | 1.058 | 1.195 | 1.105 | 0.95 | 0.911 | 0.955 | 8.89 | 9.37 | -9.34 | 0.929 | 0.953 | 0.911 | 8.93 | -9.74 | 8.37 | 0.849 | 0.87 | 0.94 | -6.16 | 7.42 | -8.08 | 0.741 | 0.983 | 0.869 | -6.67 | 6.93 | 7.13 | Very Poor_Mixed | 1637.7 | 1809.6 | 1.058 | 0.955 | 9.37 | 0.983 | 9.74 | 0.1069 | 0.5988 | 0.0747 | 0.2552 | 1 | 0.0804 | 0.16 | 0.3189 | 0.3189 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
367 | 483.1 | 240 | 82.9 | 91.7 | 7.7 | 533.6 | 4136.1 | 52.6 | 25.9 | 86.8 | 83 | 77.5 | 90.1 | 39 | 17.7 | 9018.7 | 8427 | 8957.8 | 16598.4 | 14921 | 17002.4 | 1.84 | 1.771 | 1.898 | 0.584 | 0.595 | 0.605 | 3.05 | 3.2 | -3.8 | 0.582 | 0.651 | 0.544 | -2.83 | -3.73 | -3.37 | 0.582 | 0.613 | 0.623 | 4.79 | 2.9 | 4.33 | 0.641 | 0.654 | 0.57 | 3.35 | 3.3 | 3.55 | Fair_Mixed | 8427 | 14921 | 1.771 | 0.605 | 3.8 | 0.654 | 4.79 | 0.6752 | 0.8552 | 0.6698 | 0.8173 | 1 | 0.7009 | 0.6249 | 0.7499 | 0.7499 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
368 | 602.5 | 375.6 | 85.6 | 93.8 | 11.8 | 621.7 | 4398.5 | 53.3 | 29 | 84.2 | 88.1 | 77.2 | 89.2 | 37.8 | 17.6 | 7715 | 6328.4 | 7686.3 | 13006.1 | 9855.4 | 12915.2 | 1.686 | 1.557 | 1.68 | 0.621 | 0.633 | 0.683 | 3.59 | 4.01 | 5.06 | 0.619 | 0.655 | 0.639 | 2.81 | 2.92 | -3.78 | 0.619 | 0.574 | 0.558 | -4.7 | 2.76 | -4.08 | 0.607 | 0.619 | 0.559 | 3.69 | -3.27 | 3.48 | Fair_Mixed | 6328.4 | 9855.4 | 1.557 | 0.683 | 5.06 | 0.655 | 4.7 | 0.5931 | 0.8095 | 0.6654 | 0.8203 | 1 | 0.59 | 0.6289 | 0.7088 | 0.7088 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
369 | 260.5 | 200.9 | 75.7 | 64.3 | 2.3 | 400.8 | 2846.3 | 57.8 | 21.6 | 76.4 | 78.5 | 70.7 | 82 | 36.5 | 17.9 | 9424.5 | 9313.9 | 9420.9 | 17433.8 | 17990.5 | 18841.9 | 1.85 | 1.932 | 2 | 0.505 | 0.5 | 0.524 | 2 | -2.31 | -2 | 0.523 | 0.527 | 0.541 | 2.82 | 2.32 | -2.66 | 0.5 | 0.501 | 0.5 | 2.74 | 2.26 | 2.52 | 0.5 | 0.532 | 0.55 | 2.39 | 2.55 | 2.17 | Fair_Age | 9313.9 | 17433.8 | 1.85 | 0.524 | 2.31 | 0.55 | 2.82 | 0.8505 | 0.938 | 0.907 | 0.8114 | 1 | 0.9501 | 0.8771 | 0.9073 | 0.9073 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
370 | 1569.2 | 817.4 | 138.5 | 185.1 | 34.3 | 1174.5 | 7472.5 | 31.3 | 48 | 104.1 | 106.4 | 91.6 | 116.8 | 44.5 | 31.2 | 1308.6 | 1045.3 | 690 | 1374.1 | 1200 | 1200 | 1.05 | 1.148 | 1.739 | 0.947 | 0.99 | 0.896 | 9.71 | 9.23 | 8.49 | 0.898 | 0.895 | 0.89 | 8.3 | 7.7 | -6.34 | 0.732 | 0.72 | 0.909 | 8.05 | 9.02 | -7.78 | 0.878 | 0.971 | 0.87 | 6.11 | 6.18 | -7.33 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.99 | 9.71 | 0.971 | 9.02 | 0.1191 | 0.6016 | 0.1563 | 0.3521 | 1 | 0.0798 | 0.198 | 0.342 | 0.342 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
371 | 1006.4 | 629.1 | 108 | 121.5 | 19.3 | 828.8 | 5626.3 | 58.8 | 21.6 | 77.6 | 76 | 70 | 80.5 | 35.2 | 12.7 | 7999.9 | 8446.5 | 9928.5 | 14375.8 | 15607.6 | 18701.1 | 1.797 | 1.848 | 1.884 | 0.523 | 0.501 | 0.565 | 2 | 2.58 | 3.68 | 0.521 | 0.577 | 0.53 | 3.19 | -2.31 | 2.43 | 0.558 | 0.574 | 0.563 | 2.81 | 2.87 | 2.45 | 0.5 | 0.602 | 0.505 | 2.42 | 2.82 | 2 | Poor_DGA | 7999.9 | 14375.8 | 1.797 | 0.565 | 3.68 | 0.602 | 3.19 | 0.3979 | 0.938 | 0.944 | 0.9507 | 1 | 0.8574 | 0.7917 | 0.7765 | 0.7765 | Fair | 1 | 1 | DGA | 0 |  | C2H2
372 | 794.1 | 559.5 | 113.8 | 129.9 | 19.1 | 934.4 | 6177.4 | 56 | 24.1 | 75.2 | 75.2 | 70.4 | 82.5 | 35.6 | 14.4 | 8283.3 | 9269.6 | 10000 | 14859.2 | 18539.1 | 19605.6 | 1.794 | 2 | 1.961 | 0.556 | 0.527 | 0.559 | -2 | 3.22 | -2.33 | 0.51 | 0.505 | 0.524 | -2.3 | 2.44 | 2.86 | 0.554 | 0.611 | 0.525 | 2 | -2.63 | 3.36 | 0.541 | 0.5 | 0.5 | -2.57 | 2.6 | 2 | Poor_DGA | 8283.3 | 14859.2 | 1.794 | 0.559 | 3.22 | 0.611 | 3.36 | 0.3923 | 0.8857 | 0.9687 | 0.9092 | 1 | 0.8299 | 0.8467 | 0.7753 | 0.7753 | Fair | 1 | 1 | DGA | 0 |  | C2H2
373 | 203.2 | 162.4 | 70.8 | 52.4 | 2.8 | 433.7 | 3247 | 59.2 | 21.1 | 75.4 | 75 | 70.7 | 80 | 35 | 11.9 | 8493.1 | 7432.8 | 8195.5 | 15492.2 | 13159.6 | 14748.5 | 1.824 | 1.77 | 1.8 | 0.579 | 0.594 | 0.557 | 3.31 | 2.44 | -2.25 | 0.539 | 0.5 | 0.559 | 2.37 | 2 | -2.05 | 0.531 | 0.5 | 0.5 | -2 | 2.44 | 2.22 | 0.528 | 0.5 | 0.5 | 2.94 | 2.11 | 2 | Fair_IR_PI | 7432.8 | 13159.6 | 1.77 | 0.594 | 3.31 | 0.559 | 2.94 | 0.8642 | 0.9514 | 0.9814 | 0.9682 | 1 | 0.7724 | 0.9084 | 0.9084 | 0.9084 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
374 | 133 | 156 | 68.9 | 60.4 | 3.4 | 463.9 | 3087.6 | 58.1 | 21.1 | 79.8 | 75.8 | 71.5 | 83.6 | 35.5 | 13.1 | 9187.8 | 9830.7 | 10000 | 17750 | 19449.9 | 18806.6 | 1.932 | 1.978 | 1.881 | 0.548 | 0.568 | 0.539 | 2.26 | 2.64 | 2.12 | 0.543 | 0.5 | 0.52 | 2.69 | -2.85 | -2 | 0.5 | 0.541 | 0.5 | 2.3 | 2.59 | 2.03 | 0.5 | 0.516 | 0.524 | 2.94 | 2 | 2.32 | Good_Mixed | 9187.8 | 17750 | 1.881 | 0.568 | 2.64 | 0.543 | 2.94 | 0.8436 | 0.9514 | 0.8911 | 0.9414 | 1 | 0.8328 | 0.8949 | 0.8989 | 0.8989 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
375 | 454.4 | 270.8 | 81.1 | 68 | 2.2 | 610.3 | 3675.9 | 56.6 | 21.1 | 79.6 | 76.4 | 73.7 | 82 | 35.8 | 13.4 | 799.8 | 1269.2 | 760.3 | 827.4 | 1305.2 | 797.2 | 1.035 | 1.028 | 1.049 | 0.735 | 0.643 | 0.657 | 5.18 | -10.95 | -4.54 | 0.503 | 0.547 | 0.522 | 2 | 2.32 | 2.06 | 0.517 | 0.551 | 0.557 | 2.56 | 2.21 | 2.34 | 0.5 | 0.5 | 0.568 | -2.51 | 2 | 2.34 | Critical_IR_PI | 760.3 | 797.2 | 1.028 | 0.735 | 10.95 | 0.568 | 2.56 | 0.7794 | 0.9514 | 0.8726 | 0.9342 | 0.85 | 0.4293 | 0.8584 | 0.7936 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_LV_CapChange_pct
376 | 741.5 | 507.4 | 105.9 | 120.2 | 18.1 | 711.4 | 5394.8 | 48.8 | 32.1 | 89.9 | 89.7 | 80.4 | 94.1 | 39 | 24.9 | 6172.1 | 5844.5 | 6457.9 | 9941.6 | 9361.6 | 10041.3 | 1.611 | 1.602 | 1.555 | 0.696 | 0.742 | 0.763 | 5.29 | -4.87 | 6 | 0.648 | 0.552 | 0.667 | 4.87 | 5.07 | 5.67 | 0.585 | 0.616 | 0.684 | 4.38 | 4.96 | -4.24 | 0.696 | 0.693 | 0.642 | 4.23 | 4.17 | -3.96 | Poor_Mixed | 5844.5 | 9361.6 | 1.555 | 0.763 | 6 | 0.696 | 5.67 | 0.4599 | 0.7691 | 0.5611 | 0.5831 | 1 | 0.4379 | 0.5324 | 0.6097 | 0.6097 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
377 | 1620.2 | 943.4 | 137.7 | 184.6 | 33.9 | 1259.9 | 7806.9 | 34.5 | 44.9 | 104.9 | 106.7 | 92.3 | 113.4 | 44.7 | 31.5 | 1185.1 | 2389 | 2016.3 | 1286.4 | 2834.8 | 2376.8 | 1.085 | 1.187 | 1.179 | 0.908 | 0.873 | 0.935 | 8.78 | 8.24 | 8.53 | 0.82 | 0.824 | 0.788 | 7.1 | 8.46 | 8.59 | 0.711 | 0.844 | 0.812 | -8.06 | 5.13 | 6.53 | 0.897 | 0.814 | 0.889 | -6.82 | 8.57 | 5.39 | Very Poor_Mixed | 1185.1 | 1286.4 | 1.085 | 0.935 | 8.78 | 0.897 | 8.59 | 0.0909 | 0.6309 | 0.1617 | 0.3406 | 1 | 0.1379 | 0.2413 | 0.3544 | 0.3544 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
378 | 1528.5 | 807.3 | 134.8 | 173.1 | 34.3 | 1238.4 | 7910.4 | 35.6 | 42.8 | 100.9 | 101.7 | 90.6 | 110.8 | 42.2 | 28.6 | 3226.5 | 1729.2 | 2389.3 | 3664.2 | 2083.1 | 2810.9 | 1.136 | 1.205 | 1.176 | 0.911 | 0.905 | 0.887 | 9.11 | -8.61 | -8.31 | 0.78 | 0.897 | 0.931 | -5.15 | 8.14 | 8 | 0.904 | 0.719 | 0.711 | 7.6 | 6.48 | -6.58 | 0.768 | 0.735 | 0.735 | 6.7 | 7.84 | -4.92 | Very Poor_Mixed | 1729.2 | 2083.1 | 1.136 | 0.911 | 9.11 | 0.931 | 8.14 | 0.1234 | 0.6514 | 0.253 | 0.4498 | 1 | 0.1327 | 0.2792 | 0.3856 | 0.3856 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
379 | 772 | 448.5 | 100.1 | 109.8 | 14.6 | 803.1 | 5132.2 | 47.8 | 29.1 | 84.4 | 84.2 | 77.1 | 93.1 | 37.4 | 19.8 | 6872.3 | 6621.3 | 7240.6 | 11306.6 | 11216.8 | 12081 | 1.645 | 1.694 | 1.669 | 0.595 | 0.644 | 0.654 | 3.99 | -4.95 | 4.87 | 0.687 | 0.571 | 0.653 | 2.88 | -3.54 | 2.86 | 0.595 | 0.564 | 0.587 | -3.88 | 3.25 | 4.52 | 0.606 | 0.628 | 0.657 | 3.17 | -4.32 | 3.29 | Fair_Mixed | 6621.3 | 11216.8 | 1.645 | 0.654 | 4.95 | 0.687 | 4.52 | 0.4924 | 0.8081 | 0.6752 | 0.753 | 1 | 0.5829 | 0.6118 | 0.677 | 0.677 | Fair | 1 | 1 | DGA | 0 |  | C2H2
380 | 1657.2 | 895.2 | 138.1 | 181 | 34.2 | 1215.5 | 8087.7 | 33.3 | 47.3 | 104.3 | 107.1 | 92.5 | 113.7 | 43.5 | 31.7 | 3374 | 1824.7 | 1927.3 | 4576.9 | 2152.6 | 2286.9 | 1.357 | 1.18 | 1.187 | 0.972 | 0.906 | 0.922 | 9.59 | 9 | 9.2 | 0.815 | 0.895 | 0.724 | 8.78 | 6.7 | 6.56 | 0.729 | 0.879 | 0.851 | 7.73 | -5.42 | 6.08 | 0.8 | 0.904 | 0.72 | 9.66 | 8.78 | 5.53 | Very Poor_Mixed | 1824.7 | 2152.6 | 1.18 | 0.972 | 9.59 | 0.904 | 9.66 | 0.0961 | 0.6081 | 0.1689 | 0.3329 | 1 | 0.081 | 0.2497 | 0.3468 | 0.3468 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
381 | 361.2 | 236.4 | 73.1 | 64.3 | 1 | 417.1 | 2813.9 | 59.3 | 20 | 75.4 | 77.4 | 73 | 80.2 | 35.5 | 15 | 6304.7 | 5988.4 | 6010.4 | 9904 | 9697.7 | 9923.5 | 1.571 | 1.619 | 1.651 | 0.57 | 0.598 | 0.628 | -3.46 | 3.28 | 3.45 | 0.533 | 0.557 | 0.5 | 2.49 | -2 | 2.1 | 0.5 | 0.518 | 0.533 | 3.04 | 2.28 | -2.16 | 0.528 | 0.524 | 0.527 | 2 | 2.17 | 2.87 | Poor_IR_PI | 5988.4 | 9697.7 | 1.571 | 0.628 | 3.46 | 0.557 | 3.04 | 0.9088 | 1 | 0.9234 | 0.8935 | 1 | 0.6938 | 0.8609 | 0.8963 | 0.8963 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
382 | 806.6 | 450.8 | 104.1 | 108.9 | 17.8 | 708.1 | 4944.1 | 46 | 36.6 | 90 | 90.2 | 84 | 98 | 39.8 | 25 | 6142.9 | 4158 | 4285.7 | 9320.8 | 6161.3 | 6106.2 | 1.517 | 1.482 | 1.425 | 0.733 | 0.709 | 0.697 | 5.59 | -5.8 | 5.71 | 0.745 | 0.657 | 0.769 | -5.05 | 5.93 | 4.97 | 0.601 | 0.765 | 0.741 | 5.69 | 5.86 | 3.57 | 0.636 | 0.629 | 0.613 | 5.44 | 4.69 | -4.16 | Poor_Mixed | 4158 | 6106.2 | 1.425 | 0.733 | 5.8 | 0.769 | 5.93 | 0.4804 | 0.7164 | 0.5097 | 0.5796 | 1 | 0.4381 | 0.465 | 0.591 | 0.591 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
383 | 910.4 | 544.6 | 106.7 | 110.4 | 18.1 | 888.3 | 5763.9 | 45.7 | 32.3 | 91.1 | 93.5 | 83.3 | 99 | 39.8 | 25.3 | 6358 | 5519.4 | 5967.1 | 10316.2 | 8740.8 | 9093.1 | 1.623 | 1.584 | 1.524 | 0.689 | 0.785 | 0.727 | 5.33 | 6.67 | 5.85 | 0.688 | 0.616 | 0.69 | -5.75 | -3.96 | -4.23 | 0.635 | 0.695 | 0.685 | 4.48 | 5.96 | -4.69 | 0.727 | 0.704 | 0.714 | 3.9 | -4.26 | 5.04 | Poor_Mixed | 5519.4 | 8740.8 | 1.524 | 0.785 | 6.67 | 0.727 | 5.96 | 0.4251 | 0.7666 | 0.4806 | 0.569 | 1 | 0.4072 | 0.4732 | 0.577 | 0.577 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
384 | 283.7 | 178.7 | 82.9 | 64.5 | 1 | 511.5 | 3423 | 52.6 | 28.8 | 79.1 | 75.7 | 72.8 | 84.6 | 37 | 13.9 | 7398.3 | 343.6 | 8130.1 | 13450.7 | 391.2 | 14341.8 | 1.818 | 1.139 | 1.764 | 0.923 | 0.922 | 0.98 | 8.66 | 8.86 | 9.58 | 0.534 | 0.519 | 0.531 | 2.51 | -3.08 | 2.85 | 0.53 | 0.515 | 0.545 | -3.01 | 2 | 2.74 | 0.546 | 0.5 | 0.505 | 2 | 2 | 2.12 | Critical_Winding_TD_Cap | 343.6 | 391.2 | 1.139 | 0.98 | 9.58 | 0.546 | 3.08 | 0.8975 | 0.8123 | 0.8747 | 0.9219 | 0.85 | 0.0869 | 0.8484 | 0.7563 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_TV_TanDelta_pct
385 | 299.7 | 221 | 79 | 90.6 | 3.4 | 519.4 | 3916.1 | 57.1 | 24.8 | 89.8 | 92.4 | 80.2 | 94.8 | 40.4 | 14.1 | 7989.6 | 7930.9 | 7874.5 | 13917.6 | 14121.3 | 14304 | 1.742 | 1.781 | 1.816 | 0.536 | 0.5 | 0.541 | 2.85 | 2.48 | -2.85 | 0.582 | 0.572 | 0.563 | 2.03 | 3.24 | 2.11 | 0.573 | 0.5 | 0.579 | 3.21 | -2.19 | -3.79 | 0.563 | 0.548 | 0.536 | 2.7 | 2.92 | 3.48 | Poor_Thermal | 7874.5 | 13917.6 | 1.742 | 0.541 | 2.85 | 0.582 | 3.79 | 0.7589 | 0.8734 | 0.5332 | 0.9169 | 1 | 0.8632 | 0.7524 | 0.81 | 0.81 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
386 | 1709.6 | 934.3 | 144.8 | 196.4 | 34.3 | 1224.3 | 7987.6 | 31.5 | 47.9 | 105.9 | 101.2 | 92.6 | 113.1 | 43.8 | 33.1 | 1303 | 1665.6 | 1523.1 | 1422.2 | 1928.6 | 1801.3 | 1.091 | 1.158 | 1.183 | 0.929 | 0.888 | 0.918 | -9.12 | 8.8 | 8.47 | 0.817 | 0.941 | 0.752 | 7.08 | 5.6 | 6.77 | 0.786 | 0.767 | 0.734 | -7.28 | -5.97 | -7.03 | 0.804 | 0.769 | 0.737 | 5.78 | -7 | -8.93 | Very Poor_Mixed | 1303 | 1422.2 | 1.091 | 0.929 | 9.12 | 0.941 | 8.93 | 0.0701 | 0.6025 | 0.1934 | 0.2787 | 1 | 0.1192 | 0.2843 | 0.351 | 0.351 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
387 | 815.7 | 426.8 | 94.2 | 95.9 | 9.5 | 582.5 | 4396.4 | 50.4 | 28.1 | 84.1 | 82.8 | 78.6 | 90 | 38.3 | 20.3 | 7072.7 | 7227.2 | 7729.2 | 11368.9 | 12245.1 | 13365.9 | 1.607 | 1.694 | 1.729 | 0.699 | 0.617 | 0.65 | 4.75 | -4.33 | 4.84 | 0.643 | 0.603 | 0.678 | 3.39 | 4.4 | 3.84 | 0.662 | 0.686 | 0.639 | 3.53 | 3.92 | -4.15 | 0.649 | 0.564 | 0.693 | 4.11 | 4.04 | 3.73 | Fair_Mixed | 7072.7 | 11368.9 | 1.607 | 0.699 | 4.84 | 0.693 | 4.4 | 0.5869 | 0.8221 | 0.688 | 0.7372 | 1 | 0.555 | 0.5528 | 0.6882 | 0.6882 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
388 | 1568.2 | 846 | 136.1 | 171.7 | 30.4 | 1174.6 | 7613.1 | 34.8 | 43.8 | 102.8 | 104 | 91.2 | 113 | 42.9 | 30.9 | 2845.3 | 2291.5 | 1962.8 | 3431.3 | 2772.5 | 2326.1 | 1.206 | 1.21 | 1.185 | 0.931 | 0.925 | 0.863 | 8.64 | -9.15 | 7.96 | 0.896 | 0.762 | 0.945 | 7.65 | -6.21 | 6.53 | 0.815 | 0.883 | 0.871 | 7.4 | 8.78 | 6.66 | 0.72 | 0.851 | 0.716 | 8.72 | -7.11 | 8.35 | Very Poor_Mixed | 1962.8 | 2326.1 | 1.185 | 0.931 | 9.15 | 0.945 | 8.78 | 0.1446 | 0.6415 | 0.2097 | 0.3635 | 1 | 0.134 | 0.2266 | 0.3718 | 0.3718 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
389 | 362.3 | 280.2 | 73.8 | 79.2 | 3.1 | 549.8 | 3484.4 | 55.2 | 23.9 | 81.7 | 80.8 | 75.9 | 86.5 | 37 | 12.2 | 775.2 | 845.5 | 690 | 790.7 | 910.6 | 716.3 | 1.02 | 1.077 | 1.038 | 0.735 | 0.747 | 0.702 | 5.89 | 6.37 | 5.68 | 0.575 | 0.58 | 1.295 | 3.47 | 3.65 | -3.81 | 0.603 | 0.664 | 0.615 | 3.21 | 4.64 | 3.34 | 0.615 | 0.586 | 0.638 | 3.39 | 3.68 | 3.66 | Critical_IR_PI | 690 | 716.3 | 1.02 | 0.747 | 6.37 | 1.295 | 4.64 | 0.7666 | 0.8894 | 0.7669 | 0.9618 | 0.775 | 0.4095 | 0.57 | 0.7071 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_HV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
390 | 391.7 | 161.1 | 68.3 | 77.2 | 1.6 | 486.6 | 3256.8 | 58.4 | 20 | 84 | 116.8 | 76.5 | 89.8 | 37.5 | 16.3 | 9097.1 | 7510.2 | 8464.7 | 16961.3 | 14413.1 | 14989.8 | 1.864 | 1.919 | 1.771 | 0.99 | 0.962 | 0.955 | 9.84 | -9.84 | 9.16 | 0.599 | 0.588 | 0.546 | 2.98 | 3.3 | 4.24 | 0.581 | 0.547 | 0.568 | 3.42 | 3.14 | -3.85 | 0.558 | 0.582 | 0.544 | 3.42 | -3.21 | 3.09 | Critical_Winding_TD_Cap | 7510.2 | 14413.1 | 1.771 | 0.99 | 9.84 | 0.599 | 4.24 | 0.8344 | 1 | 0.5402 | 0.8578 | 1 | 0.0394 | 0.6943 | 0.716 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | WTI_LV
391 | 251.2 | 179.2 | 79.6 | 140.6 | 2.7 | 475.7 | 2754.5 | 13.9 | 24 | 109.3 | 108.1 | 95.6 | 118.9 | 44.9 | 15.2 | 9280.9 | 9183.1 | 8745.2 | 17710.2 | 16907.9 | 16375.9 | 1.908 | 1.841 | 1.873 | 0.599 | 0.592 | 0.628 | -3.94 | 3.72 | 3.4 | 0.627 | 0.553 | 0.54 | 4 | 3.81 | 2.48 | 0.588 | 0.64 | 0.587 | 2.58 | -3.86 | 3.77 | 0.553 | 0.529 | 0.533 | 2.62 | 2.46 | 2.6 | Critical_Thermal | 8745.2 | 16375.9 | 1.841 | 0.628 | 3.94 | 0.64 | 4 | 0.7473 | 0.3042 | 0.0826 | 0.8882 | 1 | 0.6654 | 0.7058 | 0.6562 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
392 | 1580.5 | 849.3 | 135.2 | 162.4 | 33.5 | 1248.6 | 7516.2 | 34.4 | 44.2 | 105.4 | 105 | 93.3 | 116.1 | 43.1 | 32.4 | 2155.2 | 690 | 1204.2 | 2480.6 | 1200 | 1285.3 | 1.151 | 1.739 | 1.067 | 0.942 | 0.958 | 0.953 | 8.57 | -9.2 | 9.74 | 0.747 | 0.878 | 0.678 | -7.3 | -5.55 | 6.03 | 0.719 | 0.895 | 0.835 | -7.51 | 6.66 | 5.77 | 0.899 | 0.715 | 0.71 | 7.24 | 6.77 | -7.41 | Very Poor_Mixed | 690 | 1200 | 1.067 | 0.958 | 9.74 | 0.899 | 7.51 | 0.1312 | 0.6376 | 0.1607 | 0.3059 | 1 | 0.0736 | 0.295 | 0.3641 | 0.3641 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
393 | 346.8 | 235.9 | 83.6 | 80.3 | 3.1 | 531.7 | 3881.5 | 55.9 | 24 | 80.9 | 78.1 | 71.6 | 83.7 | 36 | 13.2 | 9374.5 | 9929.1 | 9306.2 | 18497.5 | 19438 | 17491.9 | 1.973 | 1.958 | 1.88 | 0.793 | 0.846 | 0.777 | 6.64 | 7.12 | 6.27 | 0.549 | 0.514 | 0.552 | 2.71 | -2.49 | 2.46 | 0.526 | 0.514 | 0.546 | 2.8 | 2.87 | 2.76 | 0.503 | 0.509 | 0.524 | 2.27 | 2.96 | 2.03 | Poor_Winding_TD_Cap | 9306.2 | 17491.9 | 1.88 | 0.846 | 7.12 | 0.552 | 2.96 | 0.7656 | 0.8875 | 0.8521 | 0.939 | 1 | 0.3079 | 0.8336 | 0.7832 | 0.7832 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
394 | 712.9 | 532 | 107.7 | 123.8 | 17.2 | 845.7 | 4767.1 | 48 | 31.8 | 87.8 | 87.7 | 80.5 | 94 | 38.6 | 23.7 | 5890.9 | 6327.5 | 5333.9 | 9423.2 | 9790.2 | 7840.4 | 1.6 | 1.547 | 1.47 | 0.758 | 0.72 | 0.685 | 6.17 | -4.81 | 4.89 | 0.638 | 0.606 | 0.604 | 4.1 | -2.74 | -3.6 | 0.609 | 0.631 | 0.58 | 3.65 | 4.29 | 3.14 | 0.6 | 0.574 | 0.532 | 4.56 | 2.96 | -3.15 | Poor_Mixed | 5333.9 | 7840.4 | 1.47 | 0.758 | 6.17 | 0.638 | 4.56 | 0.4494 | 0.7728 | 0.5912 | 0.6246 | 1 | 0.4548 | 0.6392 | 0.6342 | 0.6342 | Fair | 1 | 1 | DGA | 0 |  | C2H2
395 | 1748.6 | 951.1 | 146 | 193.1 | 33.2 | 1278.4 | 8383.5 | 36.4 | 43.9 | 105.5 | 108.2 | 93.2 | 118 | 45.3 | 32 | 1921.2 | 1775.5 | 1278.4 | 2164.6 | 1864.2 | 1368.7 | 1.127 | 1.05 | 1.071 | 0.891 | 0.983 | 0.956 | 8.12 | 9.43 | 9.47 | 0.905 | 0.862 | 0.735 | 7.32 | -9.62 | 6.16 | 0.762 | 0.951 | 0.749 | 9.54 | 8.9 | 7.24 | 0.839 | 0.887 | 0.969 | 9.15 | -6.9 | 8.9 | Very Poor_Mixed | 1278.4 | 1368.7 | 1.05 | 0.983 | 9.47 | 0.969 | 9.62 | 0.0609 | 0.6406 | 0.1177 | 0.3214 | 1 | 0.0875 | 0.1842 | 0.3253 | 0.3253 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
396 | 1687.3 | 958.1 | 139.9 | 185.4 | 34.3 | 1312.2 | 8974 | 32.6 | 48 | 108 | 107.8 | 93.4 | 116.5 | 44.5 | 36.6 | 1059.5 | 1688.9 | 690 | 1200 | 1985.7 | 1200 | 1.133 | 1.176 | 1.739 | 0.956 | 0.99 | 0.989 | 8.93 | -9.48 | -9.77 | 0.901 | 0.756 | 0.837 | 6.72 | 7.65 | 7.52 | 0.859 | 0.718 | 0.909 | 6.61 | 6.87 | 8.26 | 0.962 | 0.829 | 0.88 | -7.24 | 9.61 | 8.46 | Very Poor_Mixed | 690 | 1200 | 1.133 | 0.99 | 9.77 | 0.962 | 9.61 | 0.0592 | 0.6016 | 0.1184 | 0.1396 | 1 | 0.0443 | 0.2008 | 0.3082 | 0.3082 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
397 | 201.2 | 120 | 65.6 | 50 | 3.6 | 350 | 2619.7 | 53.9 | 27.3 | 82.1 | 80.7 | 75.5 | 88.2 | 37.4 | 12.1 | 8077.1 | 8763.1 | 8371.6 | 14670.1 | 5373.4 | 15130.2 | 1.816 | 0.613 | 1.807 | 0.962 | 0.906 | 0.924 | -9.67 | 8.8 | 9.2 | 0.613 | 0.576 | 0.571 | 2.46 | 2 | 2.79 | 0.534 | 0.573 | 0.564 | -2.9 | -3.72 | -2.88 | 0.5 | 0.546 | 0.541 | 2.51 | 2.5 | 2.37 | Critical_Winding_TD_Cap | 8077.1 | 5373.4 | 0.613 | 0.962 | 9.67 | 0.613 | 3.72 | 0.8861 | 0.8337 | 0.7568 | 0.964 | 0.8187 | 0.0847 | 0.761 | 0.7253 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_LV
398 | 234.2 | 120 | 72.1 | 94.9 | 3.8 | 504.7 | 2604.1 | 58.7 | 24.2 | 92.2 | 91 | 82.1 | 98.2 | 39.8 | 10 | 9481.4 | 8929.8 | 8847.9 | 18045.8 | 17268.8 | 17215.1 | 1.903 | 1.934 | 1.946 | 0.521 | 0.504 | 0.549 | 2 | -2.1 | -2.93 | 0.503 | 0.504 | 0.54 | 2.19 | 2.14 | -2 | 0.546 | 0.53 | 0.549 | 2.14 | 2.12 | 3.11 | 0.51 | 0.53 | 0.5 | 2.71 | 2.54 | 2 | Poor_Thermal | 8847.9 | 17215.1 | 1.903 | 0.549 | 2.93 | 0.549 | 3.11 | 0.7811 | 0.8839 | 0.5011 | 1 | 1 | 0.8906 | 0.8647 | 0.8418 | 0.8418 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
399 | 911.1 | 486.9 | 101.1 | 117.6 | 17.4 | 732.6 | 5339.5 | 48 | 31.9 | 87.7 | 86.5 | 79.8 | 95.4 | 39 | 24.9 | 5638.5 | 6562.2 | 6396 | 8560.2 | 10359.5 | 10036.7 | 1.518 | 1.579 | 1.569 | 0.719 | 0.687 | 0.661 | -5.65 | 4.86 | -4.94 | 0.701 | 0.681 | 0.682 | 3.61 | 5.38 | -3.97 | 0.604 | 0.671 | 0.593 | -4.56 | -3.81 | 4.27 | 0.594 | 0.714 | 0.63 | 4.64 | -5.52 | -3.29 | Poor_Mixed | 5638.5 | 8560.2 | 1.518 | 0.719 | 5.65 | 0.714 | 5.52 | 0.4569 | 0.7716 | 0.5954 | 0.5831 | 1 | 0.4917 | 0.5289 | 0.6195 | 0.6195 | Fair | 1 | 1 | DGA | 0 |  | C2H2
400 | 876.1 | 489.7 | 101.9 | 113 | 17.2 | 785.1 | 4633.5 | 47.2 | 31.5 | 86.9 | 87.4 | 80.5 | 94.9 | 39 | 23.5 | 6242.9 | 6761.4 | 6436 | 10114.7 | 11579.9 | 10574.2 | 1.62 | 1.713 | 1.643 | 0.68 | 0.728 | 0.728 | 5.25 | -5.51 | -5.96 | 0.652 | 0.609 | 0.558 | 5.37 | 4.32 | 4.05 | 0.6 | 0.617 | 0.66 | 4.06 | 5.36 | 4.72 | 0.68 | 0.682 | 0.645 | 4.06 | 3.24 | 5.31 | Poor_Mixed | 6242.9 | 10114.7 | 1.62 | 0.728 | 5.96 | 0.682 | 5.37 | 0.4647 | 0.7766 | 0.5926 | 0.6314 | 1 | 0.4464 | 0.5477 | 0.6213 | 0.6213 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
401 | 134.7 | 172.8 | 65 | 58 | 1 | 507.9 | 2826.9 | 47.4 | 31.8 | 77.3 | 81 | 70.1 | 80 | 35.1 | 12.5 | 8213.4 | 7961.2 | 7661.2 | 14026.8 | 14061.7 | 13798.6 | 1.708 | 1.766 | 1.801 | 0.552 | 0.552 | 0.588 | 2.49 | 2.86 | 3.77 | 0.529 | 0.555 | 0.5 | -2.53 | 2.74 | -2.08 | 0.509 | 0.556 | 0.543 | -2.76 | -2.29 | 2.33 | 0.533 | 0.513 | 0.517 | 2.74 | 2.34 | 2.3 | Fair_Oil | 7661.2 | 13798.6 | 1.708 | 0.588 | 3.77 | 0.556 | 2.76 | 0.9383 | 0.7728 | 0.8986 | 0.9552 | 1 | 0.7646 | 0.839 | 0.883 | 0.883 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
402 | 828.4 | 496.5 | 99.7 | 109.1 | 18.1 | 774.5 | 5389.7 | 45.8 | 35.8 | 91.8 | 93.4 | 83.2 | 97.8 | 39.9 | 24.9 | 6639.1 | 6193 | 5937.2 | 11482.9 | 10173.3 | 9406.5 | 1.73 | 1.643 | 1.584 | 0.751 | 0.776 | 0.711 | 6.18 | 5.38 | 5.16 | 0.586 | 0.712 | 0.713 | 4.02 | -5.2 | 4.47 | 0.647 | 0.678 | 0.698 | 4.78 | -3.83 | -5.32 | 0.709 | 0.688 | 0.734 | 4.72 | 5.59 | 4.43 | Poor_Mixed | 5937.2 | 9406.5 | 1.584 | 0.776 | 6.18 | 0.734 | 5.59 | 0.4615 | 0.7253 | 0.4827 | 0.5831 | 1 | 0.4167 | 0.4724 | 0.5832 | 0.5832 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
403 | 1407.1 | 851.7 | 134.7 | 180.3 | 29.4 | 1148.8 | 7908.4 | 26.9 | 45.8 | 101.5 | 100.3 | 91.3 | 107.7 | 42.8 | 35 | 2920.5 | 2561.9 | 2830.1 | 3489.7 | 3082.2 | 3569.2 | 1.195 | 1.203 | 1.261 | 0.931 | 0.901 | 0.886 | -8.96 | 8.88 | 8.5 | 0.676 | 0.675 | 0.772 | 7.33 | 6.6 | 7.18 | 0.764 | 0.712 | 0.86 | -7.75 | 4.89 | 7.25 | 0.762 | 0.712 | 0.67 | 7.84 | 6.57 | -7.66 | Critical_Mixed | 2561.9 | 3082.2 | 1.195 | 0.931 | 8.96 | 0.86 | 7.84 | 0.1533 | 0.0389 | 0.2649 | 0.2038 | 1 | 0.124 | 0.337 | 0.3177 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
404 | 1403.8 | 787.8 | 136.9 | 170.2 | 30.1 | 1228.3 | 7545.8 | 35.9 | 42.7 | 99.6 | 100 | 89.7 | 107.2 | 42.8 | 28.6 | 2526.3 | 983.4 | 2651.8 | 3012 | 1200 | 2991 | 1.192 | 1.22 | 1.128 | 0.906 | 0.985 | 0.99 | 8.94 | 9.27 | -9.84 | 0.851 | 0.797 | 0.761 | 5.98 | 6.66 | 7.51 | 0.838 | 0.834 | 0.826 | 7.95 | 7.53 | 8.46 | 0.699 | 0.847 | 0.738 | -6.7 | -7.95 | 6.18 | Very Poor_Mixed | 983.4 | 1200 | 1.128 | 0.99 | 9.84 | 0.851 | 8.46 | 0.1597 | 0.6524 | 0.2894 | 0.4498 | 1 | 0.0587 | 0.262 | 0.385 | 0.385 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
405 | 397.6 | 279.2 | 80.5 | 89.9 | 6.4 | 603.9 | 3965.4 | 56.1 | 24.3 | 82.1 | 81.5 | 76.2 | 85.3 | 36.5 | 14.7 | 8857.6 | 8204.1 | 8555.1 | 16040.2 | 14646.8 | 15504.9 | 1.811 | 1.785 | 1.812 | 0.636 | 0.63 | 0.684 | 3.6 | 4.22 | 4.18 | 0.555 | 0.59 | 0.54 | -2.87 | -2.37 | 2.82 | 0.574 | 0.577 | 0.585 | 3.31 | 3.54 | 2.55 | 0.576 | 0.537 | 0.579 | 3.9 | 2.45 | 3.34 | Fair_Mixed | 8204.1 | 14646.8 | 1.785 | 0.684 | 4.22 | 0.59 | 3.9 | 0.6871 | 0.8821 | 0.7642 | 0.9014 | 1 | 0.5979 | 0.7121 | 0.771 | 0.771 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
406 | 118.1 | 120 | 66.7 | 51.1 | 1 | 350 | 2500 | 60 | 20 | 75 | 78 | 70 | 80 | 35 | 12.1 | 8905.8 | 10000 | 9836.9 | 16918 | 20000 | 19133.7 | 1.9 | 2 | 1.945 | 0.501 | 0.53 | 0.508 | 2.24 | -2.46 | 2.98 | 0.5 | 0.502 | 0.5 | 2 | 2 | 2.4 | 0.5 | 0.5 | 0.508 | -2 | 2 | 2.22 | 0.541 | 0.507 | 0.5 | 2.94 | 2.31 | 2 | Good_Mixed | 8905.8 | 16918 | 1.9 | 0.53 | 2.98 | 0.541 | 2.94 | 0.9924 | 1 | 0.9604 | 0.964 | 1 | 0.9003 | 0.9478 | 0.969 | 0.969 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
407 | 530.2 | 303.1 | 89.2 | 87.4 | 4.8 | 620.4 | 4555 | 54.4 | 24.5 | 84.6 | 84.4 | 78.6 | 89.9 | 37.8 | 18.8 | 725.6 | 690 | 1510.1 | 740.2 | 704.1 | 1540.3 | 1.02 | 1.02 | 1.02 | 0.719 | 1.989 | 0.695 | 4.9 | 5.29 | -5.28 | 0.606 | 0.585 | 0.554 | 3.33 | -3.64 | -3.9 | 0.58 | 0.603 | 0.605 | 2.64 | -3.63 | 4.3 | 0.608 | 0.567 | 0.582 | -3.86 | 2.98 | -3.29 | Critical_IR_PI | 690 | 704.1 | 1.02 | 1.989 | 5.29 | 0.608 | 4.3 | 0.6828 | 0.8786 | 0.6755 | 0.7841 | 0.85 | 0.4005 | 0.6544 | 0.6927 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
408 | 1766 | 982.4 | 145.2 | 187.3 | 34.3 | 1290.8 | 9019.4 | 35 | 44.5 | 107.8 | 109 | 95.8 | 119.2 | 43.8 | 34 | 2396.6 | 1126 | 1721.9 | 2829.3 | 1212.2 | 1950.9 | 1.181 | 1.077 | 1.133 | 0.967 | 0.938 | 0.949 | 9.3 | 9.08 | 8.98 | 0.769 | 0.727 | 0.906 | 8.04 | -5.76 | 5.67 | 0.776 | 0.777 | 0.867 | 7.39 | 8.55 | -7.63 | 0.858 | 0.834 | 0.708 | 6.41 | 8.22 | 6.33 | Very Poor_Mixed | 1126 | 1212.2 | 1.077 | 0.967 | 9.3 | 0.906 | 8.55 | 0.047 | 0.6347 | 0.0913 | 0.2434 | 1 | 0.0758 | 0.2631 | 0.3272 | 0.3272 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
409 | 358.6 | 320.6 | 90.5 | 85.7 | 1 | 574.6 | 3860.7 | 34.8 | 66.3 | 83.2 | 80.8 | 77.8 | 89 | 36.3 | 15 | 4745.6 | 5002.8 | 5482.6 | 7207.1 | 7807.1 | 8322 | 1.519 | 1.561 | 1.518 | 0.693 | 0.628 | 0.667 | 5.01 | 4.07 | 4.46 | 0.594 | 0.644 | 0.552 | 3.41 | -3.61 | 3.7 | 0.637 | 0.549 | 0.587 | 3.64 | -3.69 | 2.56 | 0.581 | 0.586 | 0.593 | 3.34 | 2.37 | 4.07 | Critical_Oil | 4745.6 | 7207.1 | 1.518 | 0.693 | 5.01 | 0.644 | 4.07 | 0.8289 | 0.5833 | 0.7325 | 0.8935 | 1 | 0.5545 | 0.6565 | 0.751 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
410 | 1548.9 | 899.8 | 137.5 | 179.2 | 31.7 | 1169.7 | 7910.3 | 36.6 | 44.3 | 102.8 | 106 | 91.8 | 111.3 | 44.8 | 29.7 | 692.7 | 1602.6 | 1498.4 | 1200 | 1775.8 | 1577.1 | 1.732 | 1.108 | 1.053 | 0.889 | 0.927 | 0.946 | 8.48 | 8.73 | 8.94 | 0.892 | 0.729 | 0.842 | 7.55 | -8.29 | 6.47 | 0.891 | 0.802 | 0.889 | 8 | 7.71 | 7.69 | 0.86 | 0.867 | 0.76 | 5.09 | 7.25 | 8.81 | Very Poor_Mixed | 692.7 | 1200 | 1.053 | 0.946 | 8.94 | 0.892 | 8.81 | 0.1237 | 0.6367 | 0.19 | 0.4089 | 1 | 0.1171 | 0.2195 | 0.3627 | 0.3627 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
411 | 152.4 | 120 | 67.8 | 58 | 4 | 433.4 | 2500 | 57.2 | 21.3 | 76 | 78.1 | 70 | 80 | 36.1 | 12.6 | 9080.8 | 9146.9 | 9107.7 | 17119.1 | 18099.7 | 17448.8 | 1.885 | 1.979 | 1.916 | 0.544 | 0.551 | 0.574 | 2.48 | 2.88 | 3.12 | 0.5 | 0.5 | 0.5 | 2.44 | 2 | -2 | 0.5 | 0.556 | 0.526 | -2 | 2.03 | -2.17 | 0.5 | 0.514 | 0.546 | 2.28 | 2.33 | 2 | Good_Mixed | 9080.8 | 17119.1 | 1.885 | 0.574 | 3.12 | 0.556 | 2.44 | 0.848 | 0.9458 | 0.9377 | 0.953 | 1 | 0.7893 | 0.9195 | 0.9029 | 0.9029 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
412 | 920.8 | 556.2 | 103.8 | 126.1 | 17.2 | 890.4 | 6452.3 | 47.9 | 32.1 | 89.6 | 85.1 | 81.5 | 97 | 40.1 | 24.5 | 7374.3 | 5113.7 | 5683.7 | 12628.4 | 8177.6 | 9248.2 | 1.712 | 1.599 | 1.627 | 0.675 | 0.705 | 0.726 | 5.31 | 5.75 | -5.96 | 0.713 | 0.676 | 0.738 | 5.14 | -4.98 | 6.06 | 0.696 | 0.69 | 0.68 | -4.32 | -3.6 | 5.48 | 0.697 | 0.619 | 0.617 | 4.3 | -3.89 | -3.6 | Poor_Mixed | 5113.7 | 8177.6 | 1.599 | 0.726 | 5.96 | 0.738 | 6.06 | 0.4075 | 0.7691 | 0.5665 | 0.597 | 1 | 0.4499 | 0.4815 | 0.5903 | 0.5903 | Poor | 0 | 1 | DGA | 0 |  | C2H2
413 | 129.1 | 120 | 70.7 | 66.6 | 1.6 | 350 | 2500 | 58.6 | 23.2 | 76.2 | 76 | 71.3 | 81.2 | 35.9 | 10.1 | 9481.1 | 8945 | 9183.3 | 17394.7 | 16805.4 | 17746.9 | 1.835 | 1.879 | 1.933 | 0.574 | 0.536 | 0.541 | 3.15 | 2.34 | 2.63 | 0.581 | 0.549 | 0.529 | 2.83 | -2.73 | 2 | 0.641 | 0.558 | 0.519 | 4.87 | 2.07 | 2.57 | 0.549 | 0.515 | 0.516 | 2.35 | 3.02 | -2.7 | Fair_Bushing_TD_Cap | 8945 | 16805.4 | 1.835 | 0.574 | 3.15 | 0.641 | 4.87 | 0.9102 | 0.9027 | 0.9371 | 0.9992 | 1 | 0.8084 | 0.7697 | 0.8913 | 0.8913 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
414 | 782.4 | 484.6 | 102.4 | 110.3 | 16.4 | 715.3 | 5044.2 | 44 | 34.9 | 95.2 | 92.8 | 84.7 | 103.8 | 40.5 | 24.3 | 5406.9 | 6320.6 | 4920.9 | 7790.5 | 10021.6 | 7186 | 1.441 | 1.586 | 1.46 | 0.727 | 0.768 | 0.733 | -5.99 | 5.45 | 5.76 | 0.643 | 0.658 | 0.68 | 5.99 | 4.89 | 4.2 | 0.694 | 0.69 | 0.685 | -5.26 | -5.55 | 4.1 | 0.659 | 0.736 | 0.675 | 6.06 | 5.34 | 4.22 | Poor_Mixed | 4920.9 | 7186 | 1.441 | 0.768 | 5.99 | 0.736 | 6.06 | 0.4853 | 0.7356 | 0.4219 | 0.6039 | 1 | 0.4102 | 0.4631 | 0.5828 | 0.5828 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
415 | 152 | 120 | 69.7 | 57.1 | 2.2 | 453.3 | 2500 | 57.8 | 22.4 | 79.5 | 80.1 | 73.3 | 85.8 | 36.4 | 10.2 | 8853.5 | 7937.6 | 9424.3 | 16897.3 | 14897.3 | 18066 | 1.909 | 1.877 | 1.917 | 0.731 | 0.667 | 0.642 | 5.25 | 5.11 | 4.19 | 0.5 | 0.524 | 0.51 | 2 | 2 | 2.1 | 0.519 | 0.521 | 0.5 | -2.27 | -2.32 | -2 | 0.509 | 0.5 | 0.504 | 2.31 | 2.62 | 2.49 | Fair_Winding_TD_Cap | 7937.6 | 14897.3 | 1.877 | 0.731 | 5.25 | 0.524 | 2.62 | 0.8814 | 0.9193 | 0.8183 | 0.9981 | 1 | 0.5185 | 0.9197 | 0.8606 | 0.8606 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
416 | 430.2 | 309.7 | 86.7 | 82.2 | 2 | 519.2 | 4196.2 | 56.4 | 22 | 79.2 | 78.6 | 123.9 | 82.5 | 36.2 | 13.6 | 8378.3 | 8722.8 | 8143.3 | 14468.1 | 16225 | 14567 | 1.727 | 1.86 | 1.789 | 0.948 | 0.96 | 0.984 | -9.63 | 9.4 | 9.51 | 0.501 | 0.52 | 0.546 | 2.26 | -2.51 | 3.08 | 0.564 | 0.5 | 0.568 | 2.99 | 3.07 | 3.28 | 0.5 | 0.517 | 0.5 | 2.98 | 2.21 | -2 | Critical_Winding_TD_Cap | 8143.3 | 14468.1 | 1.727 | 0.984 | 9.63 | 0.568 | 3.28 | 0.7703 | 0.9283 | 0.6863 | 0.9294 | 1 | 0.0477 | 0.8589 | 0.7403 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Winding_TV_TanDelta_pct
417 | 194.7 | 211.9 | 65 | 58 | 2.9 | 383.1 | 2500 | 58.9 | 21.8 | 77.5 | 81 | 71.9 | 80.7 | 35.6 | 14.2 | 8249.5 | 9400.6 | 10000 | 16123.2 | 18801.3 | 20000 | 1.954 | 2 | 2 | 0.507 | 0.5 | 0.548 | 2 | 2.05 | -2.91 | 0.536 | 0.5 | 0.511 | 3.35 | -2.29 | 2.45 | 0.512 | 0.516 | 0.514 | 3 | 2 | 2.3 | 0.5 | 0.531 | 0.531 | -2 | 2.52 | 2.64 | Good_Mixed | 8249.5 | 16123.2 | 1.954 | 0.548 | 2.91 | 0.536 | 3.35 | 0.8623 | 0.9331 | 0.8713 | 0.9144 | 1 | 0.916 | 0.8753 | 0.9062 | 0.9062 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
418 | 240.5 | 137.2 | 67.1 | 55.8 | 1 | 398.6 | 2772.6 | 60 | 20.1 | 75.8 | 77.2 | 70 | 81.8 | 35.7 | 13.5 | 9502.8 | 10000 | 9800.4 | 18915.8 | 19887.3 | 19459 | 1.991 | 1.989 | 1.986 | 0.511 | 0.578 | 0.547 | 2.06 | 2.71 | 2.72 | 0.541 | 0.5 | 0.565 | 2.21 | 2 | 2 | 0.504 | 0.528 | 0.57 | 2 | -2.9 | -2.29 | 0.517 | 0.54 | 0.529 | 2.66 | -2.82 | 2.59 | Good_Mixed | 9502.8 | 18915.8 | 1.986 | 0.578 | 2.72 | 0.57 | 2.9 | 0.9531 | 0.9898 | 0.9424 | 0.9318 | 1 | 0.838 | 0.8355 | 0.9256 | 0.9256 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
419 | 383.9 | 218.9 | 72.6 | 77 | 4.7 | 555.3 | 3013.5 | 54.6 | 24.3 | 81.4 | 79.6 | 77.4 | 90.3 | 36.8 | 15.8 | 8426 | 8450.5 | 8510.8 | 15498.1 | 15917.9 | 15575.9 | 1.839 | 1.884 | 1.83 | 0.586 | 0.543 | 0.599 | 3.51 | 2.72 | 3.54 | 0.566 | 0.579 | 0.601 | 3.91 | 2.05 | -3.56 | 0.627 | 0.607 | 0.564 | -2.9 | -3.4 | 3.5 | 0.615 | 0.539 | 0.571 | 3.42 | -3.09 | 3.01 | Fair_Mixed | 8426 | 15498.1 | 1.83 | 0.599 | 3.54 | 0.627 | 3.91 | 0.7509 | 0.8821 | 0.7509 | 0.8718 | 1 | 0.7337 | 0.6741 | 0.7963 | 0.7963 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
420 | 859.7 | 507.2 | 102.3 | 124 | 18.7 | 771.6 | 5307.3 | 54.5 | 22.2 | 76.4 | 77.5 | 71.7 | 81.1 | 35 | 10.7 | 9492.8 | 9031.5 | 9316.9 | 18597.1 | 16951 | 18633.9 | 1.959 | 1.877 | 2 | 0.565 | 0.5 | 0.587 | 2.81 | 2.54 | 3.1 | 0.521 | 0.527 | 0.529 | 2.09 | 2.14 | 3.14 | 0.535 | 0.555 | 0.538 | -2.59 | -2.5 | 2 | 0.538 | 0.529 | 0.539 | 2.96 | 2.09 | 2 | Fair_DGA | 9031.5 | 16951 | 1.877 | 0.587 | 3.1 | 0.555 | 3.14 | 0.4389 | 0.9238 | 0.9175 | 0.9909 | 1 | 0.8186 | 0.8163 | 0.7834 | 0.7834 | Fair | 1 | 1 | DGA | 0 |  | C2H2
421 | 1334.9 | 833.3 | 118.8 | 156.3 | 26.1 | 1145.7 | 7706.1 | 35 | 44.8 | 102.6 | 98.3 | 93 | 112 | 42.2 | 31.4 | 3042.9 | 3292.1 | 2381.9 | 3790.8 | 4137.2 | 2890.3 | 1.246 | 1.257 | 1.213 | 0.893 | 0.943 | 0.859 | 8.64 | -9.28 | 8.36 | 0.852 | 0.775 | 0.842 | 7.15 | -7.96 | 6.73 | 0.868 | 0.84 | 0.732 | -8.89 | 5.03 | -4.98 | 0.691 | 0.722 | 0.859 | 5.7 | 7.61 | 7.02 | Very Poor_Mixed | 2381.9 | 2890.3 | 1.213 | 0.943 | 9.28 | 0.868 | 8.89 | 0.2122 | 0.6318 | 0.2434 | 0.3444 | 1 | 0.1307 | 0.279 | 0.399 | 0.399 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
422 | 260.3 | 182 | 72.4 | 66 | 1.9 | 478.7 | 2872.1 | 16.5 | 25.1 | 79.5 | 79.8 | 72.6 | 86.9 | 36.3 | 19.9 | 8942.6 | 8814.9 | 9449.7 | 16115.7 | 16482.2 | 17715.5 | 1.802 | 1.87 | 1.875 | 0.873 | 0.956 | 0.889 | 8.19 | 8.93 | 8.42 | 0.604 | 0.552 | 0.587 | -2.86 | 2.14 | 2 | 0.574 | 0.559 | 0.544 | 3.31 | 2.34 | 2.79 | 0.555 | 0.534 | 0.5 | 2.76 | 2.89 | -2.56 | Critical_Winding_TD_Cap | 8814.9 | 16115.7 | 1.802 | 0.956 | 8.93 | 0.604 | 3.31 | 0.8497 | 0.285 | 0.8219 | 0.7499 | 1 | 0.1379 | 0.7652 | 0.6833 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
423 | 1138.3 | 599 | 109 | 110.9 | 15.7 | 847.2 | 5705.1 | 58.5 | 22.1 | 78.8 | 79 | 72.7 | 84.3 | 37.1 | 12.1 | 8952.9 | 9235.4 | 9919.9 | 17604.8 | 17356.3 | 19830 | 1.966 | 1.879 | 1.999 | 0.51 | 0.523 | 0.5 | 3.07 | 2.1 | 2.2 | 0.528 | 0.513 | 0.56 | 2.46 | 2.03 | 2.44 | 0.5 | 0.5 | 0.582 | 2 | -2.43 | 2 | 0.52 | 0.527 | 0.504 | 2.18 | 2.23 | 2.27 | Fair_DGA | 8952.9 | 17356.3 | 1.879 | 0.523 | 3.07 | 0.582 | 2.46 | 0.4205 | 0.926 | 0.8435 | 0.964 | 1 | 0.9163 | 0.8702 | 0.7937 | 0.7937 | Fair | 1 | 1 | DGA | 0 |  | C2H2
424 | 151.8 | 120 | 69.3 | 50.4 | 3.8 | 398.8 | 3251.4 | 59.9 | 20 | 75 | 75 | 70.2 | 80 | 35 | 10 | 9160.3 | 8445.9 | 9078.2 | 17816.7 | 16107.2 | 17715.7 | 1.945 | 1.907 | 1.951 | 0.552 | 0.547 | 0.562 | -3.06 | 2.85 | 3.14 | 0.513 | 0.52 | 0.5 | 2.22 | 2.04 | 2.2 | 0.511 | 0.5 | 0.5 | 2 | 2.05 | 2 | 0.527 | 0.515 | 0.55 | 2.24 | 2 | 2 | Good_Mixed | 8445.9 | 16107.2 | 1.907 | 0.562 | 3.14 | 0.55 | 2.24 | 0.8693 | 1 | 0.9964 | 1 | 1 | 0.7795 | 0.9112 | 0.9201 | 0.9201 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
425 | 184.7 | 183.4 | 77.6 | 55.5 | 4.1 | 446.5 | 3378.4 | 58.8 | 23.3 | 78.7 | 79.3 | 70.7 | 80.2 | 35 | 13.4 | 9023.4 | 9319.4 | 8991.1 | 17465.4 | 18362.1 | 17463.3 | 1.936 | 1.97 | 1.942 | 0.561 | 0.595 | 0.573 | 3.4 | 3.22 | 3.85 | 0.523 | 0.573 | 0.5 | -2.79 | 2 | 2.16 | 0.501 | 0.573 | 0.525 | 2.25 | -2.26 | -3.43 | 0.525 | 0.571 | 0.526 | 2.97 | 2.71 | -2.3 | Good_Mixed | 8991.1 | 17463.3 | 1.936 | 0.595 | 3.85 | 0.573 | 3.43 | 0.8267 | 0.9008 | 0.8909 | 0.9342 | 1 | 0.7162 | 0.8246 | 0.8593 | 0.8593 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
426 | 1629 | 852.5 | 129.9 | 169.3 | 73.9 | 1154.3 | 7794.3 | 55.3 | 25.7 | 77.9 | 80.8 | 75.8 | 89.7 | 35.5 | 12.8 | 9064.8 | 8105.6 | 9335.5 | 17540.8 | 15058.6 | 18045.7 | 1.935 | 1.858 | 1.933 | 0.526 | 0.606 | 0.518 | 2 | 3.49 | 2.12 | 0.575 | 0.552 | 0.661 | -2.66 | -3.6 | 3.21 | 0.608 | 0.622 | 0.605 | -3.48 | 3.19 | 2.42 | 0.593 | 0.592 | 0.582 | 2.93 | 2.72 | 3.06 | Critical_DGA | 8105.6 | 15058.6 | 1.858 | 0.606 | 3.49 | 0.661 | 3.6 | 0.1262 | 0.8584 | 0.7926 | 0.9484 | 1 | 0.8335 | 0.6584 | 0.6565 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
427 | 740.7 | 411 | 100.1 | 120 | 16 | 761.5 | 5280.4 | 45.9 | 34.7 | 90.1 | 89.5 | 81.6 | 97 | 40 | 24.8 | 6202 | 5601 | 6480 | 9720.8 | 8577.7 | 10609.9 | 1.567 | 1.531 | 1.637 | 0.663 | 0.744 | 0.699 | 5.16 | -5.6 | 5.36 | 0.741 | 0.754 | 0.678 | -5.47 | 5.75 | 5.32 | 0.708 | 0.813 | 0.694 | 6.18 | 4.88 | -4.66 | 0.601 | 0.675 | 0.745 | 6.59 | 5.36 | -3.95 | Poor_Mixed | 5601 | 8577.7 | 1.531 | 0.744 | 5.6 | 0.813 | 6.59 | 0.4834 | 0.7379 | 0.5325 | 0.5865 | 1 | 0.4672 | 0.4185 | 0.5927 | 0.5927 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
428 | 883.6 | 498.9 | 108.2 | 110.8 | 17.7 | 808.8 | 5282.2 | 46.7 | 33.6 | 89.2 | 87.9 | 79.7 | 95.6 | 38.9 | 23.5 | 5987.1 | 5715.7 | 5562.1 | 9857.5 | 8547.6 | 8546.8 | 1.646 | 1.495 | 1.537 | 0.725 | 0.688 | 0.661 | 4.55 | 5.31 | 4.57 | 0.656 | 0.584 | 0.714 | 5.57 | 3.24 | -4.15 | 0.6 | 0.599 | 0.678 | 3.98 | 3.03 | -3.88 | 0.653 | 0.563 | 0.656 | 4.38 | 4.95 | 4.18 | Poor_Mixed | 5562.1 | 8546.8 | 1.495 | 0.725 | 5.31 | 0.714 | 5.57 | 0.4482 | 0.7509 | 0.5757 | 0.6314 | 1 | 0.509 | 0.5627 | 0.6239 | 0.6239 | Fair | 1 | 1 | DGA | 0 |  | C2H2
429 | 121.1 | 167.4 | 65 | 50 | 1.4 | 350 | 2500 | 56.1 | 21.7 | 75 | 75 | 70 | 81.8 | 36.1 | 11.8 | 9138.1 | 9496.2 | 10000 | 18126.7 | 18946.1 | 19699.2 | 1.984 | 1.995 | 1.97 | 0.553 | 0.528 | 0.5 | -2.81 | 3.16 | 2 | 0.515 | 0.5 | 0.513 | 2.41 | 2.3 | 2.4 | 0.544 | 0.539 | 0.501 | 2.17 | 2.27 | -2.28 | 0.512 | 0.518 | 0.5 | 2.57 | 2.51 | 2 | Good_Mixed | 9138.1 | 18126.7 | 1.97 | 0.553 | 3.16 | 0.544 | 2.57 | 0.9471 | 0.9355 | 0.9867 | 0.9703 | 1 | 0.8698 | 0.8914 | 0.9384 | 0.9384 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
430 | 1007.8 | 523.7 | 106.1 | 119.5 | 18.2 | 852.6 | 5690.2 | 46 | 34.2 | 90.3 | 87.3 | 81.1 | 96.7 | 39.8 | 23.7 | 6796.1 | 7418.4 | 5863.2 | 10944.9 | 12852.3 | 8863.6 | 1.61 | 1.732 | 1.512 | 0.704 | 0.709 | 0.702 | 5.83 | -5.97 | 4.68 | 0.609 | 0.658 | 0.615 | 5.92 | 4.07 | 4.69 | 0.727 | 0.677 | 0.713 | -3.19 | 5.52 | -3.7 | 0.701 | 0.682 | 0.743 | -4.22 | 4.07 | -4.88 | Poor_Mixed | 5863.2 | 8863.6 | 1.512 | 0.709 | 5.97 | 0.743 | 5.92 | 0.4159 | 0.7438 | 0.5522 | 0.6246 | 1 | 0.4571 | 0.4872 | 0.5914 | 0.5914 | Poor | 0 | 1 | DGA | 0 |  | C2H2
431 | 1447 | 886.2 | 134 | 176.9 | 30.8 | 1229.5 | 7712.2 | 36.3 | 45.3 | 103.2 | 100 | 91.1 | 111.4 | 43.3 | 30.1 | 2242.8 | 999.1 | 2020.6 | 2757.1 | 1200 | 2434.6 | 1.229 | 1.201 | 1.205 | 0.938 | 0.895 | 0.879 | 8.94 | 8.35 | -7.73 | 0.85 | 0.724 | 0.831 | 7.91 | 6.37 | 8.94 | 0.768 | 0.79 | 0.88 | 8.3 | 6.23 | -7.81 | 0.753 | 0.901 | 0.757 | -7.82 | 8.37 | 5.25 | Very Poor_Mixed | 999.1 | 1200 | 1.201 | 0.938 | 8.94 | 0.901 | 8.94 | 0.1371 | 0.627 | 0.2361 | 0.3938 | 1 | 0.148 | 0.2484 | 0.3782 | 0.3782 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
432 | 1630 | 982.4 | 138.5 | 196.1 | 34.3 | 1325.8 | 8437.1 | 50.3 | 29 | 81.1 | 79.3 | 75.6 | 86.3 | 35.1 | 21.3 | 8705.8 | 7483.2 | 8062.3 | 15816.6 | 12735.3 | 14663.9 | 1.817 | 1.702 | 1.819 | 0.542 | 0.582 | 0.572 | -10.79 | -3.09 | 3.05 | 0.609 | 0.615 | 0.605 | 3.85 | 3.11 | 4.06 | 0.589 | 0.604 | 0.618 | 3.67 | 3.56 | 3.77 | 0.615 | 0.571 | 0.601 | -3.63 | 4.12 | -3.7 | Critical_DGA | 7483.2 | 12735.3 | 1.702 | 0.582 | 10.79 | 0.618 | 4.12 | 0.0589 | 0.8095 | 0.7967 | 0.7049 | 1 | 0.6327 | 0.6197 | 0.5869 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
433 | 686.2 | 499.6 | 95.2 | 114.6 | 16.3 | 849.4 | 5357.4 | 49.9 | 30.8 | 85.5 | 89.8 | 78.8 | 94.4 | 39.5 | 24.2 | 6867.6 | 6563.5 | 6359.7 | 10727.4 | 9969.9 | 10233 | 1.562 | 1.519 | 1.609 | 0.764 | 0.652 | 0.775 | 6.03 | -5.03 | 5.95 | 0.571 | 0.678 | 0.688 | 5.45 | 5.86 | 3.97 | 0.692 | 0.611 | 0.606 | 5.46 | 5.17 | -5.01 | 0.641 | 0.728 | 0.62 | 3.96 | -6.14 | 4.32 | Poor_Mixed | 6359.7 | 9969.9 | 1.519 | 0.775 | 6.03 | 0.728 | 6.14 | 0.4727 | 0.7855 | 0.597 | 0.6074 | 1 | 0.427 | 0.5086 | 0.6138 | 0.6138 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
434 | 714.5 | 512.3 | 100 | 103.3 | 16.5 | 772.9 | 4748.4 | 55.4 | 24.3 | 80.4 | 79.5 | 74.9 | 87.7 | 36.5 | 14.2 | 8452.6 | 9007.5 | 9433.3 | 15476.5 | 16894.4 | 17933.5 | 1.831 | 1.876 | 1.901 | 0.523 | 0.52 | 0.516 | 2.62 | 2.85 | 2 | 0.522 | 0.578 | 0.533 | -2.67 | 2.48 | 2.44 | 0.569 | 0.51 | 0.506 | 2.74 | -3.06 | 2.48 | 0.516 | 0.5 | 0.55 | 2.56 | 3.57 | 3.04 | Poor_DGA | 8452.6 | 15476.5 | 1.831 | 0.523 | 2.85 | 0.578 | 3.57 | 0.4913 | 0.8821 | 0.793 | 0.9144 | 1 | 0.8827 | 0.8189 | 0.7847 | 0.7847 | Fair | 1 | 1 | DGA | 0 |  | C2H2
435 | 1031.3 | 503.9 | 105 | 111.2 | 20.3 | 872.7 | 5838.8 | 47.1 | 33.1 | 91.1 | 91.6 | 82.9 | 99.6 | 39.6 | 23.2 | 4999.4 | 5030.3 | 6464.7 | 7446.2 | 7515.1 | 10268.8 | 1.489 | 1.494 | 1.588 | 0.763 | 0.726 | 0.716 | 6.15 | -5.96 | 5.72 | 0.663 | 0.668 | 0.738 | -3.78 | 5.06 | 4.98 | 0.684 | 0.653 | 0.733 | 4.94 | 4.04 | 5.17 | 0.607 | 0.661 | 0.627 | -4.76 | 5 | 4.38 | Poor_Mixed | 4999.4 | 7446.2 | 1.489 | 0.763 | 6.15 | 0.738 | 5.17 | 0.4087 | 0.7568 | 0.4935 | 0.6416 | 1 | 0.4053 | 0.4908 | 0.5795 | 0.5795 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
436 | 1553.7 | 865.1 | 139.7 | 188.1 | 32.8 | 1267.5 | 7970.5 | 32 | 48.3 | 109.3 | 104.9 | 95.2 | 119.2 | 44.9 | 33.4 | 1387.6 | 1069 | 1375.6 | 1543.5 | 1200 | 1514.3 | 1.112 | 1.123 | 1.101 | 0.969 | 0.944 | 0.959 | 8.47 | 8.82 | -8.92 | 0.831 | 0.949 | 0.734 | 7.14 | 7.99 | 7.06 | 0.96 | 0.967 | 0.788 | 8.23 | 6.07 | 6.82 | 0.879 | 0.736 | 0.842 | 8.82 | 7.34 | 6.58 | Very Poor_Mixed | 1069 | 1200 | 1.101 | 0.969 | 8.92 | 0.967 | 8.82 | 0.1015 | 0.5988 | 0.1009 | 0.267 | 1 | 0.0911 | 0.2088 | 0.331 | 0.331 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
437 | 1101.8 | 523.4 | 101.8 | 120.3 | 16 | 801 | 5304.4 | 45.9 | 36.5 | 90.9 | 91.1 | 83 | 98.7 | 40.4 | 27 | 5303.4 | 6142.4 | 4989.7 | 8028.3 | 9565.3 | 7685.8 | 1.514 | 1.557 | 1.54 | 0.721 | 0.723 | 0.723 | 5.47 | 5.24 | -5.29 | 0.665 | 0.73 | 0.681 | 5.93 | -4.22 | 4.71 | 0.683 | 0.65 | 0.7 | 4.8 | 4.89 | 3.86 | 0.689 | 0.657 | 0.616 | 4.63 | 3.79 | 4.99 | Poor_Mixed | 4989.7 | 7685.8 | 1.514 | 0.723 | 5.47 | 0.73 | 5.93 | 0.4357 | 0.7175 | 0.4967 | 0.5083 | 1 | 0.45 | 0.4859 | 0.5806 | 0.5806 | Poor | 0 | 1 | DGA | 0 |  | C2H2
438 | 1513.3 | 870.1 | 134.2 | 169.6 | 27 | 1191.5 | 7808 | 30.6 | 47.4 | 106.1 | 108.3 | 92.7 | 115.1 | 44.7 | 31.7 | 2762.7 | 3332.6 | 3262 | 3410.2 | 4304.2 | 4424.2 | 1.234 | 1.292 | 1.356 | 0.93 | 0.931 | 0.897 | -8.77 | 8.78 | 8.77 | 0.856 | 0.822 | 0.915 | 7.43 | 7.22 | 8.84 | 0.716 | 0.824 | 0.738 | 6.71 | 6.94 | 7.14 | 0.816 | 0.823 | 0.872 | -6.16 | -8.12 | 5.94 | Very Poor_Mixed | 2762.7 | 3410.2 | 1.234 | 0.931 | 8.78 | 0.915 | 8.84 | 0.161 | 0.6072 | 0.1356 | 0.3329 | 1 | 0.115 | 0.2435 | 0.3633 | 0.3633 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
439 | 122.7 | 128.7 | 67.8 | 59.3 | 1.1 | 374.5 | 2500 | 57.7 | 21.4 | 78 | 77.3 | 71.9 | 82.6 | 36.5 | 12.3 | 9227.1 | 9097 | 8559.9 | 18018.2 | 17565.6 | 15290.9 | 1.953 | 1.931 | 1.786 | 0.543 | 0.5 | 0.5 | 2.35 | -2 | 2.05 | 0.5 | 0.504 | 0.507 | 2 | -2 | 2.32 | 0.516 | 0.508 | 0.508 | 2.09 | 2.98 | 2.15 | 0.5 | 0.557 | 0.538 | -2.17 | -2.38 | -2.42 | Good_Mixed | 8559.9 | 15290.9 | 1.786 | 0.543 | 2.35 | 0.557 | 2.98 | 0.944 | 0.9432 | 0.8866 | 0.9597 | 1 | 0.9461 | 0.8983 | 0.94 | 0.94 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
440 | 525.9 | 257.7 | 90 | 141.9 | 1.5 | 533.7 | 4129.2 | 55.6 | 23.5 | 107.6 | 107.7 | 95.2 | 117 | 45.5 | 14.8 | 8387.7 | 8019.3 | 6884.2 | 14466.4 | 14094.4 | 12609.1 | 1.725 | 1.758 | 1.832 | 0.58 | 0.517 | 0.548 | -2.83 | -11.75 | -3.21 | 0.584 | 0.617 | 0.572 | 3 | -3.44 | 3.46 | 0.645 | 0.574 | 0.575 | 2.8 | 2.58 | 3.65 | 0.585 | 0.56 | 0.559 | 3.51 | -3.25 | 3.49 | Critical_Thermal | 6884.2 | 12609.1 | 1.725 | 0.58 | 11.75 | 0.645 | 3.65 | 0.7214 | 0.8969 | 0.1013 | 0.8988 | 1 | 0.6649 | 0.6704 | 0.7168 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H4
441 | 376.8 | 155.8 | 73.4 | 52.8 | 1 | 350 | 2900.8 | 58 | 24.2 | 81 | 79.1 | 73.8 | 84.4 | 36.6 | 13.8 | 9025.6 | 9980.9 | 9381 | 16910.3 | 19361.7 | 17964 | 1.874 | 1.94 | 1.915 | 0.72 | 0.724 | 0.689 | -5.26 | 5.83 | 5.23 | 0.558 | 0.524 | 0.566 | 2 | 2.12 | 2 | 0.508 | 0.505 | 0.514 | 2.25 | 2.43 | -2.44 | 0.589 | 0.537 | 0.5 | -2.46 | 3.34 | -2.18 | Fair_Winding_TD_Cap | 9025.6 | 16910.3 | 1.874 | 0.724 | 5.83 | 0.589 | 3.34 | 0.9515 | 0.8839 | 0.8162 | 0.9244 | 1 | 0.4545 | 0.8396 | 0.8465 | 0.8465 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
442 | 784 | 491.7 | 105.4 | 109.7 | 15 | 704.2 | 4900.4 | 47.2 | 32.9 | 89 | 87.4 | 81.4 | 99.5 | 39.6 | 25.4 | 5903.9 | 6768.3 | 6590.2 | 9172.7 | 10909.6 | 10458.7 | 1.554 | 1.612 | 1.587 | 0.787 | 0.772 | 0.776 | 5.89 | -6.17 | -6.37 | 0.626 | 0.667 | 0.709 | 6.1 | -3.97 | 4.22 | 0.67 | 0.717 | 0.671 | 4.8 | 3.37 | 5.51 | 0.712 | 0.627 | 0.694 | 4.9 | 3.65 | -4.26 | Poor_Mixed | 5903.9 | 9172.7 | 1.554 | 0.787 | 6.37 | 0.717 | 6.1 | 0.4951 | 0.7593 | 0.5455 | 0.5655 | 1 | 0.3577 | 0.4879 | 0.5956 | 0.5956 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
443 | 817 | 450.8 | 98.7 | 116.9 | 18 | 874.3 | 5668.9 | 45.6 | 35.1 | 94.6 | 95.9 | 84.3 | 101 | 41.2 | 26.1 | 4552 | 5478.3 | 5012.7 | 6568.3 | 8307.1 | 7466 | 1.443 | 1.516 | 1.489 | 0.735 | 0.741 | 0.663 | 6.24 | 5.85 | 5.13 | 0.648 | 0.73 | 0.704 | 5.97 | 5.75 | 4.43 | 0.692 | 0.683 | 0.68 | 4.84 | 5.52 | 3.54 | 0.69 | 0.718 | 0.729 | 4.5 | 5.97 | 5.92 | Poor_Mixed | 4552 | 6568.3 | 1.443 | 0.741 | 6.24 | 0.73 | 5.97 | 0.4457 | 0.7333 | 0.4181 | 0.5407 | 1 | 0.437 | 0.4395 | 0.5686 | 0.5686 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
444 | 1669.5 | 971.3 | 148.3 | 192.1 | 32.7 | 1379 | 8664.7 | 15.2 | 29 | 81.1 | 83.4 | 72.3 | 86.9 | 37.6 | 10.9 | 8964.4 | 9408.8 | 8856 | 16833.2 | 18684.9 | 16298.8 | 1.878 | 1.986 | 1.84 | 0.544 | 0.524 | 0.589 | 2.5 | -2.02 | 2.62 | 0.619 | 0.641 | 0.611 | 4.78 | 3.55 | 2.93 | 0.602 | 0.588 | 0.581 | 3.96 | 3.22 | 3.7 | 0.607 | 0.61 | 0.604 | 4.86 | 4.04 | 3.25 | Critical_DGA | 8856 | 16298.8 | 1.84 | 0.589 | 2.62 | 0.641 | 4.86 | 0.0508 | 0.2262 | 0.7745 | 0.9875 | 1 | 0.833 | 0.6106 | 0.5532 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
445 | 336.4 | 237.5 | 74.9 | 69.7 | 77.7 | 418.6 | 3002.7 | 57.3 | 22 | 78.6 | 81.4 | 73.8 | 85.4 | 37.1 | 13.1 | 8253 | 9115.3 | 7693.3 | 14913.7 | 16943.4 | 13617.9 | 1.807 | 1.859 | 1.77 | 0.626 | 0.566 | 0.604 | 2.63 | 3.8 | 3.51 | 0.541 | 0.6 | 0.529 | 3.92 | -3.07 | 2.73 | 0.974 | 0.577 | 0.511 | 9.15 | 3.61 | 2.7 | 0.562 | 0.575 | 0.536 | 2 | 3.08 | -2.75 | Critical_Bushing_TD_Cap | 7693.3 | 13617.9 | 1.77 | 0.626 | 3.8 | 0.974 | 9.15 | 0.5812 | 0.9283 | 0.8099 | 0.9414 | 1 | 0.7004 | 0.6704 | 0.7635 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
446 | 244.1 | 221.6 | 65 | 66.9 | 1.9 | 407 | 2968.4 | 55.5 | 24.3 | 75.7 | 76.1 | 74.2 | 81.6 | 35.9 | 13.7 | 9421 | 8390.8 | 9088.3 | 18791.5 | 15896.1 | 17076.9 | 1.995 | 1.894 | 1.879 | 0.692 | 0.697 | 0.705 | -4.95 | -5.08 | 5.81 | 0.508 | 0.537 | 0.546 | 2 | 2.94 | 2.62 | 0.531 | 0.539 | 0.554 | -2.04 | 2.55 | -2.73 | 0.539 | 0.59 | 0.564 | -2.75 | 2.21 | 2.47 | Poor_Winding_TD_Cap | 8390.8 | 15896.1 | 1.879 | 0.705 | 5.81 | 0.59 | 2.94 | 0.8609 | 0.8821 | 0.9151 | 0.9269 | 1 | 0.4753 | 0.7892 | 0.8275 | 0.8275 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
447 | 898.4 | 462.9 | 106.1 | 134.4 | 21.1 | 907.6 | 6128.3 | 59.5 | 22.9 | 76.4 | 77.1 | 71.4 | 83.8 | 36.4 | 15.8 | 8104.5 | 6982.7 | 7622.8 | 15247.3 | 12163.6 | 13099.7 | 1.881 | 1.742 | 1.718 | 0.579 | 0.582 | 0.585 | -3.4 | -3.14 | 2.71 | 0.548 | 0.585 | 0.575 | -2.74 | 3.15 | 2.99 | 0.535 | 0.502 | 0.58 | 3.21 | 2.27 | 2.58 | 0.596 | 0.585 | 0.614 | 2.84 | -3.13 | 3.53 | Poor_DGA | 6982.7 | 12163.6 | 1.718 | 0.585 | 3.4 | 0.614 | 3.53 | 0.3886 | 0.9088 | 0.9053 | 0.8718 | 1 | 0.7345 | 0.7232 | 0.7333 | 0.7333 | Fair | 1 | 1 | DGA | 0 |  | C2H2
448 | 1417.7 | 833 | 126.8 | 162.1 | 27.2 | 1123.1 | 7232.5 | 38.9 | 40.5 | 101.7 | 102.3 | 90.3 | 111.7 | 42.3 | 34.3 | 3063 | 2655.1 | 2214.8 | 3778.7 | 3270.5 | 1924.5 | 1.234 | 1.232 | 0.869 | 0.794 | 0.831 | 0.829 | 7.18 | -7.45 | -7.8 | 0.787 | 0.837 | 0.764 | 5.04 | 5.77 | 6.58 | 0.752 | 0.785 | 0.732 | 8.07 | 6.26 | 7.31 | 0.802 | 0.791 | 0.713 | 6.86 | 7.7 | 7.03 | Critical_Mixed | 2214.8 | 1924.5 | 0.869 | 0.831 | 7.8 | 0.837 | 8.07 | 0.198 | 0.6747 | 0.2415 | 0.2316 | 0.8125 | 0.2554 | 0.3019 | 0.3863 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
449 | 632 | 444.1 | 89.8 | 134.1 | 2.4 | 638.4 | 4689.7 | 57.6 | 23.6 | 105.6 | 107 | 95.1 | 116.5 | 45.8 | 18.8 | 9789.5 | 9248.3 | 9313.9 | 18416 | 18029.3 | 17217.8 | 1.881 | 1.949 | 1.849 | 0.5 | 0.545 | 0.56 | 2.08 | 3.05 | 3.25 | 0.56 | 0.586 | 2.202 | 3.3 | 3.68 | 4.35 | 0.541 | 0.559 | 0.555 | 2.99 | 3.17 | -3.22 | 0.583 | 0.527 | 0.566 | -3.1 | 2.48 | -3 | Critical_Thermal | 9248.3 | 17217.8 | 1.849 | 0.56 | 3.25 | 2.202 | 4.35 | 0.6498 | 0.895 | 0.1169 | 0.7841 | 1 | 0.8453 | 0.6642 | 0.7186 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H4
450 | 119.5 | 152.3 | 65 | 93.4 | 2.7 | 387.3 | 2737.1 | 59.2 | 20.2 | 88 | 85 | 78.3 | 95 | 38.6 | 10 | 8093.1 | 9309.8 | 9365.9 | 15635.1 | 18249.2 | 18655.5 | 1.932 | 1.96 | 1.992 | 0.543 | 0.551 | 0.511 | 2.87 | 2.96 | -2 | 0.5 | 0.551 | 0.586 | 2 | 2 | 2.79 | 0.544 | 0.529 | 0.5 | 3.01 | 2.47 | 2.3 | 0.534 | 0.522 | 0.521 | -2.01 | 2.45 | 2.42 | Fair_Thermal | 8093.1 | 15635.1 | 1.932 | 0.551 | 2.96 | 0.586 | 3.01 | 0.8358 | 0.984 | 0.6188 | 1 | 1 | 0.8466 | 0.8422 | 0.869 | 0.869 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
451 | 1538.3 | 804 | 137 | 164.5 | 31.3 | 1265.8 | 7719 | 32.4 | 45.7 | 100.2 | 102.4 | 90 | 108.4 | 42.6 | 31 | 2835.8 | 1823.7 | 1756.7 | 3356.1 | 2086.5 | 2012.7 | 1.183 | 1.144 | 1.146 | 0.886 | 0.889 | 0.944 | 8.16 | 8.57 | 8.81 | 0.866 | 0.737 | 0.839 | 8.01 | -5.9 | -7 | 0.807 | 0.743 | 0.891 | 6.49 | 5.87 | 7.84 | 0.813 | 0.865 | 0.693 | 6.65 | 6.32 | 6 | Very Poor_Mixed | 1756.7 | 2012.7 | 1.144 | 0.944 | 8.81 | 0.891 | 8.01 | 0.1412 | 0.6232 | 0.2657 | 0.3597 | 1 | 0.1374 | 0.2739 | 0.3832 | 0.3832 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
452 | 1748.6 | 890.6 | 147.8 | 197 | 33.8 | 1379 | 8330.9 | 33.8 | 45.6 | 104 | 107.8 | 96 | 114 | 44 | 33.8 | 2135.2 | 1069.8 | 1131.8 | 2334.2 | 1200 | 1312.2 | 1.093 | 1.122 | 1.159 | 0.952 | 0.951 | 0.95 | -9.36 | 9.28 | 9.33 | 0.779 | 0.945 | 0.707 | 5.14 | 9.21 | 5.73 | 0.906 | 0.727 | 0.806 | 9.29 | 6.22 | 6.28 | 0.7 | 0.978 | 0.841 | 7.35 | 5.56 | 6.13 | Very Poor_Mixed | 1069.8 | 1200 | 1.093 | 0.952 | 9.36 | 0.978 | 9.29 | 0.0501 | 0.6241 | 0.1422 | 0.2513 | 1 | 0.0657 | 0.2608 | 0.3304 | 0.3304 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
453 | 1470.7 | 858.3 | 136.8 | 168.5 | 29 | 1241.8 | 8065.6 | 34.8 | 46.8 | 105.2 | 106.3 | 93.3 | 114.2 | 43.9 | 30.8 | 1420.9 | 1916.9 | 2037.6 | 1647.4 | 2069 | 2339.2 | 1.159 | 1.079 | 1.148 | 0.906 | 0.871 | 0.918 | 8.41 | -8.28 | 8.5 | 0.815 | 0.847 | 0.729 | 6.58 | 7.62 | 8.31 | 0.809 | 0.885 | 0.697 | 9.56 | -8.19 | 7.25 | 0.871 | 0.768 | 0.764 | -6.31 | 6.11 | -8.39 | Very Poor_Mixed | 1420.9 | 1647.4 | 1.079 | 0.918 | 8.5 | 0.885 | 9.56 | 0.1457 | 0.6128 | 0.1584 | 0.3673 | 1 | 0.1488 | 0.2513 | 0.3702 | 0.3702 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
454 | 498.2 | 401.3 | 84.8 | 81.8 | 9.8 | 583.4 | 4099.5 | 51.1 | 27.4 | 84 | 81.4 | 78.5 | 92.1 | 38.6 | 16.1 | 8441.5 | 6904.9 | 6837.3 | 14824.9 | 11694.8 | 11731.2 | 1.756 | 1.694 | 1.716 | 0.593 | 0.635 | 0.627 | 3.8 | -3.18 | 4.59 | 0.539 | 0.594 | 0.552 | 3.09 | 3.76 | 3.65 | 0.566 | 0.649 | 0.597 | 3.9 | 2.52 | -2.58 | 0.598 | 0.538 | 0.534 | 3.42 | -2.96 | -2.86 | Fair_Mixed | 6837.3 | 11694.8 | 1.694 | 0.635 | 4.59 | 0.649 | 3.9 | 0.638 | 0.8323 | 0.6884 | 0.8635 | 1 | 0.6417 | 0.6975 | 0.7468 | 0.7468 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
455 | 1021.3 | 590.7 | 99.9 | 124.6 | 21 | 950.6 | 5418.6 | 48.9 | 31.2 | 93.5 | 94.9 | 85.6 | 100.4 | 40.1 | 23 | 5900.6 | 6188.6 | 5202.4 | 9575.1 | 9514.5 | 7543.6 | 1.623 | 1.537 | 1.45 | 0.727 | 0.741 | 0.744 | 5.48 | 6.31 | 5.04 | 0.643 | 0.711 | 0.654 | 5.02 | -5.47 | 4.09 | 0.694 | 0.65 | 0.658 | 4.47 | 3.65 | 4.44 | 0.61 | 0.608 | 0.612 | 4.91 | 5.17 | 4.98 | Poor_Mixed | 5202.4 | 7543.6 | 1.45 | 0.744 | 6.31 | 0.711 | 5.47 | 0.3814 | 0.7804 | 0.4334 | 0.6484 | 1 | 0.4217 | 0.5178 | 0.577 | 0.577 | Poor | 0 | 1 | DGA | 0 |  | C2H2
456 | 359.4 | 291.6 | 70.9 | 74.5 | 1.6 | 512.7 | 3845.7 | 54.2 | 25 | 77.2 | 77.6 | 70.6 | 85.8 | 35.2 | 14.1 | 909.6 | 1053.6 | 782.6 | 927.8 | 1133.5 | 851.1 | 1.02 | 1.076 | 1.088 | 0.699 | 0.719 | 0.716 | 20.7 | 6.08 | 5.63 | 0.596 | 0.636 | 0.614 | 2.43 | -4.09 | -3.61 | 0.542 | 0.576 | 0.531 | 3.21 | 4.46 | -3.46 | 0.586 | 0.61 | 0.621 | 2.37 | 4.54 | -3.65 | Critical_IR_PI | 782.6 | 851.1 | 1.02 | 0.719 | 20.7 | 0.636 | 4.54 | 0.8152 | 0.87 | 0.8947 | 0.9169 | 0.85 | 0.3594 | 0.6544 | 0.7476 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_HV_CapChange_pct
457 | 100 | 183 | 67.6 | 56.8 | 1 | 350 | 2910.4 | 59.1 | 21.9 | 76.4 | 75 | 70.6 | 84.7 | 35 | 10.4 | 8901.5 | 9473.1 | 10000 | 17181.6 | 18760 | 19944.9 | 1.93 | 1.98 | 1.994 | 0.514 | 0.56 | 0.536 | -2.33 | 2.29 | 2.51 | 0.513 | 0.5 | 0.511 | 2.54 | 2.2 | 2.32 | 0.5 | 0.5 | 0.524 | -2.64 | 2 | 2.07 | 0.541 | 0.532 | 0.5 | 2.19 | 2.14 | 2 | Good_Mixed | 8901.5 | 17181.6 | 1.93 | 0.56 | 2.51 | 0.541 | 2.64 | 0.9734 | 0.9307 | 0.9454 | 0.9955 | 1 | 0.8578 | 0.9123 | 0.9437 | 0.9437 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
458 | 501.8 | 289.7 | 85.7 | 82.6 | 9.4 | 562.4 | 3893.8 | 60 | 20.3 | 77.9 | 76.7 | 72 | 80.8 | 36.5 | 12.4 | 9437.3 | 8842 | 9673 | 18182.7 | 16645.1 | 18947.6 | 1.927 | 1.883 | 1.959 | 0.5 | 0.567 | 0.501 | 2 | -2.87 | 2 | 0.5 | 0.541 | 0.529 | 2.75 | 2.79 | 2 | 0.54 | 0.523 | 0.527 | 2.91 | -2 | 2.42 | 0.5 | 0.553 | 0.505 | 2.38 | 2.16 | 2.89 | Fair_DGA | 8842 | 16645.1 | 1.883 | 0.567 | 2.87 | 0.553 | 2.91 | 0.6574 | 0.9791 | 0.9023 | 0.9575 | 1 | 0.9188 | 0.8566 | 0.8628 | 0.8628 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
459 | 399.7 | 297.3 | 91.4 | 80 | 12.4 | 576.1 | 4151.3 | 51 | 27.8 | 80.4 | 79.4 | 76.7 | 85.9 | 36.5 | 17.4 | 8805 | 8412.9 | 9007.1 | 16499.9 | 15751.9 | 17494.7 | 1.874 | 1.872 | 1.942 | 0.57 | 0.57 | 0.612 | -3.38 | 3.57 | 3.71 | 0.532 | 0.51 | 0.533 | 3.4 | 2.79 | -3.02 | 0.61 | 0.544 | 0.5 | 3.44 | 2.27 | 3.05 | 0.547 | 0.548 | 0.512 | 3.29 | 2.88 | -2.81 | Fair_Mixed | 8412.9 | 15751.9 | 1.872 | 0.612 | 3.71 | 0.61 | 3.44 | 0.6356 | 0.8264 | 0.7896 | 0.8262 | 1 | 0.7022 | 0.7936 | 0.7795 | 0.7795 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
460 | 859.7 | 587 | 98.3 | 122.1 | 22.9 | 788.2 | 5638.7 | 43.9 | 34.7 | 91 | 87.7 | 81.6 | 97.1 | 40.4 | 25.7 | 6041.4 | 5811.1 | 5716.7 | 9823.2 | 9076.5 | 9007.3 | 1.626 | 1.562 | 1.576 | 0.772 | 0.724 | 0.76 | 6.17 | 5.85 | 6.93 | 0.598 | 0.675 | 0.593 | 5.15 | 6.3 | 6.8 | 0.709 | 0.752 | 0.703 | 3.42 | -4.07 | 4.58 | 0.771 | 0.711 | 0.7 | 4.82 | 5.29 | -5.53 | Poor_Mixed | 5716.7 | 9007.3 | 1.562 | 0.772 | 6.93 | 0.771 | 6.8 | 0.405 | 0.7379 | 0.5358 | 0.5549 | 1 | 0.3705 | 0.4544 | 0.5648 | 0.5648 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
461 | 100 | 120 | 68.8 | 53.4 | 1 | 359.5 | 3245.8 | 60 | 20 | 79.3 | 77.8 | 71.1 | 82.1 | 35.6 | 10.1 | 9385.3 | 10000 | 9350 | 18770.5 | 20000 | 18130.1 | 2 | 2 | 1.939 | 0.503 | 0.506 | 0.505 | 2.28 | 2 | 2.7 | 0.5 | 0.5 | 0.5 | 2.18 | 2 | 2 | 0.5 | 0.5 | 0.578 | 2 | 2.07 | 2.3 | 0.503 | 0.533 | 0.504 | 2 | 2.13 | 2 | Good_Mixed | 9350 | 18130.1 | 1.939 | 0.506 | 2.7 | 0.578 | 2.3 | 0.9822 | 1 | 0.8837 | 0.9992 | 1 | 0.9394 | 0.9384 | 0.9643 | 0.9643 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_HV
462 | 109.9 | 122.1 | 69.4 | 55.7 | 1 | 382.1 | 3077 | 43.1 | 38.4 | 78.8 | 77.7 | 74.7 | 85.8 | 35.5 | 11.2 | 5972.1 | 6989.8 | 7182.5 | 9891.6 | 12097.5 | 11477.1 | 1.656 | 1.731 | 1.598 | 0.564 | 0.628 | 0.624 | 3.34 | 3.63 | -4.6 | 0.534 | 0.554 | 0.536 | 2.86 | 2.52 | 2.29 | 0.539 | 0.518 | 0.526 | 2.07 | -2.83 | -2.86 | 0.575 | 0.507 | 0.533 | 2 | 3.07 | 2 | Poor_Oil | 5972.1 | 9891.6 | 1.598 | 0.628 | 4.6 | 0.575 | 3.07 | 0.971 | 0.6968 | 0.84 | 0.9821 | 1 | 0.6583 | 0.8118 | 0.8578 | 0.8578 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
463 | 164.6 | 240.5 | 79.5 | 80.8 | 3.1 | 417.2 | 3580.1 | 55.7 | 21.9 | 80.5 | 79.8 | 75.7 | 87.3 | 37.3 | 12.7 | 5190.4 | 5959.1 | 5036 | 7787.2 | 8969.8 | 7672.6 | 1.5 | 1.505 | 1.524 | 0.613 | 0.595 | 0.644 | 3.65 | 3.24 | 4.27 | 0.504 | 0.525 | 0.557 | 2.26 | 2.18 | 2.66 | 0.58 | 0.5 | 0.551 | 2.53 | 2.59 | 3.17 | 0.549 | 0.561 | 0.539 | -2.97 | 3.6 | 3.25 | Poor_IR_PI | 5036 | 7672.6 | 1.5 | 0.644 | 4.27 | 0.58 | 3.6 | 0.8068 | 0.9307 | 0.7813 | 0.9507 | 1 | 0.6511 | 0.7939 | 0.8331 | 0.8331 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
464 | 1297.8 | 736.1 | 124.8 | 156.5 | 27.6 | 1112.8 | 6456.6 | 52.2 | 26.6 | 78.9 | 82.1 | 73 | 87.1 | 35.7 | 14.6 | 8610.6 | 10000 | 8547.7 | 16137.1 | 20000 | 15820.9 | 1.874 | 2 | 1.851 | 0.572 | 0.567 | 0.559 | 2.96 | 3.77 | 2.38 | 0.579 | 0.519 | 0.535 | -3.14 | 2.62 | 2.18 | 0.565 | 0.559 | 0.5 | 2.47 | 2.86 | 3.86 | 0.504 | 0.52 | 0.568 | 2.54 | 2.28 | -3.15 | Poor_DGA | 8547.7 | 15820.9 | 1.851 | 0.572 | 3.77 | 0.579 | 3.86 | 0.2323 | 0.8443 | 0.8065 | 0.904 | 1 | 0.7611 | 0.8014 | 0.696 | 0.696 | Fair | 1 | 1 | DGA | 0 |  | C2H2
465 | 906.1 | 492.8 | 97.1 | 123 | 17.1 | 773.1 | 4984.7 | 49.5 | 32 | 90.1 | 91.4 | 81.5 | 97.7 | 38.9 | 23 | 6669 | 5549.8 | 6148.5 | 10946.6 | 8936 | 9580.4 | 1.641 | 1.61 | 1.558 | 0.681 | 0.698 | 0.633 | 5.1 | -4.88 | 4.24 | 0.635 | 0.66 | 0.612 | 4.85 | 4.11 | -5.01 | 0.69 | 0.587 | 0.66 | 4.32 | 5.4 | 5.73 | 0.674 | 0.691 | 0.66 | 5.29 | 3.97 | 4.4 | Poor_Mixed | 5549.8 | 8936 | 1.558 | 0.698 | 5.1 | 0.691 | 5.73 | 0.4545 | 0.7703 | 0.5241 | 0.6484 | 1 | 0.5333 | 0.51 | 0.6173 | 0.6173 | Fair | 1 | 1 | DGA | 0 |  | C2H2
466 | 130 | 149.3 | 71.5 | 73.7 | 6 | 374.5 | 2500 | 60 | 20 | 75 | 75 | 70 | 80.4 | 35.2 | 10.3 | 9913 | 10000 | 9507 | 19826 | 19901.1 | 18290.8 | 2 | 1.99 | 1.924 | 0.509 | 0.5 | 0.546 | 2.48 | 2 | 2.61 | 0.556 | 0.551 | 0.533 | 2.18 | 2.84 | 3.04 | 0.535 | 0.52 | 0.509 | -2 | 2.64 | 2 | 0.5 | 0.517 | 0.505 | 2.18 | 2 | 2 | Good_Mixed | 9507 | 18290.8 | 1.924 | 0.546 | 2.61 | 0.556 | 3.04 | 0.8063 | 1 | 0.9974 | 0.9968 | 1 | 0.9098 | 0.8593 | 0.9132 | 0.9132 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
467 | 752.4 | 444.3 | 97.2 | 92.8 | 12.3 | 618.6 | 4759.3 | 51.4 | 29.9 | 87.4 | 85.1 | 81.4 | 94.6 | 37.6 | 22.2 | 6527.4 | 6545.9 | 6159.4 | 10622 | 10961.4 | 10617.7 | 1.627 | 1.675 | 1.724 | 0.644 | 0.615 | 0.687 | 3.62 | 3.62 | 4.24 | 0.668 | 0.565 | 0.615 | 4.27 | 3.75 | 3.77 | 0.58 | 0.681 | 0.604 | -4.32 | 3.99 | 3.16 | 0.533 | 0.618 | 0.609 | -3.09 | 4.17 | -4.5 | Poor_Mixed | 6159.4 | 10617.7 | 1.627 | 0.687 | 4.24 | 0.681 | 4.5 | 0.5593 | 0.7973 | 0.6093 | 0.6753 | 1 | 0.6104 | 0.6113 | 0.6857 | 0.6857 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
468 | 1061 | 692.2 | 114.3 | 135.9 | 23.7 | 1011 | 5904.8 | 58.8 | 23.3 | 77.4 | 81.1 | 70 | 84.8 | 35.9 | 14 | 8695.6 | 8910.8 | 9423.7 | 17390 | 16636.6 | 18847.4 | 2 | 1.867 | 2 | 0.606 | 0.539 | 0.548 | 3.25 | 2.1 | 2.57 | 0.534 | 0.521 | 0.509 | 2.87 | 2.42 | 2.24 | 0.537 | 0.546 | 0.542 | -2.28 | 2.65 | -2.76 | 0.512 | 0.55 | 0.58 | 3.13 | 2.86 | 2.5 | Poor_DGA | 8695.6 | 16636.6 | 1.867 | 0.606 | 3.25 | 0.58 | 3.13 | 0.3189 | 0.9008 | 0.8716 | 0.9194 | 1 | 0.7951 | 0.8016 | 0.7366 | 0.7366 | Fair | 1 | 1 | DGA | 0 |  | C2H2
469 | 1579.8 | 842.9 | 141.2 | 179.2 | 32.5 | 1240.9 | 8141.2 | 37 | 44.7 | 104.1 | 100.3 | 90.5 | 112.1 | 44 | 31.1 | 2569.9 | 2905 | 718.4 | 3216.4 | 3846.9 | 1200 | 1.252 | 1.324 | 1.67 | 0.954 | 0.951 | 0.907 | -8.86 | -9.84 | 8.5 | 0.957 | 0.685 | 0.808 | 5.51 | -7.79 | 6.05 | 0.71 | 0.902 | 0.854 | -7.47 | 8.49 | 9.07 | 0.729 | 0.718 | 0.806 | 5.25 | 8.11 | -7.4 | Very Poor_Mixed | 718.4 | 1200 | 1.252 | 0.954 | 9.84 | 0.957 | 9.07 | 0.1102 | 0.6328 | 0.2242 | 0.3559 | 1 | 0.0881 | 0.2678 | 0.3643 | 0.3643 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
470 | 1766 | 982.4 | 148.3 | 197 | 32.9 | 1379 | 8847.5 | 58.4 | 20.4 | 80.6 | 78.8 | 71.1 | 82.2 | 35.5 | 10.6 | 9032.4 | 9682.4 | 8366.3 | 15825.7 | 18463.7 | 15590.7 | 1.752 | 1.907 | 1.864 | 0.595 | 0.5 | 0.552 | -2.84 | 2 | 2 | 0.612 | 0.543 | 0.55 | 3.18 | -3.62 | 2.59 | 0.577 | 0.601 | 0.504 | 12.15 | 3.41 | 3.35 | 0.629 | 0.613 | 0.596 | 2.63 | -2.84 | -3.22 | Critical_DGA | 8366.3 | 15590.7 | 1.752 | 0.595 | 2.84 | 0.629 | 12.15 | 0.0355 | 0.9748 | 0.8626 | 0.9925 | 1 | 0.8654 | 0.668 | 0.6631 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
471 | 1628.2 | 929.9 | 139.9 | 186 | 32.7 | 1259.9 | 8627.3 | 32.8 | 49.4 | 102.4 | 101.5 | 92 | 111 | 43 | 32.3 | 772.5 | 1091.8 | 690 | 1200 | 1265.2 | 1200 | 1.553 | 1.159 | 1.739 | 0.966 | 0.938 | 0.938 | 9.51 | 9.12 | 9.01 | 0.735 | 0.758 | 0.758 | -7.04 | 7.52 | 7.89 | 0.893 | 0.735 | 0.861 | 8.07 | -6.55 | -5.12 | 0.815 | 0.817 | 0.817 | 8.56 | 8.42 | -7.73 | Very Poor_Mixed | 690 | 1200 | 1.159 | 0.966 | 9.51 | 0.893 | 8.56 | 0.0834 | 0.5888 | 0.2309 | 0.3098 | 1 | 0.0738 | 0.2552 | 0.3463 | 0.3463 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
472 | 1497.8 | 858.8 | 133.2 | 167.7 | 29.6 | 1225.3 | 7367.3 | 35.5 | 43.7 | 101.8 | 103.8 | 92.2 | 110.7 | 44.5 | 29.7 | 1575.6 | 2103.2 | 2452.8 | 1742.2 | 2524.8 | 2717.6 | 1.106 | 1.2 | 1.108 | 0.94 | 0.91 | 0.869 | -8 | 8.93 | 8.15 | 0.765 | 0.709 | 0.807 | 5.8 | 6.77 | 7.65 | 0.901 | 0.754 | 0.893 | 6.27 | 6.89 | -7.55 | 0.692 | 0.784 | 0.828 | 6.11 | 5.95 | 5.48 | Very Poor_Mixed | 1575.6 | 1742.2 | 1.106 | 0.94 | 8.93 | 0.901 | 7.65 | 0.1551 | 0.6425 | 0.2109 | 0.4089 | 1 | 0.1453 | 0.2935 | 0.3906 | 0.3906 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
473 | 244.6 | 120 | 66.5 | 58.8 | 1 | 406.8 | 2668.7 | 56.8 | 25.1 | 84.1 | 78 | 76.2 | 88 | 36.8 | 18.5 | 9499.3 | 9464.4 | 9325.1 | 18998.5 | 18359.5 | 18048.3 | 2 | 1.94 | 1.935 | 0.894 | 0.99 | 0.87 | 8.54 | 9.47 | 8.14 | 0.558 | 0.52 | 0.504 | 2.19 | 2 | -10.72 | 0.555 | 0.523 | 0.516 | 3.01 | 2.65 | -2 | 0.568 | 0.5 | 0.5 | 2 | 2.92 | 2.62 | Critical_Winding_TD_Cap | 9325.1 | 18048.3 | 1.935 | 0.99 | 9.47 | 0.568 | 10.72 | 0.9491 | 0.8683 | 0.7649 | 0.7933 | 1 | 0.1197 | 0.8264 | 0.7831 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Winding_LV_TanDelta_pct
474 | 1459 | 879.1 | 137.6 | 162.8 | 31.1 | 1300.4 | 7324.5 | 36.1 | 46.5 | 102.6 | 104.5 | 89.8 | 112.3 | 44.3 | 28 | 2265.8 | 1468.8 | 2255.9 | 2786 | 1574.6 | 2660.5 | 1.23 | 1.072 | 1.179 | 0.851 | 0.891 | 0.877 | -7.97 | 8.5 | 8.43 | 0.833 | 0.712 | 0.786 | -6.17 | 5.89 | -5.7 | 0.864 | 0.817 | 0.751 | 4.84 | -5.91 | 7.93 | 0.861 | 0.817 | 0.803 | -6.86 | 4.97 | 6 | Very Poor_Mixed | 1468.8 | 1574.6 | 1.072 | 0.891 | 8.5 | 0.864 | 7.93 | 0.1418 | 0.6156 | 0.2096 | 0.4719 | 1 | 0.1718 | 0.2957 | 0.3912 | 0.3912 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
475 | 100 | 120 | 66.5 | 59.9 | 1 | 404.1 | 2500 | 56.4 | 20 | 75.6 | 76.7 | 70 | 80 | 35 | 11.7 | 9808.8 | 9234.7 | 10000 | 19119.6 | 17682 | 19206.5 | 1.949 | 1.915 | 1.921 | 0.533 | 0.5 | 0.511 | 2.95 | 2.08 | 2.8 | 0.513 | 0.551 | 0.5 | -2 | 2.11 | 2.4 | 0.534 | 0.561 | 0.548 | 2 | 2 | 2.37 | 0.536 | 0.505 | 0.55 | 2 | 2.66 | 2.1 | Good_Mixed | 9234.7 | 17682 | 1.915 | 0.533 | 2.95 | 0.561 | 2.66 | 0.9655 | 1 | 0.9623 | 0.9724 | 1 | 0.8967 | 0.8449 | 0.9438 | 0.9438 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
476 | 1583.1 | 841.2 | 128.4 | 168.7 | 28.2 | 1225.1 | 7818.6 | 35.6 | 45.5 | 102.8 | 100.7 | 93.2 | 110.6 | 42.5 | 31.1 | 1739.8 | 763.4 | 2133.7 | 1841.8 | 1200 | 2677.2 | 1.059 | 1.572 | 1.255 | 0.94 | 0.881 | 0.944 | 9.03 | -8.16 | 8.36 | 0.797 | 0.862 | 0.792 | -8.21 | -6.44 | 7.02 | 0.75 | 0.811 | 0.761 | 7.93 | -5 | 8.83 | 0.761 | 0.702 | 0.731 | 8.23 | 7.86 | -8.22 | Very Poor_Mixed | 763.4 | 1200 | 1.059 | 0.944 | 9.03 | 0.862 | 8.83 | 0.1548 | 0.6251 | 0.232 | 0.3559 | 1 | 0.1267 | 0.2764 | 0.3822 | 0.3822 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
477 | 841.3 | 425.2 | 101.6 | 123.2 | 15.1 | 740.1 | 5601.2 | 46.7 | 31.8 | 93.2 | 93.3 | 84.3 | 98.7 | 40.7 | 25.3 | 5523.5 | 4624.4 | 5032.3 | 8403.2 | 6817.6 | 7287.9 | 1.521 | 1.474 | 1.448 | 0.711 | 0.692 | 0.705 | 5.33 | -4.63 | 4.89 | 0.73 | 0.725 | 0.727 | 5.22 | -4.36 | 6.4 | 0.672 | 0.692 | 0.693 | 4.62 | 5.02 | 6.08 | 0.66 | 0.726 | 0.621 | -4.78 | 5.32 | 4.91 | Poor_Mixed | 4624.4 | 6817.6 | 1.448 | 0.711 | 5.33 | 0.73 | 6.4 | 0.4751 | 0.7728 | 0.4578 | 0.569 | 1 | 0.4897 | 0.4427 | 0.594 | 0.594 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
478 | 895.1 | 538.4 | 104.5 | 111.6 | 20 | 828.3 | 5574.7 | 44.4 | 35.1 | 95.6 | 91.9 | 83.7 | 102.1 | 40.3 | 25.5 | 5419.4 | 6264.9 | 6009.3 | 8089.6 | 9689.7 | 9352.5 | 1.493 | 1.547 | 1.556 | 0.665 | 0.737 | 0.752 | 5.67 | -5.48 | 5.29 | 0.69 | 0.605 | 0.618 | 4.42 | 5.52 | 4.28 | 0.591 | 0.667 | 0.621 | 3.97 | 4.76 | 4.84 | 0.674 | 0.621 | 0.734 | 4.43 | 3.69 | 4.23 | Poor_Mixed | 5419.4 | 8089.6 | 1.493 | 0.752 | 5.67 | 0.734 | 5.52 | 0.4254 | 0.7333 | 0.4412 | 0.562 | 1 | 0.4469 | 0.5307 | 0.5847 | 0.5847 | Poor | 0 | 1 | DGA | 0 |  | C2H2
479 | 1421.7 | 870.8 | 137.6 | 179.1 | 34.3 | 1223 | 8405.6 | 36 | 42.6 | 105.4 | 105.9 | 91.6 | 116.4 | 44.7 | 32 | 2309.8 | 2019.8 | 1948.3 | 2719.8 | 2409.7 | 2299.8 | 1.178 | 1.193 | 1.18 | 0.899 | 0.964 | 0.988 | 8.99 | 9.39 | 9.49 | 0.808 | 0.818 | 0.785 | 6.59 | 6.38 | -4.52 | 0.724 | 0.747 | 0.678 | 6.77 | -7.25 | 8.26 | 0.921 | 0.685 | 0.851 | 7.42 | -5.65 | 7.42 | Very Poor_Mixed | 1948.3 | 2299.8 | 1.178 | 0.988 | 9.49 | 0.921 | 8.26 | 0.1122 | 0.6534 | 0.1523 | 0.3214 | 1 | 0.0683 | 0.301 | 0.3615 | 0.3615 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
480 | 1393.5 | 756.8 | 130.7 | 168.5 | 69.9 | 1136.1 | 7359.3 | 39.4 | 42.1 | 103.6 | 101.5 | 88.7 | 110.5 | 43.6 | 35.9 | 2241 | 1957.2 | 2889 | 2819.8 | 2353.3 | 3644.2 | 1.258 | 1.202 | 1.261 | 0.931 | 0.849 | 0.923 | 8.24 | 8 | 8.93 | 0.773 | 0.667 | 0.683 | 4.87 | 5.84 | 7.81 | 0.74 | 0.796 | 0.733 | 6.91 | 5.42 | 6.45 | 0.788 | 0.76 | 0.882 | 7.59 | -5.61 | 6.14 | Critical_Mixed | 1957.2 | 2353.3 | 1.202 | 0.931 | 8.93 | 0.882 | 7.81 | 0.1612 | 0.6584 | 0.2414 | 0.1678 | 1 | 0.1477 | 0.3352 | 0.3929 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
481 | 1549.1 | 888.3 | 141.8 | 171.7 | 33.3 | 1334 | 8345 | 33.3 | 48.3 | 105.3 | 107.8 | 91.8 | 111.5 | 44.3 | 33.4 | 988.3 | 2035.7 | 1568.3 | 1200 | 2534.5 | 1728.3 | 1.214 | 1.245 | 1.102 | 0.936 | 0.918 | 0.99 | 8.63 | 9.6 | 9.56 | 0.697 | 0.853 | 0.884 | 6.62 | 6.72 | 6.44 | 0.76 | 0.759 | 0.714 | 7.39 | 5.73 | 7.83 | 0.842 | 0.731 | 0.873 | 5.97 | 6.51 | -8.36 | Very Poor_Mixed | 988.3 | 1200 | 1.102 | 0.99 | 9.6 | 0.884 | 8.36 | 0.0969 | 0.5988 | 0.1687 | 0.267 | 1 | 0.0711 | 0.2842 | 0.3474 | 0.3474 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
482 | 126.4 | 205.1 | 69.1 | 59.9 | 1 | 408.8 | 3191.5 | 55.7 | 23.6 | 79.8 | 82.5 | 72.2 | 86.2 | 35.2 | 20.1 | 9007.9 | 9753.7 | 9477.6 | 16598.9 | 18670.9 | 18709.4 | 1.843 | 1.914 | 1.974 | 0.531 | 0.529 | 0.574 | 2.78 | 2.85 | 2.89 | 0.504 | 0.516 | 0.5 | 2.54 | 3.13 | -2.87 | 0.541 | 0.513 | 0.549 | 2.98 | 2 | 3.15 | 0.5 | 0.56 | 0.505 | 2.4 | 2.32 | 2.81 | Fair_Age | 9007.9 | 16598.9 | 1.843 | 0.574 | 2.89 | 0.56 | 3.15 | 0.9452 | 0.895 | 0.8086 | 0.7436 | 1 | 0.8089 | 0.86 | 0.8898 | 0.8898 | Good | 1 | 0 | No_Anomaly | 0 |  | Age_Years
483 | 1514.5 | 781.4 | 136.6 | 175.1 | 29.7 | 1235 | 8206.4 | 33.1 | 47.6 | 106.6 | 104.6 | 93.8 | 114.5 | 44.1 | 32.7 | 2789.4 | 1138.8 | 1804.7 | 3149.3 | 1200 | 2105.6 | 1.129 | 1.054 | 1.167 | 0.959 | 0.981 | 0.973 | 9.04 | 9.49 | 9.84 | 0.828 | 0.862 | 0.714 | 7.72 | 5.73 | -8.08 | 0.859 | 0.753 | 0.72 | 6.81 | 5.95 | 6.57 | 0.769 | 0.918 | 0.92 | 5.62 | 6.14 | 6.87 | Very Poor_Mixed | 1138.8 | 1200 | 1.054 | 0.981 | 9.84 | 0.92 | 8.08 | 0.1412 | 0.6053 | 0.1544 | 0.2943 | 1 | 0.0459 | 0.2676 | 0.3527 | 0.3527 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
484 | 883.7 | 504.5 | 104.8 | 119.2 | 17.2 | 842.7 | 5704.6 | 46.8 | 35 | 91.4 | 94.1 | 82.5 | 99.3 | 38.8 | 24.6 | 5251.2 | 5586.5 | 5850 | 8047.1 | 9132.7 | 8886.7 | 1.532 | 1.635 | 1.519 | 0.737 | 0.691 | 0.742 | 6.28 | 5.03 | 6.02 | 0.697 | 0.738 | 0.716 | 3.98 | 4.94 | 4.56 | 0.736 | 0.613 | 0.693 | 3.79 | 3.28 | 4.95 | 0.671 | 0.61 | 0.701 | 3.98 | 4.83 | 4.03 | Poor_Mixed | 5251.2 | 8047.1 | 1.519 | 0.742 | 6.28 | 0.738 | 4.95 | 0.4363 | 0.7345 | 0.4847 | 0.5935 | 1 | 0.4252 | 0.4882 | 0.5827 | 0.5827 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
485 | 116.4 | 161.1 | 66.2 | 58.3 | 1 | 397.2 | 2500 | 56.8 | 23.5 | 80.3 | 82.5 | 72.8 | 88.9 | 36.6 | 11.3 | 10000 | 9468.5 | 10000 | 19007.4 | 18282.1 | 19666.2 | 1.901 | 1.931 | 1.967 | 0.5 | 0.546 | 0.559 | 2.06 | 3.41 | -2.29 | 0.68 | 0.524 | 0.5 | 5.6 | 2.45 | 2 | 0.519 | 0.569 | 0.522 | 2 | -2.16 | 2 | 0.5 | 0.536 | 0.527 | 2.57 | -2 | 2 | Fair_Bushing_TD_Cap | 9468.5 | 18282.1 | 1.901 | 0.559 | 3.41 | 0.68 | 5.6 | 0.9614 | 0.8969 | 0.7793 | 0.9802 | 1 | 0.8608 | 0.8277 | 0.9044 | 0.9044 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
486 | 138.1 | 180.1 | 67.1 | 61 | 4.4 | 406.3 | 3129.7 | 59.2 | 21.5 | 76.4 | 77.8 | 71 | 80 | 35.3 | 13 | 8159.4 | 8798 | 9392.1 | 15608.1 | 16813.1 | 18133.6 | 1.913 | 1.911 | 1.931 | 0.527 | 0.535 | 0.525 | 2.01 | -2.54 | 2.6 | 0.548 | 0.529 | 0.574 | 2.84 | 2.4 | 2.47 | 0.526 | 0.583 | 0.515 | -2 | 2.53 | 2.59 | 0.573 | 0.507 | 0.52 | -2 | -2.15 | 2.42 | Good_Mixed | 8159.4 | 15608.1 | 1.911 | 0.535 | 2.6 | 0.583 | 2.84 | 0.8334 | 0.9406 | 0.926 | 0.9438 | 1 | 0.8699 | 0.8074 | 0.8881 | 0.8881 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
487 | 524.6 | 340.6 | 90.5 | 94.5 | 9.6 | 683.2 | 4386.3 | 51.9 | 31.5 | 86.4 | 89.7 | 78.9 | 89.7 | 39.8 | 20.4 | 7479.8 | 8190.3 | 8133.4 | 12811.4 | 14532.5 | 14756.2 | 1.713 | 1.774 | 1.814 | 0.647 | 0.641 | 0.65 | 4.31 | 4.18 | -4.2 | 0.66 | 0.659 | 0.593 | 3.55 | 4.63 | 4.77 | 0.627 | 0.551 | 0.618 | 3.79 | 3.65 | 3.4 | 0.676 | 0.628 | 0.602 | 4.12 | 4.97 | 4.06 | Fair_Mixed | 7479.8 | 12811.4 | 1.713 | 0.65 | 4.31 | 0.676 | 4.97 | 0.61 | 0.7766 | 0.6121 | 0.734 | 1 | 0.5873 | 0.5767 | 0.6896 | 0.6896 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
488 | 1623.3 | 854.4 | 132.8 | 189 | 30.9 | 1229 | 8195.2 | 33.4 | 44.7 | 104.1 | 103.3 | 94.1 | 115.6 | 44.2 | 31.3 | 1928.7 | 2408.3 | 824.7 | 2247.5 | 2790.5 | 1200 | 1.165 | 1.159 | 1.455 | 0.97 | 0.952 | 0.967 | 8.95 | -9.66 | -9.47 | 0.707 | 0.84 | 0.835 | 6.22 | 7.07 | -8.09 | 0.687 | 0.891 | 0.826 | 6.8 | 4.76 | 5.19 | 0.761 | 0.874 | 0.734 | 7.89 | 5.23 | -8.57 | Very Poor_Mixed | 824.7 | 1200 | 1.159 | 0.97 | 9.66 | 0.891 | 8.57 | 0.1122 | 0.6328 | 0.1677 | 0.3483 | 1 | 0.056 | 0.2872 | 0.3577 | 0.3577 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
489 | 1547.2 | 857.7 | 138.5 | 175.3 | 28.2 | 1284.9 | 7870.6 | 35.4 | 46.8 | 105.9 | 107.3 | 97.6 | 116.9 | 43.6 | 33.1 | 690 | 1188.1 | 1197.3 | 1200 | 1322.8 | 1275.2 | 1.739 | 1.113 | 1.065 | 0.981 | 0.989 | 0.978 | 9.45 | 9.84 | -9.84 | 0.863 | 0.875 | 0.723 | 6.62 | 6.67 | 5.99 | 0.754 | 0.801 | 0.752 | -8.09 | 7.3 | 7.49 | 0.844 | 0.887 | 0.885 | 8.43 | 8.76 | -8.34 | Very Poor_Mixed | 690 | 1200 | 1.065 | 0.989 | 9.84 | 0.887 | 8.76 | 0.1348 | 0.6128 | 0.114 | 0.2787 | 1 | 0.0256 | 0.232 | 0.3379 | 0.3379 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
490 | 180.3 | 175.6 | 67.6 | 53.6 | 2.4 | 357.9 | 2836.2 | 56.3 | 24.9 | 79 | 80.4 | 71.7 | 82.6 | 36.7 | 14.9 | 9956 | 9531.1 | 8995.2 | 19744.2 | 18454 | 16033 | 1.983 | 1.936 | 1.782 | 0.765 | 0.767 | 0.804 | -6.03 | 6.85 | 6.33 | 0.585 | 0.536 | 0.589 | 3.05 | 3.06 | 3.85 | 0.5 | 0.613 | 0.605 | -2.26 | -3.23 | 3.33 | 0.616 | 0.564 | 0.536 | -2.15 | 3.18 | 2.69 | Poor_Winding_TD_Cap | 8995.2 | 16033 | 1.782 | 0.804 | 6.85 | 0.616 | 3.85 | 0.8913 | 0.8717 | 0.8489 | 0.8962 | 1 | 0.3436 | 0.7224 | 0.7952 | 0.7952 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
491 | 565.6 | 352.1 | 87.1 | 161.1 | 1.1 | 602.5 | 3972.4 | 17 | 24.1 | 109.3 | 109.3 | 98.1 | 119.2 | 45.2 | 15.8 | 7319.9 | 7990 | 8081.4 | 12163.1 | 13878.8 | 13988.4 | 1.662 | 1.737 | 1.731 | 0.595 | 0.535 | 0.613 | -3.13 | 3.04 | -4.28 | 0.632 | 0.622 | 0.517 | 3.79 | 3.86 | 4.43 | 0.645 | 0.651 | 0.663 | 4.37 | -4.57 | -4 | 0.615 | 0.648 | 0.639 | 3.93 | 4.54 | 3.35 | Critical_Thermal | 7319.9 | 12163.1 | 1.662 | 0.613 | 4.28 | 0.663 | 4.57 | 0.7079 | 0.3024 | 0.0588 | 0.8718 | 1 | 0.7148 | 0.5778 | 0.6268 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
492 | 488.5 | 235.9 | 82.9 | 74.8 | 7.9 | 510.4 | 3738.9 | 54.9 | 28.4 | 83.3 | 84 | 74.2 | 89.8 | 37.6 | 17.7 | 7193.4 | 7718.3 | 7765.2 | 12179.1 | 13714.7 | 13770.3 | 1.693 | 1.777 | 1.773 | 0.562 | 0.617 | 0.587 | 2.7 | 4.11 | 3.94 | 0.557 | 0.564 | 0.537 | 2.55 | 3.25 | 3.09 | 0.58 | 0.562 | 0.633 | -2.33 | -3.07 | 2.76 | 0.525 | 0.589 | 0.576 | 3.39 | -3.48 | 3.5 | Fair_Mixed | 7193.4 | 12179.1 | 1.693 | 0.617 | 4.11 | 0.633 | 3.5 | 0.6997 | 0.8178 | 0.7221 | 0.8173 | 1 | 0.6959 | 0.7113 | 0.7716 | 0.7716 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
493 | 703.8 | 453.2 | 89.4 | 112.6 | 15.8 | 813.2 | 5714.1 | 59.7 | 20.8 | 80.3 | 77.1 | 72.2 | 84.8 | 36.6 | 12.7 | 9307.4 | 9704.1 | 9600 | 17999.4 | 17996 | 19146 | 1.934 | 1.854 | 1.994 | 0.547 | 0.536 | 0.538 | -2.29 | 2.41 | 2.43 | 0.546 | 0.505 | 0.547 | 2.1 | 2.92 | 2 | 0.56 | 0.569 | 0.5 | 2.44 | 3.02 | 2.27 | 0.577 | 0.602 | 0.5 | 2.19 | -2.89 | -2.76 | Fair_DGA | 9307.4 | 17996 | 1.854 | 0.547 | 2.43 | 0.602 | 3.02 | 0.4865 | 0.9605 | 0.8535 | 0.9507 | 1 | 0.8474 | 0.8097 | 0.7942 | 0.7942 | Fair | 1 | 1 | DGA | 0 |  | C2H2
494 | 950.3 | 585.7 | 113.3 | 141.8 | 23 | 931.2 | 5782.8 | 56.7 | 22 | 77.4 | 79.7 | 71 | 83.1 | 36.6 | 14 | 9305.9 | 7982.7 | 9720.7 | 18455.6 | 13868 | 18987.9 | 1.983 | 1.737 | 1.953 | 0.605 | 0.641 | 0.547 | 3.45 | 3.35 | 3.41 | 0.532 | 0.583 | 0.509 | 2.96 | 2.8 | 2.03 | 0.5 | 0.509 | 0.529 | 2.49 | 3.48 | 2.64 | 0.506 | 0.556 | 0.546 | 3.54 | 2.2 | 3.26 | Poor_DGA | 7982.7 | 13868 | 1.737 | 0.641 | 3.45 | 0.583 | 3.54 | 0.3491 | 0.9283 | 0.8756 | 0.9194 | 1 | 0.6975 | 0.8228 | 0.738 | 0.738 | Fair | 1 | 1 | DGA | 0 |  | C2H2
495 | 1619.9 | 927.8 | 141.2 | 192 | 31.9 | 1249 | 7874.2 | 34.4 | 49.1 | 106.2 | 102.9 | 94.8 | 115.3 | 44 | 32.8 | 1016.5 | 1546.9 | 912.8 | 1200 | 1651.1 | 1200 | 1.181 | 1.067 | 1.315 | 0.941 | 0.958 | 0.99 | -8.92 | -9.59 | 9.81 | 0.952 | 0.835 | 0.847 | 6.51 | 7.67 | -6.22 | 0.802 | 0.742 | 0.767 | -8.64 | 7.58 | -7.57 | 0.785 | 0.921 | 0.988 | 7.22 | 7.76 | -8.5 | Very Poor_Mixed | 912.8 | 1200 | 1.067 | 0.99 | 9.81 | 0.988 | 8.64 | 0.0929 | 0.5915 | 0.1573 | 0.2904 | 1 | 0.0521 | 0.207 | 0.329 | 0.329 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
496 | 1164 | 718.4 | 120.5 | 148.9 | 23.9 | 941.4 | 6588.5 | 56 | 25.7 | 81.7 | 78.1 | 75.3 | 86 | 37.1 | 13.6 | 8558 | 8195 | 9139.6 | 16432.1 | 14687.9 | 17851.8 | 1.92 | 1.792 | 1.953 | 0.563 | 0.579 | 0.578 | 2.37 | 2.43 | -2.59 | 0.58 | 0.512 | 0.5 | 2.59 | 2.86 | -2.37 | 0.527 | 0.549 | 0.51 | 2.6 | -2.05 | 2.79 | 0.533 | 0.545 | 0.558 | -2.41 | 2.07 | 2.15 | Poor_DGA | 8195 | 14687.9 | 1.792 | 0.579 | 2.59 | 0.58 | 2.86 | 0.2913 | 0.8584 | 0.7976 | 0.9294 | 1 | 0.7898 | 0.8255 | 0.7212 | 0.7212 | Fair | 1 | 1 | DGA | 0 |  | C2H2
497 | 839.6 | 666.8 | 107.5 | 119.8 | 18.4 | 919.6 | 5426.2 | 46.6 | 32.8 | 90.1 | 93.4 | 83.6 | 100.7 | 40.4 | 24.6 | 5058.6 | 5199.6 | 4564 | 7667.8 | 8212.1 | 6949.8 | 1.516 | 1.579 | 1.523 | 0.726 | 0.724 | 0.714 | 5.73 | 5.4 | 5.34 | 0.621 | 0.692 | 0.696 | 4.47 | 4.17 | 4.48 | 0.725 | 0.661 | 0.769 | 5.46 | 4.11 | 5.6 | 0.68 | 0.782 | 0.672 | 3.97 | 4.51 | 5.26 | Poor_Mixed | 4564 | 6949.8 | 1.516 | 0.726 | 5.73 | 0.782 | 5.6 | 0.4052 | 0.7605 | 0.4735 | 0.5935 | 1 | 0.4421 | 0.4562 | 0.5736 | 0.5736 | Poor | 0 | 1 | DGA | 0 |  | C2H2
498 | 1439.5 | 857.2 | 135.6 | 178.5 | 32.8 | 1146.5 | 7612.7 | 35.6 | 44.3 | 104.7 | 102.8 | 93.9 | 114.4 | 43.4 | 29.8 | 974.9 | 1523.7 | 1416.2 | 1200 | 1781.5 | 1537.2 | 1.231 | 1.169 | 1.085 | 0.912 | 0.897 | 0.865 | 8.86 | -9.23 | 7.83 | 0.754 | 0.747 | 0.766 | 7.8 | 5.82 | -6.65 | 0.868 | 0.756 | 0.772 | -7.67 | 7.71 | 5.32 | 0.836 | 0.86 | 0.891 | 6.14 | 7.91 | -7.06 | Very Poor_Mixed | 974.9 | 1200 | 1.085 | 0.912 | 9.23 | 0.891 | 7.91 | 0.1398 | 0.6367 | 0.18 | 0.4051 | 1 | 0.1416 | 0.2661 | 0.3773 | 0.3773 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
499 | 405.4 | 286.3 | 82.5 | 76.3 | 7.2 | 508.9 | 3331.4 | 53 | 27.1 | 82.2 | 80.6 | 75.6 | 85.4 | 37.4 | 16 | 7750.8 | 8040.4 | 7853.9 | 14041.3 | 14861.5 | 13934.3 | 1.812 | 1.848 | 1.774 | 0.658 | 0.549 | 0.601 | 4.01 | 3.58 | 3.61 | 0.532 | 0.587 | 0.599 | 3.17 | 2.92 | 3.58 | 0.582 | 0.558 | 0.542 | 3.34 | -2.86 | 2.18 | 0.582 | 0.586 | 0.555 | 2.54 | -2.94 | 3.14 | Fair_Mixed | 7750.8 | 13934.3 | 1.774 | 0.658 | 4.01 | 0.599 | 3.58 | 0.71 | 0.8367 | 0.7701 | 0.8663 | 1 | 0.6714 | 0.7131 | 0.7806 | 0.7806 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
500 | 145.2 | 212 | 73.9 | 72.8 | 2.8 | 480.6 | 3479.3 | 49.5 | 31.4 | 75.8 | 76 | 70.5 | 81.6 | 35 | 11.4 | 8757 | 7857.2 | 7841.7 | 15941.5 | 14194.3 | 13499.4 | 1.82 | 1.807 | 1.721 | 0.52 | 0.602 | 0.595 | 2.44 | 3.3 | 3.85 | 0.505 | 0.525 | 0.537 | 2.44 | 2.44 | 2.88 | 0.578 | 0.547 | 0.537 | 2.13 | 2.44 | 3.15 | 0.532 | 0.5 | 0.5 | 3.1 | -2.62 | 2.87 | Fair_Oil | 7841.7 | 13499.4 | 1.721 | 0.602 | 3.85 | 0.578 | 3.15 | 0.8216 | 0.7778 | 0.9524 | 0.9783 | 1 | 0.7486 | 0.8348 | 0.858 | 0.858 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
501 | 858.2 | 547 | 106.9 | 117.8 | 20 | 834.8 | 5585.8 | 47.4 | 31.8 | 90 | 89.3 | 84.6 | 97.1 | 40.4 | 27.7 | 6181.6 | 6574 | 5349.8 | 10031.8 | 10868.7 | 8054.2 | 1.623 | 1.653 | 1.506 | 0.76 | 0.798 | 0.741 | 5.1 | 6.38 | 5.78 | 0.664 | 0.638 | 0.628 | 4.21 | 4.37 | 4.49 | 0.656 | 0.648 | 0.685 | 4.74 | 5.32 | 4.42 | 0.671 | 0.653 | 0.716 | 4.51 | 4.81 | 4.13 | Poor_Mixed | 5349.8 | 8054.2 | 1.506 | 0.798 | 6.38 | 0.716 | 5.32 | 0.4186 | 0.7728 | 0.5126 | 0.4829 | 1 | 0.3895 | 0.5041 | 0.578 | 0.578 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
502 | 150.8 | 158.7 | 71.4 | 68.9 | 2.4 | 403.7 | 2755.9 | 60 | 20.7 | 76.3 | 76 | 71.1 | 81 | 35.8 | 12.9 | 10000 | 9789.3 | 9060.5 | 20000 | 19578.7 | 17274.1 | 2 | 2 | 1.907 | 0.528 | 0.541 | 0.52 | 2.05 | 3.08 | 2.15 | 0.5 | 0.5 | 0.5 | 2.21 | 2 | 2.84 | 0.528 | 0.5 | 0.5 | 2.5 | 2.1 | 2.09 | 0.523 | 0.517 | 0.534 | 2.08 | 2.2 | 2 | Good_Mixed | 9060.5 | 17274.1 | 1.907 | 0.541 | 3.08 | 0.534 | 2.84 | 0.8609 | 0.9638 | 0.9393 | 0.9461 | 1 | 0.8671 | 0.9245 | 0.9199 | 0.9199 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
503 | 1491.1 | 870.3 | 131.9 | 172.7 | 27.8 | 1175.1 | 8106.6 | 34.9 | 47.8 | 103.7 | 104.4 | 91.7 | 116 | 44.2 | 33.4 | 2784.2 | 2045.1 | 2786.8 | 3261.4 | 2272.9 | 3293.2 | 1.171 | 1.111 | 1.182 | 0.932 | 0.891 | 0.886 | 8.63 | 8.62 | 8.32 | 0.839 | 0.69 | 0.81 | -8.94 | 8.54 | -8.16 | 0.704 | 0.899 | 0.923 | 7.53 | 7.08 | 7.29 | 0.798 | 0.781 | 0.814 | 8.97 | -7.81 | -7.01 | Very Poor_Mixed | 2045.1 | 2272.9 | 1.111 | 0.932 | 8.63 | 0.923 | 8.97 | 0.1559 | 0.6035 | 0.1752 | 0.267 | 1 | 0.1391 | 0.2335 | 0.3638 | 0.3638 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
504 | 1636.4 | 833.5 | 135.3 | 170 | 26.2 | 1282.4 | 8294.4 | 36.2 | 43.1 | 106.6 | 108.3 | 95.9 | 117.2 | 45.6 | 31.4 | 2038.8 | 2465.6 | 1740.1 | 2140.7 | 2909.6 | 1845.8 | 1.05 | 1.18 | 1.061 | 0.948 | 0.891 | 0.902 | 9.29 | 8.29 | 9.06 | 0.852 | 0.89 | 0.804 | 7.26 | -9.27 | 8.09 | 0.99 | 0.942 | 0.96 | -7.89 | 9.72 | -7.08 | 0.846 | 0.827 | 0.946 | -8.28 | 8.61 | 8.87 | Very Poor_Mixed | 1740.1 | 1845.8 | 1.05 | 0.948 | 9.29 | 0.99 | 9.72 | 0.1426 | 0.6484 | 0.0979 | 0.3444 | 1 | 0.1138 | 0.1381 | 0.3413 | 0.3413 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
505 | 846.5 | 520.4 | 103.7 | 117.6 | 13.4 | 835.7 | 6085 | 44.8 | 33.6 | 93 | 90.8 | 84.3 | 101 | 40.8 | 25.7 | 6028.9 | 6100.1 | 6274.8 | 9439.4 | 10024.2 | 10250.6 | 1.566 | 1.643 | 1.634 | 0.734 | 0.73 | 0.653 | 5.01 | 6.23 | -4.67 | 0.629 | 0.616 | 0.749 | 4.64 | 5.44 | 5.58 | 0.688 | 0.718 | 0.665 | 4.78 | 4.71 | 4.8 | 0.633 | 0.696 | 0.693 | 5.77 | 4.16 | 3.78 | Poor_Mixed | 6028.9 | 9439.4 | 1.566 | 0.734 | 6.23 | 0.749 | 5.77 | 0.4625 | 0.7509 | 0.463 | 0.5549 | 1 | 0.4686 | 0.4773 | 0.5913 | 0.5913 | Poor | 0 | 1 | DGA | 0 |  | C2H2
506 | 1477.5 | 926 | 137 | 169.4 | 27.6 | 1257.7 | 8042.7 | 37.2 | 42.2 | 102 | 100.2 | 91.9 | 109.1 | 42.7 | 30.3 | 1994.3 | 3230 | 1832.2 | 2108.5 | 4224.6 | 2072.8 | 1.057 | 1.308 | 1.131 | 0.961 | 0.936 | 0.898 | 8.95 | 8.85 | -7.9 | 0.692 | 0.751 | 0.692 | 6.62 | 5.75 | 8.33 | 0.896 | 0.805 | 0.689 | 8.66 | 7.85 | 8.77 | 0.722 | 0.794 | 0.781 | -6.33 | -7.4 | -8.39 | Very Poor_Mixed | 1832.2 | 2072.8 | 1.057 | 0.961 | 8.95 | 0.896 | 8.77 | 0.1422 | 0.6574 | 0.2529 | 0.3863 | 1 | 0.1173 | 0.2934 | 0.3883 | 0.3883 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
507 | 100 | 170.8 | 65 | 66.5 | 1.9 | 451.2 | 2500 | 58 | 20 | 76.1 | 79.5 | 73.8 | 85.3 | 35.5 | 14 | 8970.6 | 9298.5 | 8744.9 | 16696.3 | 18023.1 | 16814.8 | 1.861 | 1.938 | 1.923 | 0.56 | 0.538 | 0.551 | 2.88 | -2.58 | 2.54 | 0.541 | 0.508 | 0.5 | -3.2 | 2 | 2.26 | 0.5 | 0.533 | 0.5 | 2.22 | 2.21 | 2 | 0.519 | 0.581 | 0.5 | -2.19 | 2.79 | 2.92 | Good_Mixed | 8744.9 | 16696.3 | 1.861 | 0.56 | 2.88 | 0.581 | 3.2 | 0.8788 | 1 | 0.8612 | 0.9194 | 1 | 0.8105 | 0.8875 | 0.905 | 0.905 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
508 | 796.8 | 506.3 | 93 | 109.6 | 14.3 | 770.5 | 5108.1 | 49 | 32.1 | 89.4 | 86.4 | 81 | 97.9 | 40 | 22.3 | 6516.7 | 6273.8 | 5425.4 | 10661.7 | 9907.4 | 8268.8 | 1.636 | 1.579 | 1.524 | 0.712 | 0.648 | 0.692 | 5.63 | 4.93 | 5.2 | 0.684 | 0.666 | 0.639 | 4.93 | 5.33 | 3.96 | 0.671 | 0.615 | 0.606 | 4.75 | 4.39 | 3.98 | 0.617 | 0.728 | 0.61 | -4.65 | 4.58 | 4.34 | Poor_Mixed | 5425.4 | 8268.8 | 1.524 | 0.712 | 5.63 | 0.728 | 5.33 | 0.4955 | 0.7691 | 0.5579 | 0.6719 | 1 | 0.4907 | 0.5243 | 0.6286 | 0.6286 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
509 | 498.7 | 284.6 | 82.3 | 135.9 | 44.3 | 595.3 | 4007.3 | 53 | 27.9 | 108.2 | 106.5 | 92.4 | 116 | 44.4 | 13.5 | 8258.6 | 7448.6 | 6867.1 | 14924.8 | 13169.5 | 11209.2 | 1.807 | 1.768 | 1.632 | 0.558 | 0.562 | 0.558 | -2.26 | -2.72 | 2.59 | 0.547 | 0.537 | 0.55 | 4.22 | 3.16 | -3.1 | 0.572 | 0.579 | 0.607 | 3.72 | 3.71 | 2.58 | 0.524 | 0.56 | 0.543 | 3.99 | -3.08 | 3.02 | Critical_Thermal | 6867.1 | 11209.2 | 1.632 | 0.562 | 2.72 | 0.607 | 4.22 | 0.451 | 0.825 | 0.1333 | 0.9318 | 1 | 0.8056 | 0.7175 | 0.6736 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
510 | 860.7 | 476.4 | 101.9 | 117.7 | 14.8 | 760.3 | 6112.3 | 46.3 | 36.5 | 94.9 | 91.8 | 85.5 | 100.7 | 41.2 | 26.1 | 6159.6 | 5995.3 | 6557.4 | 9724.3 | 9327.9 | 9932.8 | 1.579 | 1.556 | 1.515 | 0.744 | 0.703 | 0.794 | -5.77 | -6.06 | 6.17 | 0.682 | 0.676 | 0.674 | 4.97 | 4.19 | 3.82 | 0.669 | 0.712 | 0.736 | 6.52 | 4.76 | -5.86 | 0.677 | 0.713 | 0.723 | 6.73 | 5.26 | 4.39 | Poor_Mixed | 5995.3 | 9327.9 | 1.515 | 0.794 | 6.17 | 0.736 | 6.73 | 0.4667 | 0.7175 | 0.4361 | 0.5407 | 1 | 0.3925 | 0.4409 | 0.5677 | 0.5677 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
511 | 806.1 | 453.8 | 101.8 | 120.7 | 19.8 | 804.7 | 5496.6 | 45.9 | 34.4 | 90.5 | 92.1 | 82.5 | 98 | 39.3 | 24.8 | 5694 | 5841.3 | 5441.8 | 9247.4 | 9011.2 | 8415.5 | 1.624 | 1.543 | 1.546 | 0.738 | 0.712 | 0.794 | 5.38 | 5.09 | 6.28 | 0.675 | 0.663 | 0.708 | 5.31 | 4.61 | 4.44 | 0.735 | 0.629 | 0.735 | -5.16 | 4.31 | 3.84 | 0.711 | 0.716 | 0.655 | 5.94 | 4.91 | 3.84 | Poor_Mixed | 5441.8 | 8415.5 | 1.543 | 0.794 | 6.28 | 0.735 | 5.94 | 0.44 | 0.7414 | 0.5066 | 0.5865 | 1 | 0.4148 | 0.463 | 0.5803 | 0.5803 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
512 | 773.9 | 524.4 | 105.8 | 109.6 | 14.5 | 810.8 | 5118 | 46.1 | 33.9 | 92.1 | 91.5 | 85.2 | 98.3 | 40.1 | 25 | 5588.9 | 5994.7 | 6225.2 | 8859.1 | 8976.3 | 9430.1 | 1.585 | 1.497 | 1.515 | 0.733 | 0.677 | 0.73 | 5.85 | -5.01 | -5.82 | 0.648 | 0.745 | 0.664 | 3.9 | 5.92 | 4.38 | 0.666 | 0.665 | 0.651 | 4.01 | 5.65 | 5.64 | 0.776 | 0.672 | 0.747 | 4.39 | 5.72 | 5.62 | Poor_Mixed | 5588.9 | 8859.1 | 1.497 | 0.733 | 5.85 | 0.776 | 5.92 | 0.4797 | 0.7473 | 0.4767 | 0.5796 | 1 | 0.4461 | 0.4514 | 0.5899 | 0.5899 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
513 | 760.9 | 528.1 | 103.6 | 117.7 | 15.8 | 828.4 | 4860.1 | 46.2 | 33.7 | 91.1 | 88.9 | 82.1 | 99.2 | 40.8 | 24.8 | 5582.6 | 5628.9 | 5156.8 | 8650.2 | 7993.9 | 7704.2 | 1.549 | 1.42 | 1.494 | 0.756 | 0.751 | 0.723 | -5.79 | 5.9 | 6.09 | 0.674 | 0.611 | 0.752 | 4.48 | 5.01 | 5.1 | 0.68 | 0.739 | 0.729 | 4.82 | 4.65 | 4.36 | 0.707 | 0.692 | 0.761 | 3.76 | 4.21 | 4.23 | Poor_Mixed | 5156.8 | 7704.2 | 1.42 | 0.756 | 6.09 | 0.761 | 5.1 | 0.4653 | 0.7497 | 0.5106 | 0.5865 | 1 | 0.3989 | 0.4556 | 0.5845 | 0.5845 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
514 | 1001.8 | 602.1 | 104.2 | 123.4 | 18.4 | 931.4 | 6547.8 | 56.3 | 21.5 | 78.2 | 78.8 | 74.4 | 85.5 | 35.8 | 12.9 | 8571.9 | 8566.7 | 9853.7 | 15584.6 | 15853.2 | 19499.4 | 1.818 | 1.851 | 1.979 | 0.541 | 0.5 | 0.557 | 2.75 | -2.42 | 3.13 | 0.54 | 0.527 | 0.544 | 2 | -2.59 | 2.14 | 0.5 | 0.5 | 0.503 | 2 | -2 | 2.14 | 0.526 | 0.511 | 0.52 | 2.1 | 2 | -2 | Poor_DGA | 8566.7 | 15584.6 | 1.818 | 0.557 | 3.13 | 0.544 | 2.59 | 0.3849 | 0.9406 | 0.8376 | 0.9461 | 1 | 0.849 | 0.8941 | 0.7799 | 0.7799 | Fair | 1 | 1 | DGA | 0 |  | C2H2
515 | 466.6 | 341.2 | 90.7 | 79.7 | 12.6 | 693.9 | 4416.9 | 49.3 | 29.3 | 82.9 | 82.7 | 78.3 | 91.1 | 38.7 | 18.2 | 7760.3 | 8139.9 | 6960.3 | 13776.2 | 13726.3 | 12210.9 | 1.775 | 1.686 | 1.754 | 0.733 | 0.631 | 0.753 | 5.32 | 3.68 | 5.57 | 0.606 | 0.666 | 0.58 | 3.69 | 2.36 | -3.36 | 0.561 | 0.554 | 0.587 | 3.86 | 3.58 | 3.9 | 0.529 | 0.562 | 0.58 | 3.92 | -3.13 | -4.36 | Fair_Mixed | 6960.3 | 12210.9 | 1.686 | 0.753 | 5.57 | 0.666 | 4.36 | 0.6052 | 0.8054 | 0.6921 | 0.8024 | 1 | 0.4962 | 0.669 | 0.7072 | 0.7072 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
516 | 232.4 | 243.2 | 72.9 | 77.6 | 1 | 449.2 | 3170.7 | 58.1 | 22.9 | 84.3 | 125.3 | 79.7 | 91.8 | 37.5 | 14.3 | 8718.6 | 9115.5 | 10000 | 16399.1 | 17280.7 | 19837 | 1.881 | 1.896 | 1.984 | 0.976 | 0.944 | 0.96 | 9.43 | 8.49 | 9.31 | 0.549 | 0.51 | 0.515 | 2.53 | 2.64 | 2.78 | 0.541 | 0.566 | 0.54 | 2.47 | -2.18 | -2.39 | 0.566 | 0.534 | 0.534 | 2 | -2.87 | 2.87 | Critical_Winding_TD_Cap | 8718.6 | 16399.1 | 1.881 | 0.976 | 9.43 | 0.566 | 2.87 | 0.8954 | 0.9088 | 0.5058 | 0.9118 | 1 | 0.0722 | 0.7997 | 0.7431 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | WTI_LV
517 | 810.7 | 485 | 98.8 | 101.5 | 16.8 | 766.2 | 5526.2 | 47.6 | 33.9 | 85.7 | 88.8 | 78.7 | 93.5 | 38 | 24.2 | 4977.2 | 5732.9 | 5452.6 | 7063.6 | 8491.1 | 8342.7 | 1.419 | 1.481 | 1.53 | 0.701 | 0.708 | 0.685 | -5.31 | -5.35 | -4.77 | 0.687 | 0.68 | 0.674 | 4.66 | 4.61 | 3.5 | 0.692 | 0.723 | 0.64 | 3.77 | 4.82 | 4.73 | 0.641 | 0.677 | 0.609 | 4.25 | 4.08 | 3.67 | Poor_Mixed | 4977.2 | 7063.6 | 1.419 | 0.708 | 5.35 | 0.723 | 4.82 | 0.4805 | 0.7473 | 0.6165 | 0.6074 | 1 | 0.483 | 0.5084 | 0.621 | 0.621 | Fair | 1 | 1 | DGA | 0 |  | C2H2
518 | 1033.2 | 563.3 | 109 | 113.7 | 24 | 957.6 | 5525.8 | 45.1 | 35.4 | 92.7 | 92.4 | 79.9 | 98.8 | 38.8 | 22.3 | 5656 | 4302.6 | 5511.4 | 8640.7 | 6347.2 | 8647.9 | 1.528 | 1.475 | 1.569 | 0.763 | 0.693 | 0.733 | 6.54 | 5.51 | 5.3 | 0.655 | 0.624 | 0.707 | 5.47 | 5.05 | 3.96 | 0.663 | 0.662 | 0.661 | 6.33 | 4.28 | 5.79 | 0.718 | 0.6 | 0.721 | 6.23 | 5.4 | 5.82 | Poor_Mixed | 4302.6 | 6347.2 | 1.475 | 0.763 | 6.54 | 0.721 | 6.33 | 0.3692 | 0.7299 | 0.5064 | 0.6719 | 1 | 0.4194 | 0.4691 | 0.5673 | 0.5673 | Poor | 0 | 1 | DGA | 0 |  | C2H2
519 | 1571.9 | 891.7 | 139.6 | 180.9 | 34.3 | 1192.9 | 7194.2 | 36.3 | 44.8 | 104.7 | 103 | 92.6 | 115.4 | 44.2 | 33.4 | 2413.8 | 2181.9 | 2589.1 | 2585.8 | 2360.8 | 2986.1 | 1.071 | 1.082 | 1.153 | 0.937 | 0.881 | 0.983 | 9.64 | 8.95 | 9.84 | 0.751 | 0.804 | 0.884 | 7.57 | 5.62 | 9.37 | 0.775 | 0.961 | 0.923 | 7.76 | -6.55 | -8.94 | 0.968 | 0.736 | 0.856 | 7.73 | 5.92 | -8.75 | Very Poor_Mixed | 2181.9 | 2360.8 | 1.071 | 0.983 | 9.84 | 0.968 | 9.37 | 0.1148 | 0.6318 | 0.1754 | 0.267 | 1 | 0.0704 | 0.2041 | 0.342 | 0.342 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
520 | 182.5 | 129.4 | 71.1 | 51.5 | 2.5 | 395.8 | 3065.8 | 59 | 23.8 | 75.2 | 81.7 | 71.9 | 81.7 | 36.1 | 15.3 | 8465.3 | 9001.4 | 10000 | 15645.8 | 17874.6 | 20000 | 1.848 | 1.986 | 2 | 0.508 | 0.539 | 0.555 | 2.62 | 2.9 | 3.12 | 0.502 | 0.522 | 0.518 | -2 | 2 | -2.22 | 0.528 | 0.5 | 0.519 | 2.29 | 2 | -2.45 | 0.5 | 0.5 | 0.52 | 2 | -2.53 | 2.59 | Good_Mixed | 8465.3 | 15645.8 | 1.848 | 0.555 | 3.12 | 0.528 | 2.59 | 0.8876 | 0.8912 | 0.8876 | 0.8855 | 1 | 0.8281 | 0.9123 | 0.902 | 0.902 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
521 | 1676.3 | 969.3 | 142.3 | 190 | 34.3 | 1279.1 | 8248.7 | 35.9 | 45.4 | 105.5 | 107 | 94.5 | 116.2 | 44.2 | 33.2 | 1153.7 | 1122.9 | 896.7 | 1211.4 | 1200 | 1200 | 1.05 | 1.069 | 1.338 | 0.936 | 0.939 | 0.985 | 9.13 | 9.66 | 9.38 | 0.903 | 0.873 | 0.879 | -5.62 | 8.41 | 5.47 | 0.947 | 0.859 | 0.903 | 9.35 | 7.13 | 4.94 | 0.84 | 0.781 | 0.848 | 6.3 | -8.08 | -6.16 | Very Poor_Mixed | 896.7 | 1200 | 1.05 | 0.985 | 9.66 | 0.947 | 9.35 | 0.0665 | 0.6261 | 0.1341 | 0.2748 | 1 | 0.061 | 0.2087 | 0.325 | 0.325 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
522 | 966.7 | 527.1 | 107.2 | 123 | 21 | 832.9 | 5556.9 | 47.2 | 32 | 92.2 | 92.4 | 82.4 | 99.7 | 39.9 | 25.7 | 6797.6 | 7262.3 | 7959.2 | 11294.6 | 11865.2 | 13524.1 | 1.662 | 1.634 | 1.699 | 0.752 | 0.701 | 0.739 | 5.96 | 5.01 | 5.39 | 0.591 | 0.623 | 0.542 | 5.36 | 4.09 | -4.02 | 0.639 | 0.639 | 0.684 | 4.52 | -5.23 | -5.67 | 0.629 | 0.659 | 0.634 | 4.95 | 4.58 | 5.26 | Poor_Mixed | 6797.6 | 11294.6 | 1.634 | 0.752 | 5.96 | 0.684 | 5.67 | 0.4019 | 0.7703 | 0.482 | 0.5549 | 1 | 0.4364 | 0.5447 | 0.588 | 0.588 | Poor | 0 | 1 | DGA | 0 |  | C2H2
523 | 1048.3 | 563.5 | 103.9 | 134.9 | 19.5 | 951.8 | 5875.4 | 55 | 22 | 76.2 | 75 | 71.3 | 80.7 | 35 | 12 | 10000 | 8946.5 | 9254.8 | 19429.2 | 17361.6 | 17233.1 | 1.943 | 1.941 | 1.862 | 0.611 | 0.627 | 0.588 | -3.91 | -3.54 | -3.63 | 0.5 | 0.519 | 0.524 | 2 | 2 | -2.01 | 0.5 | 0.5 | 0.507 | 2.44 | 2.02 | -2.38 | 0.541 | 0.527 | 0.545 | -2.58 | 2.27 | 2.39 | Poor_DGA | 8946.5 | 17233.1 | 1.862 | 0.627 | 3.91 | 0.545 | 2.58 | 0.3735 | 0.9283 | 0.9603 | 0.9661 | 1 | 0.6622 | 0.8932 | 0.7626 | 0.7626 | Fair | 1 | 1 | DGA | 0 |  | C2H2
524 | 100 | 174.8 | 66.1 | 50 | 2.1 | 497.4 | 3271.6 | 58 | 21.8 | 77.1 | 75 | 71 | 80 | 35 | 10.5 | 10000 | 9268.5 | 10000 | 19121.9 | 18197.3 | 20000 | 1.912 | 1.963 | 2 | 0.517 | 0.5 | 0.512 | -2.03 | -2.48 | 2 | 0.501 | 0.516 | 0.521 | -2.61 | 2.62 | -2.1 | 0.5 | 0.527 | 0.5 | 2.06 | 2 | 2 | 0.51 | 0.5 | 0.507 | 2.06 | 2 | 2 | Good_Mixed | 9268.5 | 18197.3 | 1.912 | 0.517 | 2.48 | 0.527 | 2.62 | 0.8913 | 0.9331 | 0.9565 | 0.994 | 1 | 0.942 | 0.9291 | 0.9393 | 0.9393 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
525 | 670.5 | 370.2 | 86.3 | 94.7 | 10.5 | 636.2 | 4165.9 | 51.4 | 29.3 | 85 | 88.2 | 78 | 92.2 | 38.1 | 20.4 | 7511.6 | 7339.4 | 7643.9 | 12514.4 | 12703.3 | 13208.9 | 1.666 | 1.731 | 1.728 | 0.619 | 0.646 | 0.62 | -4.01 | -4.02 | 4.45 | 0.581 | 0.601 | 0.633 | -4.77 | 3.45 | -4.67 | 0.72 | 0.58 | 0.591 | 4.17 | -3.71 | -3.11 | 0.577 | 0.594 | 0.617 | 4.93 | 4.03 | 4.8 | Fair_Mixed | 7339.4 | 12514.4 | 1.666 | 0.646 | 4.45 | 0.72 | 4.93 | 0.5974 | 0.8054 | 0.6364 | 0.734 | 1 | 0.6109 | 0.594 | 0.6988 | 0.6988 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
526 | 1602.4 | 899.1 | 143.7 | 190.1 | 34.3 | 1316.5 | 8639.8 | 32.8 | 45.8 | 104.8 | 102.6 | 92.6 | 112.9 | 43.5 | 32.9 | 2491.9 | 858 | 2490.7 | 3107.1 | 1200 | 2902.3 | 1.247 | 1.399 | 1.165 | 0.99 | 0.946 | 0.986 | 9.61 | -9.42 | 9.84 | 0.695 | 0.888 | 0.745 | 7.63 | 8.46 | 5 | 0.9 | 0.88 | 0.76 | 8.98 | 6.19 | 8.3 | 0.711 | 0.877 | 0.948 | 5.71 | 7.26 | -8.12 | Very Poor_Mixed | 858 | 1200 | 1.165 | 0.99 | 9.84 | 0.948 | 8.98 | 0.0689 | 0.6222 | 0.1947 | 0.2865 | 1 | 0.0357 | 0.2408 | 0.334 | 0.334 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
527 | 1524 | 837 | 134.1 | 181.8 | 30.2 | 1171.7 | 8046.6 | 35.4 | 43.3 | 107.6 | 104.1 | 92.3 | 115.6 | 44.2 | 31.5 | 1980.6 | 1439.7 | 1713.4 | 2427.9 | 1721.1 | 2143.7 | 1.226 | 1.195 | 1.251 | 0.92 | 0.893 | 0.895 | -8.2 | 7.68 | 8.6 | 0.871 | 0.853 | 0.732 | 8.53 | 6.35 | -6.49 | 0.729 | 0.814 | 0.91 | -7.15 | 7.79 | 8.49 | 0.723 | 0.899 | 0.929 | 7.34 | -8.51 | 7.44 | Very Poor_Mixed | 1439.7 | 1721.1 | 1.195 | 0.92 | 8.6 | 0.929 | 8.53 | 0.1376 | 0.6465 | 0.1539 | 0.3406 | 1 | 0.1579 | 0.2241 | 0.3668 | 0.3668 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
528 | 1591.8 | 912.1 | 137.7 | 182.5 | 29.5 | 1244.8 | 7697.3 | 32.2 | 47.5 | 108.9 | 109.3 | 95.3 | 118 | 45.5 | 33.6 | 1587.1 | 2438.6 | 2818.2 | 1666.4 | 2782.7 | 3391.5 | 1.05 | 1.141 | 1.203 | 0.939 | 0.99 | 0.949 | -9.12 | 9.5 | 9.7 | 0.804 | 0.766 | 0.902 | 6.29 | 6.14 | 7.48 | 0.918 | 0.898 | 0.873 | 5.71 | -9.16 | 6.91 | 0.846 | 0.689 | 0.799 | -8.47 | 6.67 | 8.06 | Very Poor_Mixed | 1587.1 | 1666.4 | 1.05 | 0.99 | 9.7 | 0.918 | 9.16 | 0.1208 | 0.6062 | 0.08 | 0.2591 | 1 | 0.0545 | 0.2318 | 0.3333 | 0.3333 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
529 | 275.2 | 207.6 | 70.5 | 61.2 | 1 | 374.4 | 2857.4 | 60 | 23.9 | 75 | 75 | 71 | 80.6 | 35 | 10.1 | 9072.9 | 9021.1 | 8929.2 | 18091.7 | 17609.2 | 17684 | 1.994 | 1.952 | 1.98 | 0.508 | 0.552 | 0.541 | -2.22 | 2.78 | -3.04 | 0.507 | 0.513 | 0.554 | 3.14 | 2.29 | 3.2 | 0.521 | 0.531 | 0.517 | 2.15 | 2.76 | -2.75 | 0.5 | 0.606 | 0.513 | 2 | 4.41 | 2.31 | Fair_Bushing_TD_Cap | 8929.2 | 17609.2 | 1.952 | 0.552 | 3.04 | 0.606 | 4.41 | 0.9349 | 0.8894 | 0.9838 | 0.9992 | 1 | 0.8433 | 0.8297 | 0.9162 | 0.9162 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
530 | 281.4 | 162.1 | 73.1 | 50 | 1.8 | 410.3 | 2725.7 | 57.4 | 22.1 | 77.7 | 77.5 | 70.9 | 82.1 | 35 | 11.9 | 4506.4 | 3817.6 | 4449.2 | 6356.2 | 5264.3 | 5932 | 1.41 | 1.379 | 1.333 | 0.675 | 0.583 | 0.621 | 4.79 | -3.33 | 3.72 | 0.556 | 0.524 | 0.537 | 2.2 | 2.64 | 2.66 | 0.506 | 0.5 | 0.5 | -3.03 | 2.37 | -2 | 0.5 | 0.5 | 0.509 | 2.47 | 2 | -2 | Poor_IR_PI | 3817.6 | 5264.3 | 1.333 | 0.675 | 4.79 | 0.556 | 3.03 | 0.8954 | 0.926 | 0.9063 | 0.9682 | 1 | 0.6291 | 0.9046 | 0.8849 | 0.8849 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
531 | 834.9 | 586.3 | 109.4 | 121.2 | 20.3 | 799.7 | 5675.1 | 45.4 | 35.2 | 92.6 | 92.3 | 85 | 100.1 | 40.1 | 24.7 | 6114.8 | 4895.6 | 4223.6 | 9725.6 | 7842.6 | 5947.1 | 1.591 | 1.602 | 1.408 | 0.695 | 0.754 | 0.71 | 5.89 | -5.97 | -6.02 | 0.637 | 0.635 | 0.721 | -5.83 | 4.07 | 3.93 | 0.613 | 0.691 | 0.619 | 3.12 | 5.01 | -3.55 | 0.609 | 0.608 | 0.622 | 2.78 | 3.94 | 4.86 | Poor_Mixed | 4223.6 | 5947.1 | 1.408 | 0.754 | 6.02 | 0.721 | 5.83 | 0.4126 | 0.7322 | 0.4606 | 0.59 | 1 | 0.4181 | 0.5538 | 0.5848 | 0.5848 | Poor | 0 | 1 | DGA | 0 |  | C2H2
532 | 428.4 | 348.1 | 80 | 74.8 | 9.5 | 573.2 | 3604.5 | 53 | 25.5 | 85.9 | 84.3 | 76.6 | 90.3 | 38.2 | 18.4 | 8519.6 | 8311.1 | 8469.6 | 15733.6 | 15420 | 15437 | 1.847 | 1.855 | 1.823 | 0.502 | 0.522 | 0.541 | 2.25 | 2.76 | -2.36 | 0.6 | 0.592 | 0.566 | -4.24 | 2.95 | 3.02 | 0.605 | 0.604 | 0.633 | 4.08 | 4.05 | 2.96 | 0.578 | 0.615 | 0.644 | 3.04 | -4.63 | 3.99 | Fair_Mixed | 8311.1 | 15420 | 1.823 | 0.541 | 2.76 | 0.644 | 4.63 | 0.6699 | 0.8617 | 0.6765 | 0.7963 | 1 | 0.8861 | 0.6222 | 0.7744 | 0.7744 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
533 | 799 | 536.9 | 105.9 | 118.6 | 17.7 | 876.8 | 5620.1 | 44.1 | 32.4 | 93.2 | 87.6 | 79.1 | 99.4 | 40.3 | 23.2 | 5721.9 | 5482.6 | 6026.3 | 8934.3 | 8465.2 | 9847 | 1.561 | 1.544 | 1.634 | 0.67 | 0.749 | 0.741 | -5.03 | -5.97 | 5.41 | 0.671 | 0.64 | 0.648 | -3.58 | 4.4 | -3.54 | 0.634 | 0.582 | 0.649 | 4.27 | -4.63 | 3.92 | 0.61 | 0.637 | 0.649 | 3.74 | -3.82 | 5.29 | Poor_Mixed | 5482.6 | 8465.2 | 1.544 | 0.749 | 5.97 | 0.671 | 5.29 | 0.4327 | 0.7654 | 0.528 | 0.6416 | 1 | 0.4457 | 0.5564 | 0.6074 | 0.6074 | Fair | 1 | 1 | DGA | 0 |  | C2H2
534 | 237.8 | 120 | 74.9 | 66.4 | 4.6 | 442.4 | 3264.6 | 59 | 23.3 | 82.3 | 79.1 | 72.1 | 87.3 | 36.3 | 11.4 | 8355.4 | 9487 | 9039.1 | 15711 | 18974 | 16682.7 | 1.88 | 2 | 1.846 | 0.728 | 0.712 | 0.715 | 6 | 5.81 | 5.89 | 0.527 | 0.542 | 0.522 | 2.56 | 2.19 | 3.16 | 0.51 | 0.532 | 0.506 | 2.28 | 2.11 | 3.21 | 0.531 | 0.508 | 0.554 | -2.13 | 2 | 2 | Poor_Winding_TD_Cap | 8355.4 | 15711 | 1.846 | 0.728 | 6 | 0.554 | 3.21 | 0.8078 | 0.9008 | 0.8071 | 0.9783 | 1 | 0.4221 | 0.8451 | 0.8109 | 0.8109 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
535 | 855.5 | 502 | 105 | 115 | 15.8 | 911.7 | 5719.4 | 48.8 | 32 | 90.3 | 90.5 | 82.1 | 95.9 | 40.4 | 24.7 | 6004.9 | 4986.6 | 4709.6 | 9673.3 | 7440.8 | 6619 | 1.611 | 1.492 | 1.405 | 0.683 | 0.783 | 0.715 | 5.6 | 5.81 | 5.5 | 0.648 | 0.593 | 0.698 | 4.22 | 3.94 | 5.23 | 0.703 | 0.629 | 0.636 | -3.85 | 4.74 | 4.59 | 0.675 | 0.627 | 0.633 | 4.61 | -4.68 | 5.89 | Poor_Mixed | 4709.6 | 6619 | 1.405 | 0.783 | 5.81 | 0.703 | 5.89 | 0.4433 | 0.7703 | 0.5243 | 0.59 | 1 | 0.4302 | 0.5195 | 0.5989 | 0.5989 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
536 | 262.3 | 218 | 78 | 62.5 | 6.1 | 451.7 | 3792.8 | 55.3 | 25.9 | 82.4 | 81.1 | 73.7 | 86.7 | 36.9 | 15.4 | 9523.9 | 7766.9 | 9535.9 | 18602.3 | 13868.8 | 17668.1 | 1.953 | 1.786 | 1.853 | 0.59 | 0.592 | 0.658 | 3.2 | -3.73 | 4.48 | 0.548 | 0.541 | 0.559 | 2.64 | 2.73 | 3.15 | 0.589 | 0.568 | 0.627 | -3.28 | -3.13 | -2.43 | 0.537 | 0.552 | 0.591 | 2.56 | 3.05 | 3.42 | Fair_Mixed | 7766.9 | 13868.8 | 1.786 | 0.658 | 4.48 | 0.627 | 3.42 | 0.7715 | 0.8552 | 0.7752 | 0.8828 | 1 | 0.6519 | 0.7176 | 0.7976 | 0.7976 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
537 | 455.7 | 322.6 | 89.3 | 144.2 | 49 | 631.8 | 4064 | 55.5 | 26.7 | 103.1 | 103.1 | 92.3 | 116 | 42.9 | 15.5 | 6305.4 | 6526.9 | 7922.9 | 10135.5 | 11320.6 | 14342.7 | 1.607 | 1.734 | 1.81 | 0.709 | 0.618 | 0.592 | 4.54 | -3.49 | 3.65 | 0.601 | 0.528 | 0.595 | 2.98 | 3.22 | 3.18 | 0.557 | 0.55 | 0.508 | 3.8 | 3.1 | 4.2 | 0.66 | 0.557 | 0.59 | 3.63 | 2.99 | 3.74 | Critical_Thermal | 6305.4 | 10135.5 | 1.607 | 0.709 | 4.54 | 0.66 | 4.2 | 0.4326 | 0.8427 | 0.1918 | 0.88 | 1 | 0.6185 | 0.6967 | 0.6445 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
538 | 868.2 | 563.3 | 109.7 | 123.5 | 19.1 | 810.3 | 5365 | 44.3 | 35.6 | 93.3 | 92.3 | 81.4 | 98.5 | 38.9 | 24.7 | 6492.7 | 5425.6 | 6455.7 | 10665.4 | 8195.3 | 10988.3 | 1.643 | 1.51 | 1.702 | 0.808 | 0.702 | 0.691 | 6.28 | -5.83 | 5.6 | 0.721 | 0.719 | 0.755 | 4.33 | 4.44 | -4.34 | 0.628 | 0.725 | 0.667 | 5.2 | 4.28 | -5.31 | 0.602 | 0.654 | 0.644 | 5.18 | 4.72 | 4.79 | Poor_Mixed | 5425.6 | 8195.3 | 1.51 | 0.808 | 6.28 | 0.755 | 5.31 | 0.4191 | 0.7276 | 0.4943 | 0.59 | 1 | 0.4104 | 0.4786 | 0.5746 | 0.5746 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
539 | 865.8 | 479.1 | 101.8 | 120.2 | 19.3 | 831.7 | 6191.9 | 45.3 | 33.1 | 90.8 | 88.9 | 83.3 | 97 | 40 | 24.7 | 5236.1 | 5557.4 | 5975.6 | 8069 | 8397.4 | 9420.2 | 1.541 | 1.511 | 1.576 | 0.721 | 0.708 | 0.737 | -5.36 | 5.21 | 5.74 | 0.653 | 0.654 | 0.689 | 4.32 | 5.54 | 3.04 | 0.706 | 0.643 | 0.672 | -6.48 | -5.02 | 5.3 | 0.702 | 0.654 | 0.655 | 4.87 | 5.48 | 5.65 | Poor_Mixed | 5236.1 | 8069 | 1.511 | 0.737 | 5.74 | 0.706 | 6.48 | 0.4249 | 0.7568 | 0.5212 | 0.59 | 1 | 0.4446 | 0.4758 | 0.5866 | 0.5866 | Poor | 0 | 1 | DGA | 0 |  | C2H2
540 | 284.3 | 198.7 | 72.8 | 70.1 | 1.7 | 507.9 | 3215.7 | 57.6 | 23.2 | 75 | 78.4 | 70.9 | 80 | 35 | 13.2 | 8552.4 | 7317.6 | 8184.7 | 16467.6 | 13110.2 | 15337.5 | 1.925 | 1.792 | 1.874 | 0.86 | 0.845 | 0.777 | 7.68 | 7.46 | 6.76 | 0.512 | 0.539 | 0.585 | 2.35 | 2.82 | -2.56 | 0.501 | 0.58 | 0.549 | 2.78 | 2.05 | 2.61 | 0.522 | 0.557 | 0.509 | 2.65 | 2.63 | 2 | Poor_Winding_TD_Cap | 7317.6 | 13110.2 | 1.792 | 0.86 | 7.68 | 0.585 | 2.82 | 0.8396 | 0.9027 | 0.9444 | 0.939 | 1 | 0.2581 | 0.8119 | 0.8019 | 0.8019 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
541 | 362.6 | 323.8 | 95.8 | 96.3 | 7.1 | 574.9 | 3862.2 | 52.7 | 23.1 | 80.5 | 82.7 | 73.5 | 87.3 | 36.9 | 15.7 | 8541.2 | 7837.6 | 8969.2 | 15788.8 | 13894.8 | 16508 | 1.849 | 1.773 | 1.841 | 0.553 | 0.63 | 0.593 | -2.71 | 3.32 | 3.27 | 0.544 | 0.52 | 0.607 | -3.49 | 3.55 | 2.86 | 0.59 | 0.586 | 0.52 | 2.01 | 3.35 | -3.52 | 0.553 | 0.541 | 0.564 | -2.98 | 2.92 | 2.99 | Fair_Mixed | 7837.6 | 13894.8 | 1.773 | 0.63 | 3.32 | 0.607 | 3.55 | 0.665 | 0.9047 | 0.7766 | 0.8746 | 1 | 0.7233 | 0.7339 | 0.7896 | 0.7896 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
542 | 1766 | 982.4 | 146.5 | 197 | 60.6 | 1307.8 | 9111.8 | 56.7 | 25 | 77.3 | 75.8 | 70.2 | 84.4 | 35.7 | 15.8 | 8865.4 | 9989.7 | 8888.7 | 16896.4 | 19942.2 | 16816.7 | 1.906 | 1.996 | 1.892 | 0.552 | 0.5 | 0.527 | 2.51 | 2.45 | -2.21 | 0.545 | 0.51 | 0.561 | 2.95 | 2.24 | 2.17 | 0.563 | 0.535 | 0.523 | 2.37 | 2.24 | -2.97 | 0.532 | 0.533 | 0.5 | 2.21 | 2.39 | -2.64 | Critical_DGA | 8865.4 | 16816.7 | 1.892 | 0.552 | 2.51 | 0.563 | 2.97 | 0.032 | 0.87 | 0.9247 | 0.8718 | 1 | 0.8878 | 0.8242 | 0.6811 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
543 | 1622.1 | 894.9 | 137.2 | 180.2 | 26 | 1160.8 | 7850.8 | 34.4 | 47.5 | 106.1 | 107.6 | 93.6 | 113.7 | 44.4 | 34 | 2039.5 | 1335 | 1826.3 | 2331.8 | 1577 | 1948.4 | 1.143 | 1.181 | 1.067 | 0.948 | 0.954 | 0.946 | 8.85 | 9.31 | 8.79 | 0.687 | 0.859 | 0.911 | -6.44 | 6.25 | 5.27 | 0.864 | 0.858 | 0.925 | 9.01 | 7.29 | 8.18 | 0.891 | 0.848 | 0.707 | 8.88 | -6.75 | 6.92 | Very Poor_Mixed | 1335 | 1577 | 1.067 | 0.954 | 9.31 | 0.925 | 9.01 | 0.1471 | 0.6062 | 0.1435 | 0.2434 | 1 | 0.084 | 0.227 | 0.3487 | 0.3487 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
544 | 1551.9 | 773.9 | 131.8 | 185.1 | 27.9 | 1217.2 | 8071.5 | 35.8 | 47.4 | 107.2 | 107.6 | 94.9 | 112.9 | 44 | 31.6 | 2056.9 | 1062.6 | 1642.7 | 2326.2 | 1200 | 1904.5 | 1.131 | 1.129 | 1.159 | 0.911 | 0.926 | 0.929 | 8.78 | 8.79 | 9.23 | 0.875 | 0.886 | 0.752 | 7.7 | 7.32 | -8.66 | 0.742 | 0.742 | 0.837 | -8.04 | 7.31 | 7.45 | 0.689 | 0.913 | 0.887 | -5.97 | 7.68 | 8.14 | Very Poor_Mixed | 1062.6 | 1200 | 1.129 | 0.929 | 9.23 | 0.913 | 8.66 | 0.1471 | 0.6072 | 0.1372 | 0.3368 | 1 | 0.1051 | 0.2379 | 0.3577 | 0.3577 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
545 | 1738.4 | 945.3 | 140 | 184.5 | 34.3 | 1291.1 | 8854.9 | 15.1 | 25.8 | 80.1 | 79.2 | 74.3 | 88.6 | 36 | 14 | 8541.2 | 9598.8 | 9858.8 | 16355.8 | 17873.9 | 19227.7 | 1.915 | 1.862 | 1.95 | 0.553 | 0.518 | 0.573 | 3.26 | 2.28 | -2.35 | 0.536 | 0.567 | 0.515 | 2.42 | 3.04 | 3.57 | 0.531 | 0.55 | 0.58 | 2.35 | -3.52 | 3.59 | 0.6 | 0.605 | 0.55 | -3.34 | 3.02 | 2.77 | Critical_DGA | 8541.2 | 16355.8 | 1.862 | 0.573 | 3.26 | 0.605 | 3.59 | 0.0616 | 0.2735 | 0.8009 | 0.9194 | 1 | 0.821 | 0.7315 | 0.5809 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
546 | 1472.8 | 908.8 | 141.1 | 188.1 | 28.9 | 1200.6 | 8209.8 | 34.2 | 45 | 105.6 | 107.2 | 93.4 | 114.6 | 44.2 | 30.7 | 1543.5 | 3299.7 | 2845.1 | 1841.8 | 4194 | 3475.6 | 1.193 | 1.271 | 1.222 | 0.89 | 0.931 | 0.913 | 9.09 | 8.79 | 9.23 | 0.733 | 0.825 | 0.704 | 6.21 | -7.23 | 5.81 | 0.718 | 0.786 | 0.894 | 5.99 | 7.69 | -5.28 | 0.794 | 0.882 | 0.832 | 7.64 | 7.28 | 8.63 | Very Poor_Mixed | 1543.5 | 1841.8 | 1.193 | 0.931 | 9.23 | 0.894 | 8.63 | 0.1235 | 0.6299 | 0.1465 | 0.3711 | 1 | 0.1073 | 0.2774 | 0.3646 | 0.3646 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
547 | 1727.7 | 821.3 | 147.8 | 179.2 | 34.3 | 1348.3 | 7809.7 | 33.9 | 49.4 | 108 | 104.8 | 93.8 | 114.8 | 44.2 | 31.7 | 1035.6 | 2110.2 | 2110.7 | 1200 | 2318.2 | 2416.8 | 1.159 | 1.099 | 1.145 | 0.952 | 0.95 | 0.955 | 9.02 | 8.68 | 8.63 | 0.737 | 0.82 | 0.764 | -6.92 | -9.11 | 7.33 | 0.759 | 0.861 | 0.921 | 8.41 | 9.02 | 8.47 | 0.846 | 0.764 | 0.726 | 6.03 | -5.97 | -6.19 | Very Poor_Mixed | 1035.6 | 1200 | 1.099 | 0.955 | 9.02 | 0.921 | 9.11 | 0.0815 | 0.5888 | 0.1434 | 0.3329 | 1 | 0.0924 | 0.2531 | 0.3405 | 0.3405 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
548 | 813.1 | 487.2 | 100.2 | 107.4 | 18.6 | 756.5 | 5713.2 | 46.6 | 32.1 | 90.5 | 89.6 | 81.7 | 100.4 | 39.8 | 23.1 | 5971.3 | 5407.7 | 6541.7 | 9356.4 | 8184.8 | 9785.1 | 1.567 | 1.514 | 1.496 | 0.735 | 0.654 | 0.789 | 5.33 | 5.46 | -6.98 | 0.772 | 0.645 | 0.706 | 5.72 | 3.15 | 4.38 | 0.689 | 0.61 | 0.741 | 4.8 | 4.69 | 5.25 | 0.71 | 0.695 | 0.69 | 4.24 | 6.71 | 5.08 | Poor_Mixed | 5407.7 | 8184.8 | 1.496 | 0.789 | 6.98 | 0.772 | 6.71 | 0.461 | 0.7691 | 0.5129 | 0.645 | 1 | 0.4171 | 0.4538 | 0.5911 | 0.5911 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
549 | 172.3 | 120 | 72 | 61.7 | 2.1 | 391.5 | 2832.6 | 55.4 | 22.3 | 78.9 | 80.3 | 71.1 | 84.1 | 35.5 | 10.6 | 9287.9 | 8486.7 | 9406.1 | 17679.6 | 16116.7 | 18110.9 | 1.904 | 1.899 | 1.925 | 0.787 | 0.797 | 0.843 | 6.51 | 6.14 | 6.83 | 0.557 | 0.558 | 0.505 | 2.64 | -2.33 | -3 | 0.55 | 0.502 | 0.544 | 2.64 | 2 | 2.14 | 0.545 | 0.567 | 0.542 | -2.27 | 2.54 | 2.3 | Poor_Winding_TD_Cap | 8486.7 | 16116.7 | 1.899 | 0.843 | 6.83 | 0.567 | 3 | 0.8833 | 0.9215 | 0.8547 | 0.9925 | 1 | 0.3147 | 0.8065 | 0.8157 | 0.8157 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
550 | 250.5 | 211 | 75.1 | 75.1 | 36.3 | 482.3 | 3201 | 57.7 | 20.9 | 81.9 | 80.8 | 74.9 | 86.3 | 36 | 13.5 | 9157.8 | 9079.9 | 8374.5 | 18208.7 | 16383.1 | 15299.8 | 1.988 | 1.804 | 1.827 | 0.986 | 0.948 | 0.978 | 9.84 | 8.8 | 9.2 | 0.545 | 0.554 | 0.545 | 2.4 | 3.36 | -2.87 | 0.575 | 0.564 | 0.589 | 3.05 | 2.67 | 2.59 | 0.543 | 0.532 | 0.5 | 3.31 | -3.48 | 2.34 | Critical_Winding_TD_Cap | 8374.5 | 15299.8 | 1.804 | 0.986 | 9.84 | 0.589 | 3.48 | 0.5736 | 0.9574 | 0.7788 | 0.9318 | 1 | 0.055 | 0.7646 | 0.6881 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
551 | 515.1 | 344.6 | 82.9 | 79.3 | 1.7 | 624.3 | 3723.6 | 27.9 | 24.8 | 80.9 | 76 | 73 | 84.1 | 36.4 | 16.1 | 750.5 | 1193.8 | 690 | 765.5 | 1245.7 | 731.7 | 1.02 | 1.043 | 1.06 | 0.724 | 0.696 | 0.752 | 5.66 | 5.04 | 6.22 | 0.59 | 0.5 | 0.5 | 2.09 | 2 | -2.52 | 0.53 | 0.514 | 0.515 | 2 | 2 | 2.26 | 0.584 | 0.539 | 0.534 | -2 | 2.33 | 2.37 | Critical_IR_PI | 690 | 731.7 | 1.02 | 0.752 | 6.22 | 0.59 | 2.52 | 0.7629 | 0.2901 | 0.8589 | 0.8635 | 0.85 | 0.432 | 0.8527 | 0.7046 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
552 | 481.4 | 352.4 | 84 | 96.8 | 8.4 | 599.7 | 3973.2 | 53.3 | 28.3 | 81.9 | 84.3 | 77.2 | 88.8 | 37.3 | 18.8 | 7387.9 | 8154.7 | 6957.4 | 12609.2 | 14356.9 | 11899.7 | 1.707 | 1.761 | 1.71 | 0.589 | 0.601 | 0.626 | 4.25 | 3.53 | -3.42 | 0.622 | 0.621 | 0.582 | 3.6 | -4.27 | -3.99 | 0.572 | 0.516 | 0.57 | 4.15 | 4.77 | 3.26 | 0.565 | 0.567 | 0.596 | -3.82 | 3.12 | -3.55 | Fair_Mixed | 6957.4 | 11899.7 | 1.707 | 0.626 | 4.25 | 0.622 | 4.77 | 0.6406 | 0.8193 | 0.7151 | 0.7841 | 1 | 0.6639 | 0.6605 | 0.741 | 0.741 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
553 | 1613 | 939.6 | 130.3 | 177.8 | 28.2 | 1297.8 | 7188 | 34.6 | 43.6 | 103.7 | 101.7 | 92 | 111.1 | 43.7 | 31 | 2517.5 | 3068.5 | 3572.9 | 3073.2 | 3866.4 | 4392.9 | 1.221 | 1.26 | 1.23 | 0.918 | 0.948 | 0.898 | -8.94 | 8.89 | -9.22 | 0.785 | 0.931 | 0.862 | 8.45 | -4.8 | -6 | 0.782 | 0.811 | 0.813 | 6.58 | 7.12 | 7.59 | 0.884 | 0.887 | 0.923 | 6.42 | -7.69 | 8.32 | Very Poor_Mixed | 2517.5 | 3073.2 | 1.221 | 0.948 | 9.22 | 0.931 | 8.45 | 0.1327 | 0.6435 | 0.2169 | 0.3597 | 1 | 0.1014 | 0.2186 | 0.3636 | 0.3636 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
554 | 1600.8 | 941.4 | 137.2 | 191.5 | 32.3 | 1261.4 | 8446 | 57.4 | 51.8 | 84.2 | 85.5 | 80.6 | 92.3 | 38.2 | 16.6 | 6682.9 | 8687.6 | 8647.3 | 11050.4 | 16445 | 15708.9 | 1.654 | 1.893 | 1.817 | 0.545 | 0.587 | 0.631 | 3.35 | 2.79 | 3.62 | 0.567 | 0.603 | 0.615 | 3.5 | -3.73 | 3.16 | 0.549 | 0.596 | 0.595 | 3.38 | 3.69 | -3.74 | 0.568 | 0.564 | 0.613 | 3.85 | 3.78 | 2.95 | Critical_DGA | 6682.9 | 11050.4 | 1.654 | 0.631 | 3.62 | 0.615 | 3.85 | 0.0857 | 0.5833 | 0.6427 | 0.8493 | 1 | 0.7199 | 0.6577 | 0.5773 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
555 | 974.4 | 467.8 | 109.3 | 125.1 | 21 | 873.1 | 5450.3 | 48.2 | 31.5 | 89.1 | 89.7 | 80.1 | 99 | 40.5 | 26.8 | 6213.7 | 5464 | 5982.3 | 10101.2 | 8233.4 | 9432.6 | 1.626 | 1.507 | 1.577 | 0.727 | 0.767 | 0.718 | -5.01 | 6.01 | -5.97 | 0.686 | 0.664 | 0.57 | 4.95 | 4.61 | 5.72 | 0.664 | 0.712 | 0.691 | 4.22 | 3.77 | 5.12 | 0.66 | 0.578 | 0.707 | 5.05 | 4.68 | 4.49 | Poor_Mixed | 5464 | 8233.4 | 1.507 | 0.767 | 6.01 | 0.712 | 5.72 | 0.4005 | 0.7766 | 0.5344 | 0.5156 | 1 | 0.419 | 0.5057 | 0.5822 | 0.5822 | Poor | 0 | 1 | DGA | 0 |  | C2H2
556 | 1359.7 | 735.5 | 117.2 | 153 | 25 | 1026.5 | 6628.1 | 42.7 | 38.3 | 99.5 | 99.7 | 89.6 | 107.4 | 42.9 | 33.1 | 4365.8 | 2946.7 | 3026 | 6128 | 3982.2 | 3483.2 | 1.404 | 1.351 | 1.151 | 0.878 | 0.8 | 0.85 | -23.12 | 7.45 | 8.48 | 0.741 | 0.755 | 0.806 | -6.64 | -6.9 | 7.56 | 0.822 | 0.726 | 0.711 | 7.43 | 7.03 | 5.9 | 0.738 | 0.783 | 0.78 | 5.12 | -5.47 | 5.05 | Critical_Mixed | 2946.7 | 3483.2 | 1.151 | 0.878 | 23.12 | 0.822 | 7.56 | 0.2575 | 0.6978 | 0.2906 | 0.2787 | 1 | 0.1776 | 0.3266 | 0.4348 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
557 | 1056.2 | 579.7 | 114.1 | 123.8 | 20.3 | 907.1 | 6089.6 | 45.5 | 31.7 | 91.8 | 93.6 | 82 | 98.1 | 40.9 | 26.7 | 6128.1 | 5642.8 | 6488.6 | 9852.7 | 8872 | 10379 | 1.608 | 1.572 | 1.6 | 0.757 | 0.682 | 0.687 | -5.93 | 5.58 | 5.3 | 0.742 | 0.687 | 0.728 | 6.01 | 4.87 | -6.24 | 0.759 | 0.628 | 0.675 | 5.43 | 5.03 | -3.72 | 0.673 | 0.651 | 0.769 | -4.22 | 3.65 | 5.32 | Poor_Mixed | 5642.8 | 8872 | 1.572 | 0.757 | 5.93 | 0.769 | 6.24 | 0.3724 | 0.7741 | 0.481 | 0.5192 | 1 | 0.4482 | 0.4447 | 0.5628 | 0.5628 | Poor | 0 | 1 | DGA | 0 |  | C2H2
558 | 507.8 | 296.3 | 86 | 83.1 | 5.9 | 512.7 | 4130.3 | 54.6 | 27.9 | 82.6 | 82.8 | 77 | 88.6 | 37.6 | 15.3 | 8666.8 | 9689.1 | 9375.6 | 16472.9 | 18183.3 | 17411.9 | 1.901 | 1.877 | 1.857 | 0.99 | 0.959 | 0.974 | -9.42 | 9.68 | 9.42 | 0.7 | 0.56 | 0.625 | -4.08 | 4.24 | 4.93 | 0.566 | 0.568 | 0.708 | -4.07 | -3.57 | 3.74 | 1.279 | 0.635 | 0.604 | 3.01 | -4.69 | 4.08 | Critical_Winding_TD_Cap | 8666.8 | 16472.9 | 1.857 | 0.99 | 9.68 | 1.279 | 4.93 | 0.6976 | 0.825 | 0.7217 | 0.8855 | 1 | 0.0412 | 0.5444 | 0.6536 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_R_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
559 | 1082.3 | 632.2 | 112.5 | 125.4 | 19.8 | 831.8 | 5746.6 | 46 | 33.5 | 91.3 | 92.8 | 83.4 | 101.3 | 40 | 24.1 | 5631.7 | 5432.3 | 5289.2 | 8666.8 | 8473.3 | 7662.7 | 1.539 | 1.56 | 1.449 | 0.764 | 0.744 | 0.731 | 6.41 | 5.88 | 5.97 | 0.711 | 0.639 | 0.696 | 6.46 | 5.85 | 4.7 | 0.741 | 0.767 | 0.767 | -5.07 | 4.35 | -4.48 | 0.726 | 0.748 | 0.627 | 4.54 | -6.62 | -6.47 | Poor_Mixed | 5289.2 | 7662.7 | 1.449 | 0.764 | 6.41 | 0.767 | 6.62 | 0.3801 | 0.752 | 0.4703 | 0.6108 | 1 | 0.3875 | 0.4145 | 0.5517 | 0.5517 | Poor | 0 | 1 | DGA | 0 |  | C2H2
560 | 999.8 | 651.1 | 111.4 | 131.2 | 22.6 | 1001.7 | 5801.8 | 54.7 | 23.1 | 81.9 | 81 | 72.1 | 87.4 | 36.3 | 14.6 | 9307.7 | 8479.5 | 8614 | 17379.5 | 15022.8 | 15728.1 | 1.867 | 1.772 | 1.826 | 0.538 | 0.516 | 0.524 | 3.13 | 2 | 2.64 | 0.535 | 0.5 | 0.551 | 2.23 | -2 | 2 | 0.539 | 0.5 | 0.547 | 2.07 | 2.79 | -2 | 0.533 | 0.553 | 0.5 | -2 | 2.2 | 2.09 | Poor_DGA | 8479.5 | 15022.8 | 1.772 | 0.538 | 3.13 | 0.553 | 2.79 | 0.3428 | 0.9047 | 0.7933 | 0.904 | 1 | 0.863 | 0.8688 | 0.756 | 0.756 | Fair | 1 | 1 | DGA | 0 |  | C2H2
561 | 890.5 | 511.4 | 108.8 | 127 | 17.9 | 890.3 | 5385.4 | 48.6 | 33.8 | 89.2 | 90 | 80.8 | 98.7 | 39.9 | 25.5 | 7281.6 | 5865.7 | 5633 | 12074.5 | 8517.8 | 8847.6 | 1.658 | 1.452 | 1.571 | 0.743 | 0.731 | 0.763 | -5.84 | 5.5 | -6.14 | 0.706 | 0.668 | 0.684 | -5.15 | 5.77 | -5.5 | 0.657 | 0.742 | 0.699 | -5.38 | -4.09 | 5.51 | 0.641 | 0.637 | 0.634 | 4.8 | 5.47 | 3.74 | Poor_Mixed | 5633 | 8517.8 | 1.452 | 0.763 | 6.14 | 0.742 | 5.77 | 0.4177 | 0.7485 | 0.5326 | 0.562 | 1 | 0.4024 | 0.4719 | 0.5769 | 0.5769 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
562 | 316.3 | 227.9 | 71 | 56.3 | 1.7 | 357.7 | 3061.1 | 50.2 | 29 | 76.7 | 75.7 | 71.4 | 82.1 | 35.5 | 11.2 | 7831.1 | 8522.4 | 8774.1 | 13745.4 | 15735.3 | 16488.3 | 1.755 | 1.846 | 1.879 | 0.559 | 0.573 | 0.554 | 2.95 | 2.98 | 2.52 | 0.52 | 0.524 | 0.598 | 2 | -2.86 | 2.59 | 0.546 | 0.583 | 0.537 | 2.85 | 2 | 2 | 0.54 | 0.503 | 0.502 | -2 | 2.66 | -2.02 | Fair_Oil | 7831.1 | 13745.4 | 1.755 | 0.573 | 2.98 | 0.598 | 2.86 | 0.8835 | 0.8095 | 0.9314 | 0.9821 | 1 | 0.7808 | 0.824 | 0.8779 | 0.8779 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
563 | 394.8 | 254.5 | 81.8 | 106.2 | 3 | 574.5 | 3254.4 | 55.9 | 23.7 | 90.6 | 90.2 | 81.1 | 96.9 | 40.7 | 11.4 | 8276.3 | 7388.4 | 7108 | 15571.9 | 12932.1 | 11915.1 | 1.882 | 1.75 | 1.676 | 0.576 | 0.586 | 0.545 | 3.05 | 2.97 | 2.6 | 0.512 | 0.544 | 0.537 | 3.11 | 3.41 | 3.05 | 0.562 | 0.563 | 0.554 | -2.9 | -2.83 | 2 | 0.567 | 0.546 | 0.541 | 3.43 | 2.95 | 2.46 | Poor_Thermal | 7108 | 11915.1 | 1.676 | 0.586 | 3.05 | 0.567 | 3.43 | 0.7319 | 0.8931 | 0.5238 | 0.9783 | 1 | 0.7677 | 0.7614 | 0.796 | 0.796 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
564 | 1097.8 | 539.1 | 103.8 | 124.9 | 20.3 | 803.1 | 5758.6 | 45.9 | 33.7 | 94.4 | 93.8 | 83.9 | 100.1 | 41.2 | 26.1 | 5215.6 | 6921.6 | 5019.8 | 7633.7 | 10938.9 | 6981.4 | 1.464 | 1.58 | 1.391 | 0.788 | 0.77 | 0.763 | 6.42 | 5.99 | 6.32 | 0.609 | 0.668 | 0.615 | 4.06 | -4.82 | 5.21 | 0.754 | 0.678 | 0.64 | 4.1 | 4.25 | 4.16 | 0.627 | 0.615 | 0.701 | 4.39 | 4.09 | 5.98 | Poor_Mixed | 5019.8 | 6981.4 | 1.391 | 0.788 | 6.42 | 0.754 | 5.98 | 0.3967 | 0.7497 | 0.4393 | 0.5407 | 1 | 0.3561 | 0.5142 | 0.5625 | 0.5625 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
565 | 1608 | 911.9 | 142.3 | 181.1 | 33.6 | 1320.8 | 8465.1 | 35.7 | 45.5 | 106 | 106.1 | 92.6 | 115.1 | 44.3 | 29.9 | 1703.9 | 2151.3 | 2830.8 | 1915 | 2603.8 | 3356.9 | 1.124 | 1.21 | 1.186 | 0.883 | 0.884 | 0.904 | 8.28 | -8.49 | 9.46 | 0.908 | 0.743 | 0.794 | -6.57 | 7.81 | -7.51 | 0.821 | 0.754 | 0.8 | 7.25 | -8.06 | 8.67 | 0.773 | 0.788 | 0.819 | 7.47 | -6.65 | 6 | Very Poor_Mixed | 1703.9 | 1915 | 1.124 | 0.904 | 9.46 | 0.908 | 8.67 | 0.0805 | 0.6251 | 0.1517 | 0.4014 | 1 | 0.1369 | 0.2564 | 0.3557 | 0.3557 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
566 | 1614.8 | 888.4 | 137.9 | 172.3 | 34.3 | 1270.2 | 7579.7 | 33.1 | 47.1 | 104.5 | 103.1 | 94.3 | 114.3 | 42.9 | 31.6 | 1192 | 981.4 | 2397.1 | 1349.6 | 1200 | 2908.3 | 1.132 | 1.223 | 1.213 | 0.981 | 0.986 | 0.968 | -9.34 | 8.44 | 9.18 | 0.836 | 0.785 | 0.788 | -5.81 | 8.46 | -8.09 | 0.805 | 0.877 | 0.793 | -5.63 | 5.65 | 5.52 | 0.773 | 0.825 | 0.749 | 7.14 | 8.19 | 8.3 | Very Poor_Mixed | 981.4 | 1200 | 1.132 | 0.986 | 9.34 | 0.877 | 8.46 | 0.1073 | 0.61 | 0.1812 | 0.3368 | 1 | 0.0646 | 0.2648 | 0.3517 | 0.3517 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
567 | 305.4 | 233 | 76 | 78.9 | 1.9 | 508 | 3553.2 | 54.5 | 26.2 | 75.6 | 76.5 | 70.6 | 80.7 | 35.5 | 12.3 | 9828.7 | 9106.9 | 9290.3 | 19657.5 | 17002.5 | 17831 | 2 | 1.867 | 1.919 | 0.784 | 0.724 | 0.729 | -6.59 | 6.07 | 5.79 | 0.541 | 0.57 | 0.527 | 2.98 | -3.91 | -3.1 | 0.543 | 0.596 | 0.513 | -2.77 | 3.03 | 3.56 | 0.557 | 0.55 | 0.532 | 2.8 | 3.03 | 2 | Poor_Winding_TD_Cap | 9106.9 | 17002.5 | 1.867 | 0.784 | 6.59 | 0.596 | 3.91 | 0.8115 | 0.8505 | 0.9507 | 0.9597 | 1 | 0.3851 | 0.7577 | 0.7983 | 0.7983 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Moisture_PPM
568 | 1133.7 | 585.2 | 112.4 | 125.4 | 20.7 | 944.3 | 6013 | 54.5 | 22.1 | 79.9 | 78.5 | 72.8 | 85 | 36.9 | 10 | 8798.5 | 9730.4 | 8405.4 | 16740.9 | 18233.3 | 15953.4 | 1.903 | 1.874 | 1.898 | 0.572 | 0.521 | 0.5 | 2.77 | 2.01 | 2 | 0.5 | 0.5 | 0.5 | 2 | 2 | 2 | 0.55 | 0.5 | 0.543 | 2.72 | 2.94 | 2.69 | 0.592 | 0.514 | 0.526 | 2.19 | 2.54 | 2.04 | Poor_DGA | 8405.4 | 15953.4 | 1.874 | 0.572 | 2.77 | 0.592 | 2.94 | 0.3597 | 0.926 | 0.8349 | 1 | 1 | 0.8958 | 0.8795 | 0.7783 | 0.7783 | Fair | 1 | 1 | DGA | 0 |  | C2H2
569 | 894.6 | 560.3 | 102.7 | 120.4 | 16.9 | 863.2 | 4910.5 | 44.1 | 35.5 | 92.4 | 90.7 | 83.7 | 98.2 | 39.9 | 24.6 | 5219.4 | 4767.5 | 5411.8 | 8700.3 | 6953.7 | 8044.4 | 1.667 | 1.459 | 1.486 | 0.752 | 0.668 | 0.724 | 6.15 | 4.67 | 5.52 | 0.564 | 0.759 | 0.672 | 6.27 | 3.62 | 4.97 | 0.721 | 0.744 | 0.714 | 4.42 | 5 | -3.91 | 0.774 | 0.714 | 0.651 | -4.9 | -6.57 | 4.71 | Poor_Mixed | 4767.5 | 6953.7 | 1.459 | 0.752 | 6.15 | 0.774 | 6.57 | 0.437 | 0.7287 | 0.491 | 0.5935 | 1 | 0.452 | 0.4485 | 0.5795 | 0.5795 | Poor | 0 | 1 | DGA | 0 |  | C2H2
570 | 558.3 | 463.6 | 95 | 105.9 | 11.3 | 756.2 | 4436.6 | 53.6 | 27.3 | 84.8 | 82.5 | 78.2 | 90.2 | 37.7 | 21.7 | 7270.3 | 8402.8 | 8421.6 | 12347.4 | 14510.9 | 15655.1 | 1.698 | 1.727 | 1.859 | 0.576 | 0.625 | 0.673 | 3.63 | 4.27 | 4.06 | 0.582 | 0.635 | 0.661 | 3.51 | 4.2 | 3.21 | 0.633 | 0.617 | 0.609 | 4.01 | 3.84 | 3.35 | 0.663 | 0.594 | 0.59 | 4.13 | 3.47 | 3.97 | Fair_Mixed | 7270.3 | 12347.4 | 1.698 | 0.673 | 4.27 | 0.663 | 4.2 | 0.5534 | 0.8337 | 0.6904 | 0.6918 | 1 | 0.6282 | 0.5938 | 0.6969 | 0.6969 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
571 | 743.7 | 463.5 | 97 | 118.5 | 13.1 | 737.8 | 4821.8 | 54.5 | 21.1 | 75 | 75.7 | 70.3 | 80.2 | 36.5 | 10.6 | 9144.7 | 9055.6 | 8555.3 | 17488.9 | 17215.1 | 16132 | 1.912 | 1.901 | 1.886 | 0.53 | 0.59 | 0.572 | 3.05 | 3.15 | 3.82 | 0.513 | 0.533 | 0.577 | 3.36 | 2.7 | 2.52 | 0.532 | 0.529 | 0.574 | 2.46 | 2.38 | 3.21 | 0.592 | 0.571 | 0.537 | 3.13 | 2.85 | 2.1 | Fair_DGA | 8555.3 | 16132 | 1.886 | 0.59 | 3.82 | 0.592 | 3.36 | 0.5088 | 0.9514 | 0.9744 | 0.9925 | 1 | 0.7461 | 0.7642 | 0.7904 | 0.7904 | Fair | 1 | 1 | DGA | 0 |  | C2H2
572 | 1766 | 940.8 | 148.3 | 194 | 32.6 | 1367.3 | 8775.8 | 55.9 | 81.3 | 87.1 | 86.4 | 77.1 | 93.7 | 36.7 | 15.5 | 8929 | 7426.9 | 8232.7 | 16817.1 | 12719.9 | 15153.2 | 1.883 | 1.713 | 1.841 | 0.575 | 0.592 | 0.577 | 3.36 | -3.77 | 3.55 | 0.588 | 0.546 | 0.565 | 2 | 2.8 | 2.95 | 0.523 | 0.542 | 0.544 | 2.31 | 2.74 | 3.38 | 0.518 | 0.555 | 0.584 | 2.44 | 3.31 | 2.28 | Critical_DGA | 7426.9 | 12719.9 | 1.713 | 0.592 | 3.77 | 0.588 | 3.38 | 0.046 | 0.5833 | 0.6405 | 0.88 | 1 | 0.7044 | 0.7641 | 0.5857 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
573 | 1009.5 | 510 | 105.2 | 117.8 | 18.9 | 859.4 | 4885.1 | 46 | 32.8 | 90 | 91.9 | 83.7 | 100 | 40.4 | 24.6 | 5319.4 | 4484.2 | 5257.3 | 8238.1 | 6345.2 | 7349.4 | 1.549 | 1.415 | 1.398 | 0.744 | 0.73 | 0.683 | -5.59 | 5.84 | 5.31 | 0.724 | 0.633 | 0.687 | 5.15 | 3.9 | 4.5 | 0.779 | 0.633 | 0.653 | 4.9 | 5.22 | -4.3 | 0.677 | 0.655 | 0.677 | 5.65 | -5.4 | 3.51 | Poor_Mixed | 4484.2 | 6345.2 | 1.398 | 0.744 | 5.84 | 0.779 | 5.65 | 0.4227 | 0.7605 | 0.4866 | 0.5935 | 1 | 0.4398 | 0.4778 | 0.5829 | 0.5829 | Poor | 0 | 1 | DGA | 0 |  | C2H2
574 | 816.1 | 524.8 | 111 | 106.2 | 14.3 | 817.3 | 4993.2 | 44.6 | 34.4 | 96.6 | 90.3 | 83.7 | 102 | 40.8 | 24 | 5827.9 | 6000.1 | 5646.3 | 9429 | 9389.8 | 8835.3 | 1.618 | 1.565 | 1.565 | 0.826 | 0.781 | 0.732 | -6.54 | 7.08 | 5.86 | 0.639 | 0.669 | 0.706 | 4.83 | 5.26 | 5.06 | 0.663 | 0.626 | 0.719 | -4.12 | 5.28 | 5.04 | 0.599 | 0.672 | 0.63 | 4.8 | -4.65 | -4.86 | Poor_Mixed | 5646.3 | 8835.3 | 1.565 | 0.826 | 7.08 | 0.719 | 5.28 | 0.4777 | 0.7414 | 0.4427 | 0.6143 | 1 | 0.3387 | 0.4986 | 0.5806 | 0.5806 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
575 | 431.2 | 292.8 | 83.1 | 76.2 | 1.9 | 478.7 | 3691.9 | 53.3 | 27.8 | 78.1 | 127.1 | 70.8 | 84 | 35.7 | 13.9 | 690 | 1194.8 | 1499.1 | 753.6 | 1303.7 | 1529.1 | 1.092 | 1.091 | 1.02 | 0.753 | 0.767 | 0.816 | 6.14 | 6.31 | 5.35 | 0.5 | 0.542 | 0.555 | 3.12 | 2.49 | 2 | 0.54 | 0.508 | 0.578 | 2.65 | 3.41 | -3.92 | 0.584 | 0.576 | 0.533 | -2.52 | -2.81 | 2.49 | Critical_IR_PI | 690 | 753.6 | 1.02 | 0.816 | 6.31 | 0.584 | 3.92 | 0.7953 | 0.8264 | 0.6759 | 0.9219 | 0.925 | 0.3695 | 0.7808 | 0.7519 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature; IR_Min_10min<1000 Mohm: critical insulation resistance | WTI_LV
576 | 889.5 | 573.5 | 102.8 | 111 | 19.5 | 780 | 5670.6 | 45.2 | 33 | 91.1 | 90.2 | 80.3 | 94.6 | 40.6 | 25.4 | 5339 | 5638.4 | 6170.6 | 8295.2 | 8390.1 | 9995.2 | 1.554 | 1.488 | 1.62 | 0.727 | 0.707 | 0.691 | -5.32 | -5.92 | 5.3 | 0.635 | 0.62 | 0.65 | 4.76 | 4.88 | 4.42 | 0.715 | 0.64 | 0.596 | 3.95 | 4.31 | -4.64 | 0.676 | 0.741 | 0.645 | 4.35 | 4.45 | 4.04 | Poor_Mixed | 5339 | 8295.2 | 1.488 | 0.727 | 5.92 | 0.741 | 4.88 | 0.4318 | 0.7581 | 0.5379 | 0.5655 | 1 | 0.4528 | 0.5172 | 0.5975 | 0.5975 | Poor | 0 | 1 | DGA | 0 |  | C2H2
577 | 221 | 215.1 | 75.3 | 66 | 3.5 | 399.4 | 3417.7 | 58.9 | 20 | 75.5 | 77.2 | 70.3 | 80.6 | 35.1 | 12.4 | 10000 | 10000 | 10000 | 20000 | 19551.5 | 19224.4 | 2 | 1.955 | 1.922 | 0.524 | 0.514 | 0.521 | 2.32 | 2.4 | 2.51 | 0.5 | 0.5 | 0.545 | 2.49 | 2.75 | -2.49 | 0.5 | 0.517 | 0.5 | 2.29 | -2 | 2 | 0.503 | 0.545 | 0.525 | 2 | -2.13 | -2 | Good_Mixed | 10000 | 19224.4 | 1.922 | 0.524 | 2.51 | 0.545 | 2.75 | 0.8222 | 1 | 0.95 | 0.9575 | 1 | 0.8865 | 0.9111 | 0.9166 | 0.9166 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
578 | 589 | 348.7 | 77.8 | 88.7 | 1.4 | 539.5 | 3898.7 | 13.9 | 32.1 | 75 | 75 | 71.9 | 80.4 | 36.7 | 14.1 | 8167 | 8545.3 | 7940.9 | 14508 | 15628.5 | 14245.9 | 1.776 | 1.829 | 1.794 | 0.92 | 0.99 | 0.955 | 8.96 | 9.64 | -9.46 | 0.703 | 0.603 | 0.591 | -3.96 | 3.92 | 3.44 | 0.62 | 0.577 | 0.596 | 4.08 | 3.97 | 4.26 | 0.631 | 0.677 | 0.669 | 3.83 | 3.57 | 3.96 | Critical_Winding_TD_Cap | 7940.9 | 14245.9 | 1.776 | 0.99 | 9.64 | 0.703 | 4.26 | 0.7717 | 0.1857 | 0.9687 | 0.9169 | 1 | 0.0619 | 0.5765 | 0.6304 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
579 | 1569.4 | 892.8 | 138.7 | 174.6 | 33.8 | 1222.4 | 7676.1 | 51.2 | 29 | 75.8 | 78.2 | 73.1 | 81 | 35.8 | 12.4 | 8425.3 | 9055.4 | 8511 | 16081.2 | 17450.7 | 14870 | 1.909 | 1.927 | 1.747 | 0.637 | 1.83 | 0.634 | 3.58 | 3.77 | 3.46 | 0.549 | 0.5 | 0.536 | 2.51 | 2.73 | 2.53 | 0.552 | 0.535 | 0.536 | 2.78 | 2.5 | 3.06 | 0.569 | 0.52 | 0.51 | 2.91 | -2.45 | -2 | Critical_DGA | 8425.3 | 14870 | 1.747 | 1.83 | 3.77 | 0.569 | 3.06 | 0.1137 | 0.8095 | 0.9032 | 0.9575 | 1 | 0.5399 | 0.8158 | 0.6462 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
580 | 701.1 | 416.6 | 90.8 | 94.8 | 12.8 | 662.8 | 4173.3 | 51.7 | 29.8 | 82.5 | 83 | 77.3 | 90.8 | 37.5 | 21.2 | 7740.9 | 7121.1 | 7064.6 | 13368.9 | 11754.2 | 12130.4 | 1.727 | 1.651 | 1.717 | 0.637 | 0.692 | 0.646 | -4.52 | -4.7 | -4.81 | 0.594 | 0.618 | 0.633 | 3.85 | 4.15 | 3.72 | 0.594 | 0.661 | 0.646 | 2.11 | -4.06 | -2.99 | 0.623 | 0.626 | 0.531 | -4.1 | -2.78 | 3.46 | Fair_Mixed | 7064.6 | 11754.2 | 1.651 | 0.692 | 4.81 | 0.661 | 4.15 | 0.5642 | 0.7986 | 0.7084 | 0.7082 | 1 | 0.549 | 0.6193 | 0.6915 | 0.6915 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
581 | 1727.2 | 945.9 | 144.7 | 186.5 | 32.5 | 1323 | 8087.7 | 33.1 | 46.8 | 105.1 | 105.8 | 91.7 | 113.9 | 43.4 | 32.4 | 2107 | 1777.4 | 1718.6 | 2303.8 | 1956 | 1804.5 | 1.093 | 1.1 | 1.05 | 0.943 | 0.935 | 0.948 | 9.58 | 9.2 | 8.17 | 0.77 | 0.895 | 0.95 | 5.53 | 6.69 | 7.02 | 0.772 | 0.719 | 0.866 | 5.07 | 5.95 | 7.39 | 0.763 | 0.909 | 0.854 | 6.55 | 9.1 | -8.14 | Very Poor_Mixed | 1718.6 | 1804.5 | 1.05 | 0.948 | 9.58 | 0.95 | 9.1 | 0.0715 | 0.6128 | 0.1759 | 0.3059 | 1 | 0.0891 | 0.2444 | 0.3408 | 0.3408 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
582 | 725.6 | 462.9 | 104.6 | 108.3 | 19 | 790.8 | 4942.7 | 47 | 32 | 93.2 | 94.9 | 80.3 | 102.8 | 40.5 | 24.5 | 4836.6 | 5991.5 | 6302.2 | 7224.6 | 9559.4 | 10036.9 | 1.494 | 1.595 | 1.593 | 0.733 | 0.702 | 0.689 | -5.11 | 5.27 | 5.05 | 0.729 | 0.632 | 0.707 | 4.93 | 5.58 | 5.05 | 0.656 | 0.684 | 0.622 | 5.47 | 4.2 | 4.92 | 0.627 | 0.683 | 0.658 | -4.89 | 5.63 | 4.02 | Poor_Mixed | 4836.6 | 7224.6 | 1.494 | 0.733 | 5.27 | 0.729 | 5.63 | 0.4677 | 0.7703 | 0.4542 | 0.597 | 1 | 0.4739 | 0.4846 | 0.5982 | 0.5982 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
583 | 853.2 | 501.4 | 105.3 | 130.4 | 16.6 | 906.8 | 5254.2 | 47.6 | 33.9 | 91.1 | 90.3 | 85.3 | 101.7 | 40.3 | 24 | 4622.8 | 5427.7 | 4904.5 | 6804.7 | 8097 | 7113.8 | 1.472 | 1.492 | 1.45 | 0.764 | 0.736 | 0.721 | -4.94 | -5.94 | -4.91 | 0.734 | 0.675 | 0.675 | -5.03 | 4.69 | 4.19 | 0.63 | 0.678 | 0.711 | 3.92 | -4.86 | -5.23 | 0.652 | 0.618 | 0.64 | 4.69 | 5.5 | 5.06 | Poor_Mixed | 4622.8 | 6804.7 | 1.45 | 0.764 | 5.94 | 0.734 | 5.5 | 0.4287 | 0.7473 | 0.4721 | 0.6143 | 1 | 0.4387 | 0.4886 | 0.5841 | 0.5841 | Poor | 0 | 1 | DGA | 0 |  | C2H2
584 | 264.9 | 209.3 | 68.7 | 70.2 | 1 | 457.7 | 2753.8 | 42.3 | 36.3 | 79.1 | 79 | 71.2 | 85.8 | 35 | 13.1 | 7486.1 | 6347.4 | 7248.1 | 12879.6 | 10162.4 | 12238.2 | 1.72 | 1.601 | 1.688 | 0.613 | 0.556 | 0.588 | 3.7 | 3.52 | 3.66 | 0.541 | 0.539 | 0.552 | 2.49 | 2.83 | -2 | 0.57 | 0.509 | 0.541 | 2.59 | -3.45 | 3.35 | 0.547 | 0.575 | 0.509 | -2.64 | -2.59 | 3.02 | Poor_Oil | 6347.4 | 10162.4 | 1.601 | 0.613 | 3.7 | 0.575 | 3.45 | 0.9087 | 0.7197 | 0.8566 | 0.9414 | 1 | 0.696 | 0.7825 | 0.8446 | 0.8446 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
585 | 904.5 | 554.7 | 103.2 | 117.5 | 15.3 | 854.8 | 4668.4 | 59.6 | 21.9 | 84.5 | 83.4 | 74.6 | 84.9 | 36.4 | 13.1 | 9291.2 | 7880.4 | 9166 | 17732.7 | 14959.1 | 17197.8 | 1.909 | 1.898 | 1.876 | 0.511 | 0.584 | 0.55 | 2.03 | 3.02 | 2.38 | 0.5 | 0.5 | 0.54 | 2.3 | 2.16 | 2.28 | 0.541 | 0.553 | 0.511 | 2.56 | 2.36 | 2.01 | 0.542 | 0.545 | 0.534 | 2.04 | 2.08 | 2 | Poor_DGA | 7880.4 | 14959.1 | 1.876 | 0.584 | 3.02 | 0.553 | 2.56 | 0.4533 | 0.9307 | 0.7453 | 0.9414 | 1 | 0.836 | 0.8561 | 0.7777 | 0.7777 | Fair | 1 | 1 | DGA | 0 |  | C2H2
586 | 792.3 | 545.1 | 99.8 | 114.7 | 17.7 | 891.3 | 5188.2 | 45.7 | 34.4 | 91.9 | 87 | 83 | 95.9 | 38.8 | 22.7 | 5268 | 5547.5 | 5630.9 | 8138.4 | 8392.6 | 7984.5 | 1.545 | 1.513 | 1.418 | 0.801 | 0.746 | 0.759 | -5.88 | 6.2 | -6.26 | 0.658 | 0.702 | 0.668 | -5.01 | 4.78 | 4.72 | 0.704 | 0.693 | 0.644 | 4.41 | 4.24 | -5.89 | 0.617 | 0.658 | 0.702 | 4.05 | 4.4 | 3.89 | Poor_Mixed | 5268 | 7984.5 | 1.418 | 0.801 | 6.26 | 0.704 | 5.89 | 0.4432 | 0.7414 | 0.542 | 0.6585 | 1 | 0.3675 | 0.4909 | 0.5867 | 0.5867 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
587 | 1219.2 | 674 | 127.7 | 155.2 | 24.6 | 1000.8 | 6702.8 | 56.4 | 21.8 | 77 | 75 | 72.4 | 82.8 | 36.7 | 15.4 | 9780.4 | 9454.3 | 9561 | 19071.9 | 18474 | 18304.9 | 1.95 | 1.954 | 1.915 | 0.508 | 0.504 | 0.502 | 2 | -2 | 2.46 | 0.544 | 0.58 | 0.578 | 2.61 | 2.72 | 2.89 | 0.563 | 0.561 | 0.548 | -2.69 | 3.12 | 2.46 | 0.603 | 0.577 | 0.563 | 3.17 | 2.98 | 3.3 | Poor_DGA | 9454.3 | 18304.9 | 1.915 | 0.508 | 2.46 | 0.603 | 3.3 | 0.2689 | 0.9331 | 0.9229 | 0.8828 | 1 | 0.955 | 0.7161 | 0.7382 | 0.7382 | Fair | 1 | 1 | DGA | 0 |  | C2H2
588 | 959.9 | 576.9 | 107.1 | 128.4 | 15.8 | 942.6 | 6164.2 | 47.2 | 34.8 | 92.9 | 95.5 | 82.3 | 97.9 | 40.2 | 22.1 | 6082 | 5489.7 | 4878 | 9430.8 | 8089.8 | 7024.1 | 1.551 | 1.474 | 1.44 | 0.725 | 0.736 | 0.733 | 5.84 | -5.27 | -5.51 | 0.584 | 0.659 | 0.694 | 4.53 | 4.24 | 4.58 | 0.624 | 0.669 | 0.69 | 4.72 | 4.53 | 4.76 | 0.653 | 0.604 | 0.671 | 5.43 | 4.85 | -4.51 | Poor_Mixed | 4878 | 7024.1 | 1.44 | 0.736 | 5.84 | 0.694 | 5.43 | 0.4037 | 0.7368 | 0.4659 | 0.6786 | 1 | 0.4305 | 0.5171 | 0.5832 | 0.5832 | Poor | 0 | 1 | DGA | 0 |  | C2H2
589 | 265.1 | 164.6 | 71.4 | 57.8 | 2.9 | 417.8 | 2570.7 | 56.8 | 23.7 | 77.2 | 76 | 72.1 | 81.2 | 36.1 | 14.2 | 8142.1 | 8654 | 9190.2 | 14536.5 | 16439.5 | 17593 | 1.785 | 1.9 | 1.914 | 0.5 | 0.501 | 0.5 | 2 | 2.13 | 2.53 | 0.534 | 0.543 | 0.518 | 2.5 | 2.08 | 2.49 | 0.504 | 0.518 | 0.502 | -2.69 | 2.02 | 3.15 | 0.587 | 0.517 | 0.516 | 2.44 | 3.22 | 3.05 | Good_Mixed | 8142.1 | 14536.5 | 1.785 | 0.501 | 2.53 | 0.587 | 3.22 | 0.8512 | 0.8931 | 0.9171 | 0.9144 | 1 | 0.9756 | 0.837 | 0.9046 | 0.9046 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
590 | 284.3 | 176.5 | 74.4 | 55.3 | 2.3 | 358.9 | 2500 | 60 | 20.2 | 75 | 77 | 70.2 | 83.5 | 35.9 | 11.8 | 9316 | 10000 | 8963.8 | 18620.9 | 20000 | 17606.2 | 1.999 | 2 | 1.964 | 0.5 | 0.5 | 0.527 | -2 | -2 | 2.85 | 0.5 | 0.506 | 0.531 | -3.23 | 2.47 | 2.6 | 0.534 | 0.529 | 0.5 | 2.37 | 2.03 | 2 | 0.522 | 0.5 | 0.5 | 2 | -2.12 | 2 | Good_Mixed | 8963.8 | 17606.2 | 1.964 | 0.527 | 2.85 | 0.534 | 3.23 | 0.8769 | 0.984 | 0.9462 | 0.9703 | 1 | 0.946 | 0.9089 | 0.9365 | 0.9365 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
591 | 281.1 | 235.8 | 73.8 | 157.1 | 2.8 | 489.2 | 3444.9 | 56.4 | 79 | 109.3 | 107.2 | 96 | 118.5 | 46 | 17.8 | 8092.5 | 8404.1 | 8196.1 | 14756.5 | 15140.4 | 14823.8 | 1.823 | 1.802 | 1.809 | 0.548 | 0.578 | 0.591 | 2 | 3.28 | 2.9 | 0.591 | 0.584 | 0.614 | 2.63 | -2.97 | 3.93 | 0.534 | 0.576 | 0.598 | 3.8 | -3.52 | 2.84 | 0.58 | 0.586 | 0.625 | 4.07 | -2.57 | 3.38 | Critical_Thermal | 8092.5 | 14756.5 | 1.802 | 0.591 | 3.28 | 0.625 | 4.07 | 0.7179 | 0.5833 | 0.0791 | 0.8143 | 1 | 0.7767 | 0.6655 | 0.6866 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
592 | 1701.9 | 982.4 | 148.3 | 197 | 34.3 | 1332.8 | 8783.3 | 31.1 | 49.4 | 108 | 105.8 | 95.7 | 115.9 | 45.3 | 32.1 | 2079.3 | 800.1 | 1425.8 | 2415.4 | 1200 | 1573.6 | 1.162 | 1.5 | 1.104 | 0.99 | 0.972 | 0.919 | -9.63 | -9.44 | 8.25 | 0.894 | 0.953 | 0.862 | 6.51 | -6.18 | 7.2 | 0.728 | 0.819 | 0.944 | 9.84 | 7.66 | 5.48 | 0.776 | 0.781 | 0.932 | 7.34 | 6.03 | 6.31 | Very Poor_Mixed | 800.1 | 1200 | 1.104 | 0.99 | 9.63 | 0.953 | 9.84 | 0.0398 | 0.5888 | 0.1137 | 0.3175 | 1 | 0.0708 | 0.2209 | 0.3175 | 0.3175 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
593 | 211.4 | 233.9 | 65 | 69.8 | 1 | 350 | 2565.7 | 57.3 | 23.2 | 79.3 | 77.8 | 71.9 | 84.3 | 35.7 | 15.2 | 8392.5 | 7959.7 | 7974.5 | 14589.7 | 14254.3 | 14140.6 | 1.738 | 1.791 | 1.773 | 0.574 | 1.923 | 0.553 | 3.37 | -3.35 | 2.19 | 0.983 | 0.586 | 0.537 | 9.18 | 3.45 | 3.15 | 0.637 | 0.527 | 0.615 | 2.63 | 3.43 | -5.06 | 0.623 | 0.684 | 0.558 | -2.75 | 2.88 | 3.6 | Critical_Bushing_TD_Cap | 7959.7 | 14140.6 | 1.738 | 1.923 | 3.37 | 0.983 | 9.18 | 0.9367 | 0.9027 | 0.8645 | 0.8882 | 1 | 0.6431 | 0.5882 | 0.8293 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_LV_TanDelta_pct
594 | 620.1 | 388.1 | 89.4 | 97.8 | 5 | 630.7 | 3349.9 | 52.3 | 54 | 79.2 | 76.6 | 74.2 | 84.8 | 36.2 | 15.6 | 10000 | 10000 | 8619.8 | 19247.6 | 19951.5 | 15811.5 | 1.925 | 1.995 | 1.834 | 0.965 | 0.985 | 0.931 | 9.64 | -8.85 | 9.61 | 0.505 | 0.531 | 0.5 | 2.22 | 2.41 | 2.19 | 0.519 | 0.51 | 0.5 | -2.31 | 2 | 2.65 | 0.542 | 0.5 | 0.52 | 2.26 | 2.55 | -2.05 | Critical_Winding_TD_Cap | 8619.8 | 15811.5 | 1.834 | 0.985 | 9.64 | 0.542 | 2.65 | 0.6593 | 0.5833 | 0.854 | 0.8773 | 1 | 0.0576 | 0.9017 | 0.6944 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
595 | 495.7 | 246 | 73.9 | 113.5 | 1.5 | 502.5 | 2941.8 | 58.3 | 22 | 97.2 | 94.2 | 86.6 | 105.8 | 41.1 | 12.9 | 8933.5 | 8986.2 | 8359.9 | 16444.1 | 16102.4 | 15692.7 | 1.841 | 1.792 | 1.877 | 0.573 | 0.58 | 0.56 | -2.7 | 3.81 | 2.8 | 0.59 | 0.573 | 0.623 | -2.48 | 4 | 2.62 | 0.59 | 0.543 | 0.585 | 3.39 | 3.31 | 3.16 | 0.618 | 0.542 | 0.549 | 3.15 | 2.85 | 2.89 | Poor_Thermal | 8359.9 | 15692.7 | 1.792 | 0.58 | 3.81 | 0.623 | 4 | 0.7756 | 0.9283 | 0.3754 | 0.9461 | 1 | 0.7491 | 0.6899 | 0.7792 | 0.7792 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H4
596 | 1660.6 | 871.4 | 132.5 | 171.4 | 32.8 | 1216.2 | 7682.1 | 31.3 | 47.5 | 102 | 104.5 | 92.6 | 112.1 | 43.6 | 28.5 | 2662.9 | 1996.6 | 2026.6 | 3521 | 2369.3 | 2429.2 | 1.322 | 1.187 | 1.199 | 0.882 | 0.926 | 0.819 | -8.13 | 9.03 | 7.58 | 0.734 | 0.821 | 0.741 | -6.14 | 4.72 | -6.33 | 0.75 | 0.847 | 0.786 | 5.13 | 8.29 | 5.01 | 0.747 | 0.877 | 0.869 | -7.36 | 8 | 7.62 | Very Poor_Mixed | 1996.6 | 2369.3 | 1.187 | 0.926 | 9.03 | 0.877 | 8.29 | 0.1221 | 0.6062 | 0.2031 | 0.4535 | 1 | 0.1735 | 0.2882 | 0.3824 | 0.3824 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
597 | 100 | 127 | 67.7 | 52.4 | 2.9 | 350 | 2500 | 59 | 20.8 | 76.4 | 75.2 | 73.7 | 82.7 | 35.3 | 13 | 10000 | 9049.4 | 10000 | 20000 | 16615.1 | 19246.5 | 2 | 1.836 | 1.925 | 0.5 | 0.5 | 0.5 | 2 | 2 | 2 | 0.524 | 0.535 | 0.528 | 3.23 | 2.49 | 2.17 | 0.5 | 0.507 | 0.5 | -2.11 | 2.6 | 2.46 | 0.549 | 0.515 | 0.54 | 2.12 | 2.61 | 2.23 | Good_Mixed | 9049.4 | 16615.1 | 1.836 | 0.5 | 2 | 0.549 | 3.23 | 0.9033 | 0.9605 | 0.9205 | 0.9438 | 1 | 1 | 0.863 | 0.9357 | 0.9357 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
598 | 799.2 | 486.3 | 103 | 121.7 | 16.6 | 818.5 | 5644.4 | 46.1 | 34 | 90.4 | 90.6 | 83.4 | 99.1 | 40.5 | 23.4 | 4719.7 | 5537.9 | 6088 | 6821.6 | 8566.6 | 8887.1 | 1.445 | 1.547 | 1.46 | 0.798 | 0.738 | 0.741 | -7.21 | 5.18 | 5.52 | 0.656 | 0.737 | 0.704 | 4.08 | -4.55 | -6 | 0.671 | 0.674 | 0.765 | -3.96 | 4.57 | 4.67 | 0.692 | 0.683 | 0.639 | 6.47 | -3.57 | 4.88 | Poor_Mixed | 4719.7 | 6821.6 | 1.445 | 0.798 | 7.21 | 0.765 | 6.47 | 0.4515 | 0.7461 | 0.4981 | 0.6348 | 1 | 0.3843 | 0.4626 | 0.581 | 0.581 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
599 | 823.8 | 452.5 | 99.1 | 113.6 | 13.3 | 736.9 | 5435.4 | 45.9 | 34.2 | 92 | 91.1 | 82 | 100.3 | 41 | 24.9 | 6060.4 | 6434.4 | 4622.5 | 9235.7 | 10533 | 7281.9 | 1.524 | 1.637 | 1.575 | 0.728 | 0.767 | 0.75 | 6.03 | 5.81 | 6.51 | 0.739 | 0.635 | 0.772 | 5.17 | 5.18 | -3.65 | 0.687 | 0.622 | 0.643 | -5.23 | 4.18 | 4.82 | 0.664 | 0.708 | 0.665 | -5.74 | -4.7 | 5.15 | Poor_Mixed | 4622.5 | 7281.9 | 1.524 | 0.767 | 6.51 | 0.772 | 5.74 | 0.4995 | 0.7438 | 0.484 | 0.5831 | 1 | 0.3843 | 0.4705 | 0.5902 | 0.5902 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
600 | 752.4 | 535 | 107.2 | 121.5 | 20.1 | 831.9 | 5504.5 | 45.4 | 34.7 | 92.3 | 91.8 | 81.4 | 100.1 | 39.2 | 27 | 6282.9 | 5680.6 | 5985.5 | 10090.4 | 9144.9 | 9690.6 | 1.606 | 1.61 | 1.619 | 0.784 | 0.72 | 0.765 | -6.15 | 5.43 | 5.86 | 0.603 | 0.645 | 0.725 | 4.11 | -3.75 | 4.25 | 0.668 | 0.654 | 0.759 | 4.63 | -4.35 | -5.78 | 0.651 | 0.672 | 0.725 | 5.3 | 3.65 | -4.88 | Poor_Mixed | 5680.6 | 9144.9 | 1.606 | 0.784 | 6.15 | 0.759 | 5.78 | 0.4252 | 0.7379 | 0.494 | 0.5083 | 1 | 0.3945 | 0.4882 | 0.5728 | 0.5728 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
601 | 957.5 | 546.4 | 107.4 | 131.1 | 20.5 | 861.5 | 5965.4 | 46.6 | 34.8 | 90.8 | 92.5 | 83.1 | 99.7 | 39.4 | 24.7 | 5017.6 | 6034.5 | 5344.7 | 7723.4 | 9604.2 | 7935.8 | 1.539 | 1.592 | 1.485 | 0.801 | 0.675 | 0.721 | 6.51 | -6.03 | -5.61 | 0.68 | 0.652 | 0.685 | 5.29 | 6.1 | -3.94 | 0.723 | 0.646 | 0.65 | 5.43 | 5.28 | 5.61 | 0.727 | 0.676 | 0.635 | -5.6 | -5.5 | 5.98 | Poor_Mixed | 5017.6 | 7723.4 | 1.485 | 0.801 | 6.51 | 0.727 | 6.1 | 0.3875 | 0.7368 | 0.4891 | 0.59 | 1 | 0.4036 | 0.4573 | 0.5625 | 0.5625 | Poor | 0 | 1 | DGA | 0 |  | C2H2
602 | 504.9 | 347.4 | 85.3 | 91.2 | 1 | 641.2 | 3564 | 55.7 | 29.1 | 82.8 | 77.7 | 76.5 | 87.3 | 35.6 | 15.1 | 8922.9 | 9419.4 | 421.5 | 16516.7 | 18583.1 | 618.2 | 1.851 | 1.973 | 1.467 | 0.891 | 0.917 | 0.873 | 8.2 | -8.68 | 8.29 | 0.548 | 0.637 | 0.614 | 4.07 | 4.29 | -3.24 | 0.647 | 0.615 | 0.621 | 5.24 | -3.71 | 2.87 | 0.582 | 0.603 | 0.603 | 3.55 | -4.32 | 3.09 | Critical_Winding_TD_Cap | 421.5 | 618.2 | 1.467 | 0.917 | 8.68 | 0.647 | 5.24 | 0.8028 | 0.8081 | 0.7849 | 0.8908 | 0.85 | 0.1525 | 0.6112 | 0.6881 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
603 | 1582 | 851.4 | 136.1 | 180.2 | 27.9 | 1209.2 | 7695.1 | 35.5 | 45.5 | 102.8 | 104.9 | 92.6 | 112.8 | 44.7 | 29.7 | 3215.9 | 1493.7 | 2552.6 | 4091.6 | 1602.1 | 2794.9 | 1.272 | 1.073 | 1.095 | 0.878 | 0.929 | 0.909 | -8.43 | 8.19 | -9.43 | 0.886 | 0.832 | 0.84 | 8.29 | -8.62 | -4.94 | 0.875 | 0.797 | 0.843 | 5.97 | 7 | 7.99 | 0.837 | 0.764 | 0.841 | 7.7 | 7.17 | 6.32 | Very Poor_Mixed | 1493.7 | 1602.1 | 1.073 | 0.929 | 9.43 | 0.886 | 8.62 | 0.1428 | 0.6251 | 0.1848 | 0.4089 | 1 | 0.1295 | 0.2304 | 0.3692 | 0.3692 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
604 | 865 | 489.5 | 98 | 107.2 | 18.2 | 812 | 5058 | 46.1 | 35 | 92.1 | 91 | 80 | 96.5 | 39.6 | 24.3 | 5964.7 | 5447.9 | 4754.4 | 8971.4 | 7950.3 | 7703.2 | 1.504 | 1.459 | 1.62 | 0.741 | 0.738 | 0.689 | 5.45 | 5.15 | 5.93 | 0.684 | 0.634 | 0.692 | 4.4 | 4.78 | -5.96 | 0.598 | 0.718 | 0.623 | -4.16 | 5.29 | 3.81 | 0.702 | 0.675 | 0.69 | 3.89 | 5.1 | 4.82 | Poor_Mixed | 4754.4 | 7703.2 | 1.459 | 0.741 | 5.93 | 0.718 | 5.96 | 0.4605 | 0.7345 | 0.5252 | 0.6039 | 1 | 0.4404 | 0.4931 | 0.5964 | 0.5964 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
605 | 231.2 | 142.5 | 69.9 | 55.3 | 73.3 | 369.9 | 3336.1 | 30.8 | 49.4 | 83.2 | 81.9 | 75 | 88.7 | 36.2 | 12.4 | 5606.3 | 4988.6 | 5964.9 | 8548.5 | 7896.5 | 9355.9 | 1.525 | 1.583 | 1.568 | 0.686 | 0.708 | 0.673 | 4.79 | 5.02 | 4.72 | 0.543 | 0.551 | 0.575 | 2.73 | 3.19 | -2.66 | 0.558 | 0.547 | 0.567 | -2.35 | 3.38 | 3.38 | 0.59 | 0.587 | 0.547 | 3.18 | 2.47 | 3.12 | Critical_Oil | 4988.6 | 7896.5 | 1.525 | 0.708 | 5.02 | 0.59 | 3.38 | 0.6358 | 0.5888 | 0.7458 | 0.9575 | 1 | 0.5087 | 0.725 | 0.7138 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
606 | 276 | 165.9 | 65 | 50 | 4.3 | 350 | 2721.8 | 58.1 | 22.2 | 78.5 | 78.6 | 73.2 | 82.7 | 36.1 | 11.3 | 10000 | 9072.7 | 9277.2 | 19838.2 | 17783.7 | 18107.2 | 1.984 | 1.96 | 1.952 | 0.5 | 0.5 | 0.536 | 2.41 | 2.03 | 3.16 | 0.529 | 0.528 | 0.519 | 2.26 | 2.58 | 2 | 0.509 | 0.514 | 0.5 | 2.24 | 2.55 | 2.5 | 0.509 | 0.5 | 0.537 | 2.7 | 2.26 | 2.41 | Good_Mixed | 9072.7 | 17783.7 | 1.952 | 0.536 | 3.16 | 0.537 | 2.7 | 0.8609 | 0.9238 | 0.8589 | 0.9802 | 1 | 0.9195 | 0.8826 | 0.9086 | 0.9086 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
607 | 609.9 | 430.9 | 95.2 | 104.2 | 13.1 | 717 | 4585.4 | 54.6 | 26.2 | 87.2 | 84.5 | 80.5 | 94.2 | 38.7 | 19.5 | 6481 | 6803.8 | 6810.2 | 10831 | 11682.4 | 11521.5 | 1.671 | 1.717 | 1.692 | 0.645 | 0.665 | 0.671 | 3.7 | -4.35 | 4.84 | 0.623 | 0.627 | 0.533 | 2.93 | 4.02 | -4.31 | 0.596 | 0.573 | 0.557 | 3.8 | 2.54 | 4.09 | 0.562 | 0.618 | 0.621 | -3.37 | 2.74 | 4.21 | Fair_Mixed | 6481 | 10831 | 1.671 | 0.671 | 4.84 | 0.627 | 4.31 | 0.544 | 0.8505 | 0.6166 | 0.7625 | 1 | 0.5691 | 0.6529 | 0.695 | 0.695 | Fair | 1 | 1 | DGA | 0 |  | C2H2
608 | 1486.4 | 982.4 | 141 | 187.5 | 32.8 | 1243.2 | 8246.2 | 35.6 | 43.6 | 103.8 | 102.7 | 90.3 | 111.6 | 43.9 | 32.1 | 2992.6 | 1507.9 | 1359.2 | 3273.1 | 1620.7 | 1509.6 | 1.094 | 1.075 | 1.111 | 0.942 | 0.971 | 0.919 | 8.55 | 9.16 | -8.25 | 0.721 | 0.923 | 0.729 | 8.49 | 8.13 | 7.58 | 0.841 | 0.785 | 0.755 | -7.86 | -6.44 | 8.12 | 0.834 | 0.855 | 0.792 | -7.8 | 9.17 | -8.35 | Very Poor_Mixed | 1359.2 | 1509.6 | 1.075 | 0.971 | 9.16 | 0.923 | 9.17 | 0.0922 | 0.6435 | 0.2165 | 0.3175 | 1 | 0.1044 | 0.2326 | 0.3543 | 0.3543 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
609 | 1675.5 | 982.4 | 142.5 | 186.4 | 31.9 | 1314.7 | 8380.8 | 31.9 | 48 | 102.5 | 104.2 | 92.5 | 113.2 | 43.9 | 30.7 | 1182.4 | 1562.1 | 2205.2 | 1267.9 | 1794.4 | 2552.1 | 1.072 | 1.149 | 1.157 | 0.865 | 0.886 | 0.92 | 8.31 | 8.19 | 8.34 | 0.771 | 0.785 | 0.868 | 6.78 | -7.58 | 7.3 | 0.778 | 0.902 | 0.94 | 5.89 | 9.66 | 7 | 0.974 | 0.818 | 0.912 | -7.28 | 6.01 | 8.19 | Very Poor_Mixed | 1182.4 | 1267.9 | 1.072 | 0.92 | 8.34 | 0.974 | 9.66 | 0.0728 | 0.6016 | 0.1948 | 0.3711 | 1 | 0.1605 | 0.2027 | 0.3474 | 0.3474 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
610 | 116.6 | 169.9 | 73 | 54.1 | 1.1 | 361.5 | 3129.9 | 57.5 | 23.1 | 76 | 77.1 | 70.4 | 80.6 | 35.2 | 13.5 | 9612.6 | 9803.3 | 9989.6 | 18550 | 19606.5 | 19128.7 | 1.93 | 2 | 1.915 | 0.72 | 0.717 | 0.748 | -5.46 | 5.04 | 6.17 | 0.5 | 0.548 | 0.5 | 2.57 | 2.35 | 2.43 | 0.539 | 0.5 | 0.507 | 2.19 | 2.49 | -2.48 | 0.542 | 0.5 | 0.5 | 2.13 | -2.3 | -2.1 | Fair_Winding_TD_Cap | 9612.6 | 18550 | 1.915 | 0.748 | 6.17 | 0.548 | 2.57 | 0.9462 | 0.9047 | 0.9424 | 0.9318 | 1 | 0.4326 | 0.9087 | 0.8701 | 0.8701 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
611 | 933.4 | 552.7 | 108.4 | 130.6 | 16 | 905.2 | 5529.5 | 46 | 35 | 89.9 | 91.9 | 81 | 97 | 38.5 | 26.5 | 5130.7 | 6059.9 | 5921.2 | 7794.1 | 9327.1 | 9520.7 | 1.519 | 1.539 | 1.608 | 0.767 | 0.802 | 0.718 | 5.93 | 6.47 | 5.85 | 0.731 | 0.684 | 0.607 | -5.16 | 4.71 | 5.03 | 0.727 | 0.709 | 0.644 | 4.77 | 5.85 | 3.64 | 0.69 | 0.626 | 0.768 | 4.38 | 5.12 | -4.73 | Poor_Mixed | 5130.7 | 7794.1 | 1.519 | 0.802 | 6.47 | 0.768 | 5.85 | 0.4155 | 0.7345 | 0.5314 | 0.5264 | 1 | 0.3749 | 0.466 | 0.5678 | 0.5678 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
612 | 1408.9 | 825.9 | 130.8 | 168.4 | 33.8 | 1163.9 | 8334.6 | 38.1 | 41.9 | 104.7 | 104.9 | 92.6 | 115.3 | 42.5 | 29.7 | 3038.5 | 2742.9 | 3288.5 | 3917.6 | 3281.1 | 4308.1 | 1.289 | 1.196 | 1.31 | 0.893 | 0.838 | 0.864 | 8.48 | 7.45 | 7.69 | 0.888 | 0.878 | 0.884 | -6.74 | 8.28 | 7.37 | 0.747 | 0.899 | 0.738 | -7.16 | 8.91 | -6.35 | 0.814 | 0.836 | 0.828 | 8.39 | -6.98 | 5.9 | Very Poor_Mixed | 2742.9 | 3281.1 | 1.196 | 0.893 | 8.48 | 0.899 | 8.91 | 0.142 | 0.6604 | 0.1773 | 0.4089 | 1 | 0.1998 | 0.2242 | 0.3813 | 0.3813 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
613 | 1393.2 | 856 | 132.2 | 152.5 | 31.4 | 1225.7 | 7935.8 | 36 | 42.4 | 102.7 | 103.8 | 92.9 | 112.2 | 43.8 | 32.7 | 3412.8 | 1919.4 | 1612.5 | 4608.8 | 2307.8 | 1788.6 | 1.35 | 1.202 | 1.109 | 0.932 | 0.902 | 0.915 | -9.19 | 8.27 | 8.66 | 0.814 | 0.858 | 0.78 | 6.83 | 5.52 | 5.27 | 0.874 | 0.768 | 0.852 | 7.57 | 8.16 | 6.59 | 0.73 | 0.724 | 0.827 | 7.03 | 7.54 | 5.38 | Very Poor_Mixed | 1612.5 | 1788.6 | 1.109 | 0.932 | 9.19 | 0.874 | 8.16 | 0.1614 | 0.6554 | 0.1994 | 0.2943 | 1 | 0.1205 | 0.2768 | 0.3804 | 0.3804 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
614 | 100 | 129.4 | 71.1 | 62 | 1 | 370.5 | 2817.4 | 56.1 | 21.1 | 75 | 75.4 | 70.1 | 81.6 | 35.1 | 11.9 | 9552.9 | 8742.7 | 8608.7 | 18131.2 | 16584.1 | 14736.9 | 1.898 | 1.897 | 1.712 | 0.5 | 0.5 | 0.5 | 2.19 | -2 | -2.11 | 0.5 | 0.531 | 0.5 | 2.2 | 2.35 | 2 | 0.5 | 0.552 | 0.528 | -2 | -2.05 | 2.08 | 0.51 | 0.5 | 0.5 | 2.11 | -2.05 | 2 | Good_Mixed | 8608.7 | 14736.9 | 1.712 | 0.5 | 2.19 | 0.552 | 2.35 | 0.9646 | 0.9514 | 0.9809 | 0.9682 | 1 | 0.9895 | 0.9282 | 0.9674 | 0.9674 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
615 | 1552.9 | 871.2 | 145.8 | 184.3 | 33.3 | 1239.8 | 8829.7 | 30.6 | 48.9 | 104.1 | 108.7 | 92.2 | 114.1 | 43.5 | 32.9 | 1967.7 | 2017.4 | 2247.2 | 2331.8 | 2250.7 | 2714.1 | 1.185 | 1.116 | 1.208 | 0.98 | 0.904 | 0.928 | 8.64 | 8.49 | -8.92 | 0.932 | 0.879 | 0.824 | 7.8 | 5.4 | -8.9 | 0.899 | 0.762 | 0.838 | 5.75 | 6.44 | 5.78 | 0.884 | 0.784 | 0.773 | 8.25 | 6.54 | 7.03 | Very Poor_Mixed | 1967.7 | 2250.7 | 1.116 | 0.98 | 8.92 | 0.932 | 8.9 | 0.0886 | 0.5933 | 0.1611 | 0.2865 | 1 | 0.1075 | 0.2332 | 0.3408 | 0.3408 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
616 | 280.6 | 244.4 | 79.3 | 69.9 | 1.8 | 514.8 | 2987.4 | 30.6 | 56.8 | 82.8 | 81.6 | 77.9 | 88.2 | 35.9 | 19.2 | 4609.4 | 4406.2 | 4109.5 | 6072.3 | 6243.4 | 5692.1 | 1.317 | 1.417 | 1.385 | 0.668 | 0.697 | 0.671 | 4.89 | -4.23 | 5.15 | 0.62 | 0.542 | 0.645 | 3.26 | 2.78 | -2.89 | 0.622 | 0.68 | 0.599 | 5.03 | 3.13 | 4.06 | 0.683 | 0.61 | 0.586 | 3.36 | 3.13 | -3.9 | Critical_Oil | 4109.5 | 5692.1 | 1.317 | 0.697 | 5.15 | 0.683 | 5.03 | 0.8277 | 0.5833 | 0.7342 | 0.7718 | 1 | 0.5238 | 0.6074 | 0.7316 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
617 | 367.6 | 231.6 | 78.6 | 80.8 | 7.8 | 537.5 | 3741.3 | 52.8 | 26.5 | 79.5 | 80 | 74.9 | 85.7 | 37.1 | 15.7 | 7564.1 | 7990.9 | 7927.5 | 14040 | 14208.9 | 14089.9 | 1.856 | 1.778 | 1.777 | 0.662 | 0.605 | 0.589 | 3.87 | -3.92 | 3.92 | 0.592 | 0.524 | 0.621 | -2.9 | 4.54 | -3.06 | 0.594 | 0.666 | 0.589 | 3.86 | -2.6 | 3.48 | 0.555 | 0.58 | 0.535 | -3.77 | -3.92 | 3.09 | Fair_Mixed | 7564.1 | 14040 | 1.777 | 0.662 | 3.92 | 0.666 | 4.54 | 0.7033 | 0.8458 | 0.8033 | 0.8746 | 1 | 0.6388 | 0.6697 | 0.7714 | 0.7714 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
618 | 1557.7 | 898.4 | 131.7 | 185.3 | 33 | 1228.1 | 7564.6 | 33.8 | 47.2 | 103.2 | 101.3 | 93.5 | 114.1 | 43.4 | 29.6 | 2523.3 | 1242.1 | 2243.2 | 2969.4 | 1354.4 | 2678.6 | 1.177 | 1.09 | 1.194 | 0.877 | 0.876 | 0.884 | -7.43 | -8.24 | -8.27 | 0.735 | 0.824 | 0.787 | 6.66 | 6.69 | 7.7 | 0.75 | 0.817 | 0.86 | -7.98 | -6.06 | 8.46 | 0.851 | 0.813 | 0.783 | 5.64 | 8.2 | 7.68 | Very Poor_Mixed | 1242.1 | 1354.4 | 1.09 | 0.884 | 8.27 | 0.86 | 8.46 | 0.1148 | 0.609 | 0.2007 | 0.4126 | 1 | 0.1839 | 0.2575 | 0.3746 | 0.3746 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
619 | 901.9 | 500.2 | 103.4 | 120.1 | 18.5 | 967.6 | 5316.5 | 44.4 | 35.5 | 92 | 88.2 | 80.6 | 94.8 | 39.6 | 23.3 | 4896.9 | 6412.9 | 5268.1 | 7176 | 9953.1 | 7968.9 | 1.465 | 1.552 | 1.513 | 0.746 | 0.726 | 0.72 | 6.01 | 5.35 | 5.79 | 0.675 | 0.704 | 0.674 | 4.3 | 3.72 | 4.83 | 0.63 | 0.672 | 0.636 | 4.4 | 4.63 | 4.03 | 0.658 | 0.66 | 0.639 | -4.37 | 4.56 | 4.48 | Poor_Mixed | 4896.9 | 7176 | 1.465 | 0.746 | 6.01 | 0.704 | 4.83 | 0.4163 | 0.7287 | 0.549 | 0.6382 | 1 | 0.4214 | 0.5125 | 0.5896 | 0.5896 | Poor | 0 | 1 | DGA | 0 |  | C2H2
620 | 1599.1 | 889.9 | 142.9 | 191.7 | 34 | 1331.8 | 8545.8 | 33.8 | 45.6 | 107.9 | 106.3 | 93.9 | 117.5 | 44.1 | 33.6 | 1796.1 | 1029.7 | 1021.2 | 1955.6 | 1200 | 1200 | 1.089 | 1.165 | 1.175 | 0.99 | 0.962 | 0.99 | 9.76 | 8.98 | 9.62 | 0.776 | 0.926 | 0.811 | -8.89 | 5.79 | 8.15 | 0.742 | 0.856 | 0.754 | 6.61 | 7.68 | 7.94 | 0.881 | 0.792 | 0.79 | 5.34 | 8.51 | -7.2 | Very Poor_Mixed | 1021.2 | 1200 | 1.089 | 0.99 | 9.76 | 0.926 | 8.89 | 0.0703 | 0.6241 | 0.1223 | 0.2591 | 1 | 0.0397 | 0.2436 | 0.3271 | 0.3271 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
621 | 282.3 | 130.8 | 70.7 | 57.5 | 3.6 | 550.7 | 2776.9 | 13 | 20 | 82.1 | 83.6 | 76.9 | 87.4 | 37.4 | 17.4 | 8478.1 | 9098.9 | 8676.8 | 14759.9 | 17634.9 | 15682 | 1.741 | 1.938 | 1.807 | 0.935 | 0.863 | 0.874 | 9.84 | 8.38 | 8.09 | 0.545 | 0.521 | 0.552 | 2.52 | 2.87 | 2.26 | 0.505 | 0.501 | 0.506 | -2.25 | 2.31 | 2.26 | 0.527 | 0.517 | 0.505 | 2 | 2.7 | -2.14 | Critical_Winding_TD_Cap | 8478.1 | 14759.9 | 1.741 | 0.935 | 9.84 | 0.552 | 2.87 | 0.8191 | 0.4167 | 0.7274 | 0.8262 | 1 | 0.1358 | 0.8695 | 0.7043 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
622 | 926.2 | 540.3 | 106.3 | 113.5 | 22.4 | 845.8 | 5643 | 47.4 | 33.3 | 94.3 | 92.5 | 83.8 | 99.1 | 39.6 | 24.5 | 4936.4 | 5386.2 | 5583.5 | 7759.1 | 8076.9 | 8590.7 | 1.572 | 1.5 | 1.539 | 0.691 | 0.776 | 0.736 | 5.5 | -5.8 | 5.67 | 0.738 | 0.7 | 0.743 | 3.45 | 4.58 | -4.43 | 0.656 | 0.741 | 0.673 | -5.63 | -4.63 | 3.62 | 0.69 | 0.69 | 0.738 | 5.15 | 4.98 | -4.89 | Poor_Mixed | 4936.4 | 7759.1 | 1.5 | 0.776 | 5.8 | 0.743 | 5.63 | 0.4031 | 0.7544 | 0.4642 | 0.597 | 1 | 0.4223 | 0.4483 | 0.5674 | 0.5674 | Poor | 0 | 1 | DGA | 0 |  | C2H2
623 | 265.4 | 244.3 | 73.6 | 95.6 | 2.8 | 536.6 | 3542.4 | 58 | 23.4 | 93.1 | 90.9 | 85.3 | 102.5 | 39.9 | 13.9 | 9494.8 | 8672.1 | 6289.5 | 17964.4 | 16547 | 11082.2 | 1.892 | 1.908 | 1.762 | 0.564 | 0.583 | 0.558 | 3.48 | 2.72 | 2.62 | 0.536 | 0.585 | 0.585 | -3.63 | 3.7 | -2.46 | 0.614 | 0.571 | 0.569 | -2.68 | 3.35 | -2.89 | 0.59 | 0.545 | 0.555 | 2.98 | 3.76 | -2.84 | Poor_Thermal | 6289.5 | 11082.2 | 1.762 | 0.583 | 3.48 | 0.614 | 3.76 | 0.7693 | 0.8988 | 0.4539 | 0.9219 | 1 | 0.7637 | 0.6992 | 0.7844 | 0.7844 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
624 | 996.7 | 610.3 | 108.5 | 131.1 | 21.3 | 907.9 | 5589.6 | 58.1 | 20.9 | 78.9 | 78.4 | 72 | 85.7 | 35 | 13.5 | 9112.7 | 9264.6 | 8841.1 | 17331.9 | 17734.6 | 16922.4 | 1.902 | 1.914 | 1.914 | 0.558 | 0.566 | 0.549 | 2.55 | 2.93 | -3.46 | 0.55 | 0.521 | 0.505 | -2.26 | 2.02 | -3.66 | 0.537 | 0.568 | 0.5 | 2 | 2 | 2.44 | 0.5 | 0.507 | 0.53 | -2.27 | 2 | 2 | Poor_DGA | 8841.1 | 16922.4 | 1.902 | 0.566 | 3.46 | 0.568 | 3.66 | 0.3704 | 0.9574 | 0.8569 | 0.9318 | 1 | 0.7765 | 0.8724 | 0.7655 | 0.7655 | Fair | 1 | 1 | DGA | 0 |  | C2H2
625 | 213.9 | 218.1 | 67.2 | 62.8 | 1.3 | 358.6 | 2903.9 | 56.8 | 24.4 | 79.8 | 77.4 | 73 | 84.2 | 36.5 | 20.7 | 8839.5 | 9426.7 | 9727.2 | 16526.7 | 17469.8 | 18706 | 1.87 | 1.853 | 1.923 | 0.524 | 0.506 | 0.549 | 2.16 | 2.19 | 2.11 | 0.577 | 0.565 | 0.578 | -2.28 | 2.79 | 2.73 | 0.543 | 0.5 | 0.528 | 2 | -2.74 | 2.82 | 0.516 | 0.531 | 0.5 | -3.6 | 2.26 | 2.68 | Fair_Age | 8839.5 | 16526.7 | 1.853 | 0.549 | 2.19 | 0.578 | 3.6 | 0.9047 | 0.8804 | 0.8512 | 0.7244 | 1 | 0.8982 | 0.8154 | 0.8857 | 0.8857 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
626 | 899.1 | 509.3 | 105.6 | 107.4 | 15.6 | 767.4 | 5398.2 | 47.8 | 33 | 91.5 | 91.2 | 83.3 | 98.5 | 39.4 | 23.4 | 5583 | 5984.4 | 4052.7 | 9129 | 8513.2 | 6005.7 | 1.635 | 1.423 | 1.482 | 0.707 | 0.752 | 0.699 | 4.98 | 6.09 | 4.56 | 0.757 | 0.689 | 0.651 | -4.7 | 4.64 | 5.32 | 0.748 | 0.708 | 0.66 | 4.98 | -4.05 | 5.33 | 0.675 | 0.703 | 0.735 | 5.25 | 5.56 | 4.84 | Poor_Mixed | 4052.7 | 6005.7 | 1.423 | 0.752 | 6.09 | 0.757 | 5.56 | 0.4689 | 0.7581 | 0.4977 | 0.6348 | 1 | 0.4606 | 0.4401 | 0.5934 | 0.5934 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
627 | 967.5 | 606.1 | 104.4 | 133.9 | 18.7 | 903.2 | 5471.2 | 46.1 | 34.4 | 92.7 | 92.8 | 84.7 | 96.4 | 39.7 | 24.4 | 6137.3 | 6658 | 4591.1 | 9595.6 | 10952.9 | 6453.6 | 1.563 | 1.645 | 1.406 | 0.682 | 0.755 | 0.728 | 5 | 6.58 | -6.13 | 0.61 | 0.638 | 0.56 | -4.36 | -4.3 | 5.22 | 0.695 | 0.691 | 0.626 | 5.61 | 3.23 | 4.93 | 0.675 | 0.647 | 0.599 | 4.25 | -3.72 | 4.38 | Poor_Mixed | 4591.1 | 6453.6 | 1.406 | 0.755 | 6.58 | 0.695 | 5.61 | 0.3905 | 0.7414 | 0.4796 | 0.6005 | 1 | 0.4201 | 0.5444 | 0.5814 | 0.5814 | Poor | 0 | 1 | DGA | 0 |  | C2H2
628 | 1742.2 | 981.7 | 148.3 | 193.6 | 33.6 | 1365.4 | 8202.6 | 52.8 | 28.4 | 86.9 | 86 | 77.1 | 91.5 | 38.9 | 16.8 | 7791.1 | 9139.3 | 8925.5 | 14263.1 | 16964.8 | 8220.1 | 1.831 | 1.856 | 0.921 | 0.538 | 0.593 | 0.538 | -3.55 | 3.56 | 3.22 | 0.502 | 0.517 | 0.517 | -3.39 | 3.57 | 2.84 | 0.557 | 0.563 | 0.566 | 3.4 | 2.81 | 2.22 | 0.575 | 0.521 | 0.53 | -2.6 | 3.38 | -3.08 | Critical_DGA | 7791.1 | 8220.1 | 0.921 | 0.593 | 3.56 | 0.575 | 3.57 | 0.047 | 0.8178 | 0.6432 | 0.8436 | 0.8125 | 0.7506 | 0.7832 | 0.5924 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
629 | 1678 | 908.9 | 139.1 | 176 | 29.5 | 1244.5 | 8110.8 | 52.4 | 29.9 | 83.7 | 82.7 | 78.1 | 90 | 37.4 | 12.3 | 82.4 | 7747.3 | 8261.7 | 107.5 | 13445.5 | 15209.7 | 1.305 | 1.736 | 1.841 | 0.597 | 0.563 | 0.583 | 3.58 | 2.7 | 3.15 | 0.596 | 0.593 | 0.578 | -3.17 | 3.94 | 2.81 | 0.629 | 0.633 | 0.559 | 3.21 | 2.52 | 2.72 | 0.556 | 0.547 | 0.63 | -3.18 | 2.49 | 3.84 | Critical_DGA | 82.4 | 107.5 | 1.305 | 0.597 | 3.58 | 0.633 | 3.94 | 0.114 | 0.7973 | 0.7004 | 0.9597 | 0.85 | 0.7327 | 0.6695 | 0.6013 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
630 | 158.7 | 163.1 | 69.1 | 55.5 | 1 | 540.3 | 3117.3 | 54.7 | 25.2 | 81.7 | 81.3 | 111 | 86.4 | 38 | 10.9 | 1354.5 | 1608.9 | 1788.4 | 1403.3 | 1706.8 | 1938.1 | 1.036 | 1.061 | 1.084 | 0.733 | 0.713 | 0.649 | 5.41 | -5.42 | 4.68 | 0.549 | 0.524 | 0.512 | 2.49 | 2.74 | -3.17 | 0.555 | 0.554 | 0.518 | 2.74 | 3.12 | 3.03 | 0.535 | 0.541 | 0.535 | 2.69 | -2.37 | -2.67 | Critical_IR_PI | 1354.5 | 1403.3 | 1.036 | 0.733 | 5.42 | 0.555 | 3.17 | 0.9326 | 0.8666 | 0.6121 | 0.9875 | 1 | 0.4825 | 0.7934 | 0.8181 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | OTI
631 | 956.6 | 498.2 | 103.9 | 125.6 | 18.3 | 856 | 5200.9 | 46.2 | 33.5 | 90.1 | 90.4 | 81.8 | 99.6 | 38.9 | 25.6 | 5495.7 | 5601.9 | 5499.2 | 7911.6 | 8304.1 | 8415.4 | 1.44 | 1.482 | 1.53 | 0.729 | 0.793 | 0.705 | -5.11 | 6.45 | 5.16 | 0.663 | 0.735 | 0.762 | 5.18 | 4.33 | 3.83 | 0.699 | 0.723 | 0.631 | 5.27 | -4.6 | 3.53 | 0.674 | 0.645 | 0.709 | 4.72 | 4.08 | -4.37 | Poor_Mixed | 5495.7 | 7911.6 | 1.44 | 0.793 | 6.45 | 0.762 | 5.27 | 0.4225 | 0.752 | 0.5192 | 0.5584 | 1 | 0.4205 | 0.4718 | 0.5795 | 0.5795 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
632 | 925.1 | 625.6 | 104.7 | 107.8 | 14.8 | 769.2 | 5533.7 | 57 | 23.2 | 80.7 | 79.3 | 74.1 | 85.8 | 36.6 | 12.6 | 8447.6 | 10000 | 9953.8 | 15699.1 | 20000 | 19296.1 | 1.858 | 2 | 1.939 | 0.564 | 0.541 | 0.569 | 2.71 | -2.18 | 3.17 | 0.58 | 0.518 | 0.629 | 2.25 | 2.4 | 3.39 | 0.524 | 0.552 | 0.6 | 3.09 | -2 | 3.66 | 0.556 | 0.507 | 0.561 | 3.41 | 2.43 | 2.32 | Poor_DGA | 8447.6 | 15699.1 | 1.858 | 0.569 | 3.17 | 0.629 | 3.66 | 0.4579 | 0.9027 | 0.8075 | 0.953 | 1 | 0.7976 | 0.7542 | 0.7586 | 0.7586 | Fair | 1 | 1 | DGA | 0 |  | C2H2
633 | 1111.5 | 609 | 107 | 132 | 24.5 | 958.8 | 5855.2 | 56.1 | 26 | 81.2 | 83.3 | 75.9 | 86.2 | 36.3 | 11.1 | 9987 | 9328.3 | 9539.6 | 19420 | 17855.9 | 18714.9 | 1.945 | 1.914 | 1.962 | 0.556 | 0.522 | 0.551 | 3.04 | 3.16 | -2.49 | 0.587 | 0.577 | 0.595 | -3.03 | 2.77 | -2.88 | 0.563 | 0.534 | 0.549 | 3.02 | 3.7 | 3.62 | 0.585 | 0.549 | 0.626 | 3.43 | 3.89 | 3.21 | Poor_DGA | 9328.3 | 17855.9 | 1.914 | 0.556 | 3.16 | 0.626 | 3.89 | 0.3358 | 0.8536 | 0.756 | 0.984 | 1 | 0.8075 | 0.6906 | 0.7085 | 0.7085 | Fair | 1 | 1 | DGA | 0 |  | C2H2
634 | 1616.6 | 868 | 134.7 | 178.7 | 30 | 1293.8 | 8009.4 | 34.7 | 44.6 | 104.5 | 105 | 92.2 | 113.2 | 45 | 33.4 | 835.5 | 690 | 1442 | 1200 | 1200 | 1549 | 1.436 | 1.739 | 1.074 | 0.912 | 0.93 | 0.964 | 8.8 | -8.61 | 8.82 | 0.806 | 0.879 | 0.89 | 6.74 | 5.7 | 7.35 | 0.822 | 0.849 | 0.755 | 9.18 | -6.21 | -6.83 | 0.896 | 0.776 | 0.918 | 8.11 | 8.06 | -5.52 | Very Poor_Mixed | 690 | 1200 | 1.074 | 0.964 | 8.82 | 0.918 | 9.18 | 0.1177 | 0.6338 | 0.1727 | 0.267 | 1 | 0.1056 | 0.2247 | 0.3513 | 0.3513 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
635 | 293.2 | 240.4 | 78.2 | 72.7 | 3.6 | 509 | 2986 | 55.5 | 25.4 | 78.9 | 81.1 | 72.6 | 83.9 | 36.4 | 15.4 | 9074.7 | 7936.1 | 8023.4 | 17327.2 | 13648.7 | 14720.5 | 1.909 | 1.72 | 1.835 | 0.739 | 0.75 | 0.779 | 6.75 | 6.04 | -6.22 | 0.569 | 0.6 | 0.515 | 2.72 | -3.46 | 3.08 | 0.544 | 0.55 | 0.544 | 2.43 | -2.46 | -2 | 0.53 | 0.535 | 0.589 | 2.67 | 3.25 | 2 | Poor_Winding_TD_Cap | 7936.1 | 13648.7 | 1.72 | 0.779 | 6.75 | 0.6 | 3.46 | 0.7834 | 0.8633 | 0.8308 | 0.8828 | 1 | 0.3659 | 0.7641 | 0.7754 | 0.7754 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
636 | 1582.5 | 917.1 | 138.3 | 184.8 | 31.6 | 1301 | 8436.1 | 32.3 | 48 | 107.4 | 106.4 | 97.1 | 115.5 | 44.4 | 35.8 | 1264.8 | 2665.8 | 2171.4 | 1394.2 | 3107.1 | 2458.5 | 1.102 | 1.166 | 1.132 | 0.959 | 0.982 | 0.894 | -9.35 | -9.54 | -8.54 | 0.867 | 0.768 | 0.894 | 6.8 | 8.35 | 7.27 | 0.825 | 0.827 | 0.758 | 7.44 | 4.68 | 6.83 | 0.971 | 0.734 | 0.766 | -6.98 | -4.77 | 8.43 | Very Poor_Mixed | 1264.8 | 1394.2 | 1.102 | 0.982 | 9.54 | 0.971 | 8.43 | 0.0932 | 0.6016 | 0.1147 | 0.1718 | 1 | 0.0793 | 0.2531 | 0.3322 | 0.3322 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
637 | 802.6 | 522.2 | 89.8 | 110.1 | 13.6 | 841.3 | 5089.8 | 58 | 22.9 | 78.5 | 78.5 | 71.7 | 80 | 35.1 | 13.6 | 9838.3 | 9257.7 | 10000 | 19210.3 | 17754.8 | 20000 | 1.953 | 1.918 | 2 | 0.587 | 0.518 | 0.53 | -3.16 | -2 | 2.5 | 0.501 | 0.546 | 0.531 | 2.71 | 3.03 | -2.63 | 0.52 | 0.551 | 0.529 | 2.59 | 2 | 2.13 | 0.543 | 0.515 | 0.539 | -2.79 | 2.12 | -3.08 | Fair_DGA | 9257.7 | 17754.8 | 1.918 | 0.587 | 3.16 | 0.551 | 3.08 | 0.4913 | 0.9088 | 0.8907 | 0.9294 | 1 | 0.8355 | 0.8233 | 0.7926 | 0.7926 | Fair | 1 | 1 | DGA | 0 |  | C2H2
638 | 1571.4 | 828.8 | 134.9 | 188.2 | 32.1 | 1183.9 | 7892.1 | 36.1 | 44.5 | 104.6 | 102.9 | 95 | 112 | 44.3 | 31.6 | 1034.2 | 1652.3 | 690 | 1200 | 1819.7 | 1200 | 1.16 | 1.101 | 1.739 | 0.952 | 0.924 | 0.963 | 8.92 | 9.01 | 8.92 | 0.931 | 0.913 | 0.846 | 6.83 | -8.22 | -6.32 | 0.885 | 0.869 | 0.845 | 7.5 | 8.4 | 8.68 | 0.71 | 0.88 | 0.912 | -6.84 | 5.86 | 5.56 | Very Poor_Mixed | 690 | 1200 | 1.101 | 0.963 | 9.01 | 0.931 | 8.68 | 0.1213 | 0.6347 | 0.1794 | 0.3368 | 1 | 0.0877 | 0.2035 | 0.3502 | 0.3502 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
639 | 942.9 | 579.5 | 100.6 | 121.4 | 22.1 | 852.8 | 5497.1 | 46.5 | 35 | 90.8 | 91.6 | 81.3 | 97.4 | 39.9 | 25.3 | 3854.9 | 5982.6 | 5378.3 | 5272 | 9030.1 | 7792.8 | 1.368 | 1.509 | 1.449 | 0.768 | 0.726 | 0.789 | 6.36 | 5.58 | -6.65 | 0.63 | 0.642 | 0.71 | 4.04 | 5.15 | -5.12 | 0.644 | 0.671 | 0.682 | 5.14 | -5.73 | 4.11 | 0.725 | 0.687 | 0.713 | 4.73 | 4.48 | 5.78 | Poor_Mixed | 3854.9 | 5272 | 1.368 | 0.789 | 6.65 | 0.725 | 5.78 | 0.3962 | 0.7345 | 0.5147 | 0.569 | 1 | 0.3697 | 0.4712 | 0.5637 | 0.5637 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
640 | 196 | 270.6 | 71.6 | 64.7 | 1.3 | 381.7 | 3067 | 60 | 22.2 | 79.7 | 82.4 | 74.7 | 87.8 | 37.8 | 16.5 | 8973 | 8808.8 | 8283.9 | 17178.6 | 15781.5 | 15273.2 | 1.914 | 1.792 | 1.844 | 0.774 | 0.782 | 0.777 | 5.71 | 6.04 | 6.46 | 0.549 | 0.5 | 0.557 | 2.24 | 2.6 | -2 | 0.5 | 0.574 | 0.524 | 2.66 | 3.33 | 2.38 | 0.54 | 0.53 | 0.556 | 2.92 | 3.28 | 3.48 | Poor_Winding_TD_Cap | 8283.9 | 15273.2 | 1.792 | 0.782 | 6.46 | 0.574 | 3.48 | 0.8889 | 0.9238 | 0.7689 | 0.8522 | 1 | 0.3623 | 0.8098 | 0.8091 | 0.8091 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
641 | 833.6 | 418.9 | 101.8 | 118 | 17.7 | 805.4 | 4968.1 | 45.6 | 34.6 | 93.3 | 89.5 | 83 | 97.7 | 38.1 | 24.8 | 3986.6 | 6170.5 | 5872.4 | 5744.4 | 9440 | 9187 | 1.441 | 1.53 | 1.564 | 0.768 | 0.772 | 0.777 | 6.02 | 5.86 | 7 | 0.625 | 0.723 | 0.648 | 5.68 | -4.34 | 5.27 | 0.669 | 0.641 | 0.662 | 4.92 | -5.8 | 5.35 | 0.696 | 0.722 | 0.597 | 5.84 | -5.19 | 4.49 | Poor_Mixed | 3986.6 | 5744.4 | 1.441 | 0.777 | 7 | 0.723 | 5.84 | 0.4623 | 0.7391 | 0.5112 | 0.5865 | 1 | 0.3546 | 0.4786 | 0.5805 | 0.5805 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
642 | 1001.6 | 577.3 | 109.9 | 113.8 | 20.7 | 917.7 | 5108.8 | 47.1 | 33.1 | 91.2 | 95.5 | 82.1 | 98.9 | 38.8 | 25.7 | 6001.2 | 5691.9 | 6541.7 | 9545.2 | 9432 | 10017.2 | 1.591 | 1.657 | 1.531 | 0.804 | 0.688 | 0.719 | -6.88 | 5.48 | -5.98 | 0.693 | 0.671 | 0.716 | 4.75 | 4 | 4.18 | 0.672 | 0.597 | 0.639 | 4.22 | 4.11 | 5.24 | 0.747 | 0.681 | 0.689 | -6.19 | 4.78 | 5.58 | Poor_Mixed | 5691.9 | 9432 | 1.531 | 0.804 | 6.88 | 0.747 | 6.19 | 0.3964 | 0.7568 | 0.4819 | 0.5549 | 1 | 0.396 | 0.4775 | 0.5672 | 0.5672 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
643 | 911.1 | 529.5 | 105.4 | 115.9 | 16.6 | 831.1 | 4795.6 | 46.5 | 34.7 | 94.6 | 88.4 | 83.8 | 99.5 | 39.6 | 23.1 | 5353.8 | 7035.1 | 6149.8 | 8062.9 | 12282.1 | 9497.7 | 1.506 | 1.746 | 1.544 | 0.714 | 0.693 | 0.768 | 5.46 | 4.79 | -6.68 | 0.684 | 0.687 | 0.616 | 3.06 | 4.63 | 4.03 | 0.674 | 0.68 | 0.691 | 4.66 | 4.48 | -2.8 | 0.66 | 0.673 | 0.724 | 5.42 | 3.83 | 4.52 | Poor_Mixed | 5353.8 | 8062.9 | 1.506 | 0.768 | 6.68 | 0.724 | 5.42 | 0.4486 | 0.7379 | 0.4873 | 0.645 | 1 | 0.4317 | 0.5024 | 0.5926 | 0.5926 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
644 | 852.5 | 490 | 100.5 | 117.1 | 20.7 | 870.6 | 5812.3 | 45.5 | 33.6 | 90.5 | 93.8 | 83.3 | 97.8 | 39.7 | 27.8 | 5129 | 5002.4 | 6223.6 | 7664.5 | 7270.8 | 9537.8 | 1.494 | 1.453 | 1.533 | 0.738 | 0.769 | 0.801 | 6.14 | 6.16 | -6.68 | 0.706 | 0.748 | 0.632 | 5.4 | -4.6 | 6.54 | 0.706 | 0.692 | 0.682 | 4.9 | 5.2 | -4.65 | 0.71 | 0.699 | 0.661 | -4.12 | 5.17 | -5.39 | Poor_Mixed | 5002.4 | 7270.8 | 1.453 | 0.801 | 6.68 | 0.748 | 6.54 | 0.4198 | 0.7509 | 0.4892 | 0.4793 | 1 | 0.3555 | 0.4465 | 0.5581 | 0.5581 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
645 | 898 | 514.6 | 102.4 | 118.9 | 21.3 | 811.3 | 5303.4 | 46.9 | 33.7 | 88.3 | 89.5 | 80.5 | 100 | 39 | 26.7 | 5100.7 | 6234.2 | 5264.9 | 7706.1 | 9903.7 | 8018.1 | 1.511 | 1.589 | 1.523 | 0.778 | 0.831 | 0.746 | 5.58 | 6.51 | 5.83 | 0.696 | 0.697 | 0.701 | -4.66 | -3.57 | 6.1 | 0.649 | 0.649 | 0.735 | 5.02 | -4.25 | 5.3 | 0.78 | 0.672 | 0.633 | 4.11 | 4.79 | -4.4 | Poor_Mixed | 5100.7 | 7706.1 | 1.511 | 0.831 | 6.51 | 0.78 | 6.1 | 0.4197 | 0.7497 | 0.5431 | 0.5192 | 1 | 0.3624 | 0.4665 | 0.5698 | 0.5698 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
646 | 100 | 144.8 | 71 | 62.1 | 1.3 | 350 | 2640.4 | 60 | 21.6 | 78.9 | 78.8 | 73 | 84.7 | 35.8 | 12.9 | 10000 | 9977 | 10000 | 19861.5 | 19196.3 | 19176.3 | 1.986 | 1.924 | 1.918 | 0.502 | 0.538 | 0.5 | -2.45 | 2.54 | -2 | 0.5 | 0.532 | 0.5 | 2.12 | 2.31 | 2.52 | 0.543 | 0.5 | 0.513 | 2.25 | -2.23 | 2.21 | 0.524 | 0.507 | 0.5 | 2.14 | 2.45 | 2.05 | Good_Mixed | 9977 | 19176.3 | 1.918 | 0.538 | 2.54 | 0.543 | 2.52 | 0.9311 | 0.938 | 0.8463 | 0.9461 | 1 | 0.9264 | 0.9117 | 0.9311 | 0.9311 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
647 | 775.8 | 508.7 | 106.9 | 120.9 | 19 | 833.5 | 5193 | 46.4 | 35.6 | 92.5 | 96.4 | 81.6 | 101 | 40.1 | 26.4 | 5807.6 | 4878.5 | 6018.5 | 8923.4 | 7308.1 | 9483.2 | 1.537 | 1.498 | 1.576 | 0.789 | 0.78 | 0.741 | 7.11 | -5.5 | 5.4 | 0.679 | 0.721 | 0.678 | 4.08 | 3.99 | 4.66 | 0.682 | 0.676 | 0.609 | 4.8 | 4.78 | 5.02 | 0.77 | 0.732 | 0.69 | 5.27 | 4.26 | 3.87 | Poor_Mixed | 4878.5 | 7308.1 | 1.498 | 0.789 | 7.11 | 0.77 | 5.27 | 0.4366 | 0.7276 | 0.4526 | 0.5299 | 1 | 0.373 | 0.469 | 0.5648 | 0.5648 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
648 | 100 | 137.5 | 67 | 57.6 | 1 | 389.2 | 3381.9 | 58.8 | 20.9 | 79.7 | 82 | 73 | 85.1 | 35.4 | 10.4 | 9794 | 9082.6 | 9729.6 | 19588.1 | 17207.4 | 18811.2 | 2 | 1.895 | 1.933 | 0.646 | 0.626 | 0.611 | 3.72 | 4.54 | 3.66 | 0.516 | 0.53 | 0.51 | -2 | 2.76 | 2.85 | 0.569 | 0.521 | 0.5 | 2.95 | -2.53 | 2.44 | 0.534 | 0.528 | 0.5 | 2.55 | 2.4 | 2 | Fair_Winding_TD_Cap | 9082.6 | 17207.4 | 1.895 | 0.646 | 4.54 | 0.569 | 2.95 | 0.9652 | 0.9574 | 0.8113 | 0.9955 | 1 | 0.6233 | 0.8585 | 0.8889 | 0.8889 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
649 | 921 | 580.4 | 109.9 | 120.4 | 18.8 | 843.1 | 6088.8 | 57.9 | 20.4 | 75.3 | 79.8 | 70.6 | 80.3 | 35.4 | 14.6 | 8886.2 | 10000 | 9611.1 | 17369.8 | 19497.7 | 17777.5 | 1.955 | 1.95 | 1.85 | 0.573 | 0.61 | 0.567 | 3.18 | 3.34 | 3.2 | 0.501 | 0.561 | 0.558 | -2 | 2.14 | -2.45 | 0.5 | 0.517 | 0.5 | 2.25 | 2.15 | 2.51 | 0.524 | 0.5 | 0.547 | 2.62 | 2 | 2.98 | Poor_DGA | 8886.2 | 17369.8 | 1.85 | 0.61 | 3.34 | 0.561 | 2.98 | 0.4058 | 0.9748 | 0.9251 | 0.904 | 1 | 0.7231 | 0.879 | 0.7756 | 0.7756 | Fair | 1 | 1 | DGA | 0 |  | C2H2
650 | 1711.8 | 887.7 | 138.3 | 183.8 | 32.2 | 1254.3 | 8732.4 | 31.3 | 47.6 | 108.6 | 104 | 95 | 117.4 | 45.9 | 33.1 | 1738.6 | 2203 | 1959.9 | 1924.2 | 2526.1 | 2150.3 | 1.107 | 1.147 | 1.097 | 0.911 | 0.917 | 0.99 | 8.85 | -8.84 | -9.84 | 0.847 | 0.728 | 0.712 | 6.29 | 6.35 | 8.08 | 0.89 | 0.84 | 0.842 | 7.01 | 5.16 | 8.19 | 0.908 | 0.906 | 0.845 | 7.59 | -7.98 | 7.68 | Very Poor_Mixed | 1738.6 | 1924.2 | 1.097 | 0.99 | 9.84 | 0.908 | 8.19 | 0.0865 | 0.6053 | 0.1124 | 0.2787 | 1 | 0.0814 | 0.231 | 0.3324 | 0.3324 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
651 | 388.1 | 187.2 | 72.5 | 65.6 | 2.6 | 378.6 | 3377 | 55.3 | 23.8 | 79.5 | 75 | 72 | 83.7 | 35.6 | 10.8 | 10000 | 9658.8 | 10000 | 19418.5 | 19149.4 | 19850.5 | 1.942 | 1.983 | 1.985 | 0.726 | 0.693 | 0.71 | 4.65 | -5.39 | 4.63 | 0.5 | 0.5 | 0.531 | 2.29 | 3.08 | 2.97 | 0.564 | 0.52 | 0.502 | 2.25 | -2.03 | 2.8 | 0.518 | 0.539 | 0.501 | 3.09 | 2.33 | 2 | Fair_Winding_TD_Cap | 9658.8 | 19149.4 | 1.942 | 0.726 | 5.39 | 0.564 | 3.09 | 0.8342 | 0.8912 | 0.9028 | 0.9892 | 1 | 0.4869 | 0.8746 | 0.8408 | 0.8408 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
652 | 1324.7 | 809.8 | 127.5 | 168.8 | 34.3 | 1119 | 6909.8 | 38.1 | 42.7 | 106.2 | 98.6 | 89.2 | 110.8 | 42.9 | 31.3 | 1549.3 | 3243.2 | 1808.8 | 1683 | 4054.8 | 2081.3 | 1.086 | 1.25 | 1.151 | 0.925 | 0.888 | 0.909 | -8.42 | -8.57 | 9.17 | 0.902 | 0.892 | 0.91 | -5.92 | -7.16 | 8.39 | 0.771 | 0.813 | 0.81 | 6.1 | -6.54 | 5.71 | 0.89 | 0.871 | 0.777 | 7.17 | 6.51 | 6.8 | Very Poor_Mixed | 1549.3 | 1683 | 1.086 | 0.925 | 9.17 | 0.91 | 8.39 | 0.1731 | 0.6524 | 0.2443 | 0.3483 | 1 | 0.1261 | 0.2321 | 0.3828 | 0.3828 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
653 | 1476.9 | 806 | 138.8 | 178 | 31.8 | 1237.7 | 7404 | 37 | 42.5 | 105.6 | 103.4 | 94 | 113.7 | 43.2 | 31.2 | 2737 | 1860.4 | 2681.6 | 3487.1 | 2293.7 | 3320.6 | 1.274 | 1.233 | 1.238 | 0.927 | 0.974 | 0.843 | 8.42 | 9.39 | 8.55 | 0.85 | 0.801 | 0.802 | 7.93 | 8.65 | 7.79 | 0.884 | 0.978 | 0.811 | 9.1 | -8.14 | 6.48 | 0.901 | 0.958 | 0.741 | 8.76 | 6.24 | -6.69 | Very Poor_Mixed | 1860.4 | 2293.7 | 1.233 | 0.974 | 9.39 | 0.978 | 9.1 | 0.1374 | 0.6544 | 0.176 | 0.3521 | 1 | 0.1186 | 0.1903 | 0.3589 | 0.3589 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
654 | 1766 | 982.4 | 146.1 | 197 | 33.6 | 1354.9 | 8446.7 | 54.1 | 23.9 | 78.5 | 76 | 70 | 82 | 35 | 18.7 | 8890.9 | 9855.4 | 8790.4 | 16748.4 | 18760.3 | 16440.4 | 1.884 | 1.904 | 1.87 | 0.597 | 0.628 | 0.624 | 3.95 | -23.49 | 4.47 | 0.5 | 0.5 | 0.518 | 2.34 | 2.06 | 2.54 | 0.537 | 0.558 | 0.516 | 2 | 2.32 | -2 | 0.531 | 0.566 | 0.5 | 2 | 2.21 | 2 | Critical_DGA | 8790.4 | 16440.4 | 1.87 | 0.628 | 23.49 | 0.566 | 2.54 | 0.0422 | 0.8894 | 0.9282 | 0.7872 | 1 | 0.5187 | 0.8795 | 0.6404 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
655 | 599.4 | 401.4 | 97.1 | 99.8 | 10.8 | 687.5 | 4513.6 | 50.8 | 31.1 | 85.1 | 86.1 | 76.9 | 90.3 | 37.3 | 22.4 | 7623.2 | 6644.9 | 6162.9 | 12555 | 11643.3 | 10108.2 | 1.647 | 1.752 | 1.64 | 0.696 | 0.755 | 0.681 | 5.35 | 6.09 | 4.72 | 0.596 | 0.65 | 0.662 | 4.32 | 4.37 | 5.11 | 0.612 | 0.646 | 0.693 | -4.32 | 5.15 | -2.95 | 0.657 | 0.736 | 0.613 | 4.88 | 3.97 | 4.18 | Poor_Mixed | 6162.9 | 10108.2 | 1.64 | 0.755 | 6.09 | 0.736 | 5.15 | 0.5743 | 0.7817 | 0.6722 | 0.6686 | 1 | 0.4587 | 0.5277 | 0.6572 | 0.6572 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
656 | 811.2 | 519 | 108.9 | 133.2 | 18.4 | 853.4 | 5764.1 | 57.6 | 22.3 | 79.3 | 82.3 | 73 | 84.8 | 36.3 | 11.4 | 9092.1 | 9540 | 9461.1 | 16491.9 | 18707.7 | 18699.7 | 1.814 | 1.961 | 1.976 | 0.5 | 0.517 | 0.528 | 2.37 | 2 | 2.34 | 0.5 | 0.506 | 0.537 | 2.23 | 2.15 | 2.26 | 0.528 | 0.5 | 0.5 | -2 | -2.11 | 2.48 | 0.526 | 0.5 | 0.507 | 2 | 2.1 | -2.04 | Poor_DGA | 9092.1 | 16491.9 | 1.814 | 0.528 | 2.37 | 0.537 | 2.48 | 0.4147 | 0.9215 | 0.81 | 0.9783 | 1 | 0.9229 | 0.9244 | 0.7998 | 0.7998 | Fair | 1 | 1 | DGA | 0 |  | C2H2
657 | 275.5 | 199 | 68.3 | 61.5 | 1 | 379.5 | 3297.7 | 53.6 | 28.2 | 77.5 | 75 | 70.3 | 82.4 | 36.2 | 10.2 | 8050.6 | 9435.2 | 7647.8 | 15112.3 | 18154.9 | 13719.6 | 1.877 | 1.924 | 1.794 | 0.551 | 0.505 | 0.575 | 3.01 | 2.76 | 2.86 | 0.517 | 0.504 | 0.515 | 2 | 2.16 | -2.12 | 0.518 | 0.519 | 0.5 | 2 | 2 | 2 | 0.5 | 0.5 | 0.577 | -2.07 | 2.45 | -2 | Fair_Oil | 7647.8 | 13719.6 | 1.794 | 0.575 | 3.01 | 0.577 | 2.45 | 0.9329 | 0.8207 | 0.9436 | 0.9981 | 1 | 0.8153 | 0.9112 | 0.9141 | 0.9141 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
658 | 1302.5 | 839 | 129.9 | 162.3 | 34 | 1141.3 | 7484.6 | 36.7 | 43.4 | 102.9 | 103.5 | 91.3 | 112.7 | 43.4 | 34.8 | 2472.5 | 2246.1 | 2467.6 | 2902.3 | 2725.6 | 2924.5 | 1.174 | 1.213 | 1.185 | 0.923 | 0.883 | 0.88 | -9.3 | 7.84 | 11.09 | 0.778 | 0.781 | 0.766 | 5.55 | 5.7 | 8.5 | 0.715 | 0.799 | 0.737 | 6.28 | 5.72 | 5.35 | 0.834 | 0.853 | 0.714 | 6.2 | 8.47 | 7.46 | Critical_Mixed | 2246.1 | 2725.6 | 1.174 | 0.923 | 11.09 | 0.853 | 8.5 | 0.1669 | 0.6455 | 0.2094 | 0.2118 | 1 | 0.1185 | 0.3066 | 0.3825 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
659 | 453.3 | 178.5 | 76.2 | 92 | 7.8 | 517.2 | 3836 | 59.4 | 22.6 | 81.3 | 85.5 | 74.9 | 89.6 | 37.8 | 15.6 | 7901.6 | 8348.2 | 6990.9 | 14000 | 15007.1 | 11818 | 1.772 | 1.798 | 1.69 | 0.566 | 0.583 | 0.596 | -3.31 | -2.84 | -3.26 | 0.581 | 0.621 | 0.55 | 3.48 | 2.75 | 3.11 | 0.547 | 0.572 | 0.6 | 2.96 | 3.12 | 3.01 | 0.605 | 0.585 | 0.582 | 3.38 | -2.66 | 3.6 | Fair_Mixed | 6990.9 | 11818 | 1.69 | 0.596 | 3.31 | 0.621 | 3.6 | 0.6931 | 0.915 | 0.7213 | 0.8773 | 1 | 0.7317 | 0.6809 | 0.7841 | 0.7841 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
660 | 896 | 560.1 | 112.6 | 124.1 | 24.4 | 855 | 5562.5 | 46.4 | 31.7 | 88.3 | 91.1 | 82.5 | 97.6 | 40 | 26.7 | 4755 | 5863.7 | 5403 | 7069.9 | 8886.3 | 8109.2 | 1.487 | 1.515 | 1.501 | 0.652 | 0.689 | 0.71 | 5.06 | 5.99 | 4.81 | 0.668 | 0.634 | 0.622 | 3.99 | 3.45 | 4.57 | 0.664 | 0.622 | 0.716 | 4.38 | 4.92 | 4.05 | 0.683 | 0.747 | 0.631 | 4.03 | 5.4 | 5.02 | Poor_Mixed | 4755 | 7069.9 | 1.487 | 0.71 | 5.99 | 0.747 | 5.4 | 0.3774 | 0.7741 | 0.5253 | 0.5192 | 1 | 0.4892 | 0.5072 | 0.5855 | 0.5855 | Poor | 0 | 1 | DGA | 0 |  | C2H2
661 | 341.9 | 120 | 70.7 | 50 | 3.1 | 390 | 2709.7 | 57.8 | 21 | 77.3 | 75 | 70.3 | 81.9 | 35 | 10 | 8368.3 | 9245.4 | 8883.9 | 15770.1 | 17990.3 | 16981.8 | 1.885 | 1.946 | 1.912 | 0.5 | 0.517 | 0.512 | -2 | 2.48 | -2 | 0.521 | 0.528 | 0.517 | 2 | 2.37 | 2.35 | 0.509 | 0.5 | 0.5 | 2.23 | 2.04 | -2.39 | 0.5 | 0.543 | 0.502 | 2 | 2 | 2.21 | Good_Mixed | 8368.3 | 15770.1 | 1.885 | 0.517 | 2.48 | 0.543 | 2.39 | 0.8683 | 0.9543 | 0.953 | 1 | 1 | 0.9433 | 0.9131 | 0.9333 | 0.9333 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
662 | 719.5 | 446.2 | 95.3 | 102.2 | 14.7 | 778.6 | 5108.9 | 60 | 21.2 | 77.7 | 77.8 | 71 | 83.4 | 36.1 | 11.5 | 10000 | 9884.4 | 8941.9 | 20000 | 19768.7 | 17244.6 | 2 | 2 | 1.929 | 0.555 | 0.609 | 0.589 | -3.37 | -3.42 | 3.79 | 0.529 | 0.588 | 0.5 | 3.34 | 2.84 | 3.28 | 0.543 | 0.502 | 0.504 | 3.56 | 2.34 | 2.83 | 0.529 | 0.522 | 0.554 | 3.08 | 2.58 | 2.62 | Fair_DGA | 8941.9 | 17244.6 | 1.929 | 0.609 | 3.79 | 0.588 | 3.56 | 0.5107 | 0.9486 | 0.8913 | 0.9764 | 1 | 0.704 | 0.818 | 0.7853 | 0.7853 | Fair | 1 | 1 | DGA | 0 |  | C2H2
663 | 168.7 | 163.7 | 74.3 | 70.8 | 2.2 | 476.1 | 2589.5 | 59.7 | 20 | 75.7 | 78.1 | 73.3 | 81.2 | 36.2 | 14.9 | 9535.4 | 9396.4 | 9231.5 | 18523.8 | 18792.8 | 18194.3 | 1.943 | 2 | 1.971 | 0.5 | 0.529 | 0.557 | 2 | -3.69 | 3.33 | 0.5 | 0.504 | 0.5 | -2.23 | 2.37 | -2.4 | 0.506 | 0.531 | 0.506 | 2.03 | 2.12 | 2.32 | 0.5 | 0.501 | 0.5 | 2.38 | -2.62 | 2.36 | Good_Mixed | 9231.5 | 18194.3 | 1.943 | 0.557 | 3.69 | 0.531 | 2.62 | 0.8471 | 1 | 0.9011 | 0.8962 | 1 | 0.8442 | 0.9396 | 0.914 | 0.914 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
664 | 1508.9 | 813.7 | 128.4 | 171.2 | 32.3 | 1185.1 | 7746 | 32.5 | 48.4 | 109.3 | 107.6 | 96.2 | 118 | 44.5 | 31 | 1748.9 | 1084.1 | 2177.5 | 1905.5 | 1224 | 2390.1 | 1.09 | 1.129 | 1.098 | 0.968 | 0.977 | 0.979 | -9.28 | -8.97 | 9.4 | 0.883 | 0.909 | 0.908 | 7.33 | 6.19 | -5.06 | 0.804 | 0.818 | 0.742 | 6.98 | 8.89 | 6.67 | 0.881 | 0.944 | 0.737 | -8.89 | 8.06 | 8.01 | Very Poor_Mixed | 1084.1 | 1224 | 1.09 | 0.979 | 9.4 | 0.944 | 8.89 | 0.1475 | 0.5979 | 0.0895 | 0.3597 | 1 | 0.0554 | 0.214 | 0.3418 | 0.3418 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
665 | 368.9 | 223.3 | 76.6 | 82.2 | 3.3 | 573.2 | 2935.8 | 56.4 | 21.4 | 80.6 | 131.7 | 74.7 | 88.1 | 36.1 | 16.7 | 9157.4 | 8027.7 | 8496.1 | 17285.1 | 14322.4 | 16554.4 | 1.888 | 1.784 | 1.948 | 0.561 | 0.541 | 0.551 | 2.41 | 3.28 | 2.88 | 0.525 | 0.61 | 0.572 | 2.27 | 2 | 2.17 | 0.657 | 0.979 | 0.572 | 2.14 | -9.84 | 4.44 | 0.531 | 0.505 | 0.583 | 2.85 | 2.54 | 2.98 | Critical_Bushing_TD_Cap | 8027.7 | 14322.4 | 1.784 | 0.561 | 3.28 | 0.979 | 9.84 | 0.7637 | 0.9432 | 0.5965 | 0.8465 | 1 | 0.7956 | 0.6622 | 0.7966 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | WTI_LV
666 | 1504.1 | 897 | 134.3 | 183.1 | 33.8 | 1199.1 | 7631.9 | 33.5 | 45.7 | 106.6 | 106.1 | 94.9 | 115.7 | 44.2 | 30.3 | 2288.2 | 2084.7 | 1870.5 | 2675 | 2299.2 | 2111.5 | 1.169 | 1.103 | 1.129 | 0.884 | 0.905 | 0.9 | -8.02 | 8.77 | -8.27 | 0.882 | 0.853 | 0.791 | 6.38 | -7.51 | 7.21 | 0.83 | 0.728 | 0.902 | 7.64 | 7.86 | 6.34 | 0.873 | 0.736 | 0.942 | 8.61 | 6.75 | 8.89 | Very Poor_Mixed | 1870.5 | 2111.5 | 1.103 | 0.905 | 8.77 | 0.942 | 8.89 | 0.1175 | 0.6232 | 0.1332 | 0.3863 | 1 | 0.1524 | 0.2185 | 0.3575 | 0.3575 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
667 | 758.2 | 455.5 | 97.4 | 108.8 | 16.5 | 734.5 | 4439.4 | 49.2 | 30.4 | 86.4 | 85.9 | 79.7 | 94.8 | 38.5 | 23.6 | 5117.2 | 6660.8 | 5575.5 | 7595.9 | 10605.9 | 8318.7 | 1.484 | 1.592 | 1.492 | 0.749 | 0.719 | 0.752 | 5.95 | 5.33 | 4.95 | 0.704 | 0.685 | 0.725 | 4.97 | 4.18 | 4.59 | 0.702 | 0.702 | 0.686 | 4.11 | -4.16 | 5.11 | 0.657 | 0.609 | 0.744 | 4.73 | 4.47 | -4.03 | Poor_Mixed | 5117.2 | 7595.9 | 1.484 | 0.752 | 5.95 | 0.744 | 5.11 | 0.4982 | 0.7907 | 0.6155 | 0.628 | 1 | 0.4306 | 0.473 | 0.6178 | 0.6178 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
668 | 238 | 168.8 | 70.6 | 73 | 3.5 | 481.9 | 2627.5 | 52.2 | 29.8 | 83.9 | 81 | 76.6 | 88.5 | 37.3 | 12.9 | 1073 | 802.8 | 1218.7 | 1193.8 | 602.4 | 1295.2 | 1.113 | 0.75 | 1.063 | 0.666 | 0.749 | 0.701 | 4.86 | -5.21 | 5.05 | 0.519 | 0.542 | 0.524 | 2 | 2.98 | -2.17 | 0.558 | 0.557 | 0.511 | 2.08 | 2.19 | -2 | 0.5 | 0.541 | 0.526 | 2 | 2.75 | -2.04 | Critical_IR_PI | 802.8 | 602.4 | 0.75 | 0.749 | 5.21 | 0.558 | 2.98 | 0.8094 | 0.7986 | 0.7313 | 0.9461 | 0.7437 | 0.483 | 0.845 | 0.7573 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_LV
669 | 286.2 | 206 | 65 | 161.2 | 1.2 | 495.4 | 2500 | 55.5 | 25.4 | 106.5 | 107.5 | 95.2 | 117.3 | 46.1 | 18.3 | 7213 | 6852.5 | 6887.9 | 11900.6 | 11463.1 | 11407.3 | 1.65 | 1.673 | 1.656 | 0.562 | 1.477 | 0.548 | 2.73 | -2.79 | 2.77 | 0.531 | 0.553 | 0.531 | 3.04 | 3.5 | 2.26 | 0.55 | 0.619 | 0.536 | 2.75 | 2.8 | 3.81 | 0.539 | 0.545 | 0.535 | 2.42 | 2.09 | 2.45 | Critical_Thermal | 6852.5 | 11407.3 | 1.65 | 1.477 | 2.79 | 0.619 | 3.81 | 0.7793 | 0.8633 | 0.1024 | 0.7993 | 1 | 0.6636 | 0.765 | 0.7392 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H4
670 | 820.5 | 538.5 | 99.8 | 128.8 | 14.2 | 776 | 5239.2 | 47.3 | 32.1 | 93.4 | 92.3 | 80.1 | 101 | 40.4 | 25.1 | 5736.2 | 5180.4 | 6254.8 | 8743.5 | 8173.4 | 10039.4 | 1.524 | 1.578 | 1.605 | 0.742 | 0.775 | 0.738 | 5.88 | -5.66 | 5.97 | 0.742 | 0.748 | 0.77 | 4.96 | 4.23 | -3.54 | 0.636 | 0.63 | 0.739 | 4.86 | 3.98 | 4.84 | 0.74 | 0.722 | 0.689 | 4.23 | 4.07 | 4.03 | Poor_Mixed | 5180.4 | 8173.4 | 1.524 | 0.775 | 5.97 | 0.77 | 4.96 | 0.4653 | 0.7691 | 0.4802 | 0.576 | 1 | 0.3967 | 0.4548 | 0.5829 | 0.5829 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
671 | 612.9 | 362.2 | 93.5 | 94.8 | 11.1 | 650.6 | 4226.7 | 52.9 | 28.3 | 86.5 | 85.1 | 76.7 | 91.1 | 37.3 | 20 | 7333.4 | 6998.3 | 8100 | 13472.9 | 11932.7 | 15208.6 | 1.837 | 1.705 | 1.878 | 0.615 | 0.599 | 0.609 | -4.01 | 3.47 | 2.76 | 0.641 | 0.587 | 0.606 | 4.21 | 3.68 | 3.31 | 0.595 | 0.558 | 0.58 | 4.16 | 3.25 | 3.75 | 0.63 | 0.664 | 0.576 | 3.24 | 4.11 | 3.87 | Fair_Mixed | 6998.3 | 11932.7 | 1.705 | 0.615 | 4.01 | 0.664 | 4.21 | 0.5906 | 0.8193 | 0.6668 | 0.7467 | 1 | 0.6815 | 0.6203 | 0.717 | 0.717 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
672 | 199.6 | 142.3 | 65 | 52.7 | 4.8 | 395.4 | 2596.4 | 58 | 22.2 | 75 | 75 | 70.4 | 80 | 35 | 10.5 | 9569.6 | 10000 | 9397.7 | 18936.5 | 19632.2 | 18371.2 | 1.979 | 1.963 | 1.955 | 0.517 | 0.553 | 0.534 | 2.34 | 2.56 | 2.3 | 0.524 | 0.514 | 0.5 | -2.11 | 2.06 | -2.31 | 0.539 | 0.5 | 0.5 | 2 | -2 | 2.28 | 0.509 | 0.5 | 0.533 | 2.56 | 2.01 | 2 | Good_Mixed | 9397.7 | 18371.2 | 1.955 | 0.553 | 2.56 | 0.539 | 2.56 | 0.8456 | 0.9238 | 0.9937 | 0.994 | 1 | 0.8583 | 0.9187 | 0.9169 | 0.9169 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
673 | 1692.9 | 915.3 | 135.1 | 183.5 | 33.3 | 1262.2 | 8365.3 | 34.7 | 46.9 | 105.4 | 109.3 | 92.3 | 114.9 | 44.5 | 32.7 | 2275 | 1393.8 | 1548.7 | 2492.3 | 1569.2 | 1715.3 | 1.096 | 1.126 | 1.108 | 0.957 | 0.9 | 0.912 | -9.84 | 8.29 | 9 | 0.841 | 0.896 | 0.827 | -8.15 | 5.45 | 8.7 | 0.826 | 0.748 | 0.706 | 6 | 7.82 | 7.33 | 0.878 | 0.768 | 0.696 | -8.58 | 8.37 | 8.35 | Very Poor_Mixed | 1393.8 | 1569.2 | 1.096 | 0.957 | 9.84 | 0.896 | 8.7 | 0.0868 | 0.6119 | 0.1388 | 0.2943 | 1 | 0.0992 | 0.2505 | 0.3427 | 0.3427 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
674 | 145.8 | 173.5 | 68.3 | 60.5 | 4.1 | 350 | 2667.1 | 57.3 | 25.3 | 80.6 | 81 | 73.9 | 83.6 | 35.6 | 15 | 9734.4 | 9669.4 | 9981.5 | 19460.5 | 19145.5 | 19549.2 | 1.999 | 1.98 | 1.959 | 0.503 | 0.518 | 0.533 | 2.85 | 2.39 | 2.93 | 0.5 | 0.528 | 0.537 | 2 | -2.04 | 2 | 0.516 | 0.536 | 0.538 | 2 | 2 | -2.02 | 0.52 | 0.582 | 0.5 | -2.3 | 2.07 | 2.17 | Good_Mixed | 9669.4 | 19145.5 | 1.959 | 0.533 | 2.93 | 0.582 | 2.3 | 0.8539 | 0.865 | 0.8109 | 0.8935 | 1 | 0.8727 | 0.8692 | 0.8817 | 0.8817 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
675 | 709.3 | 462.7 | 98.3 | 100.4 | 16.3 | 683.6 | 5490.8 | 57.9 | 23.8 | 79.5 | 78.5 | 73.6 | 81.9 | 36.3 | 15.4 | 8613.5 | 9949.4 | 8372.6 | 16679.6 | 19747 | 16352.9 | 1.936 | 1.985 | 1.953 | 0.52 | 0.546 | 0.513 | 2.4 | 2.39 | 2.11 | 0.606 | 0.557 | 0.578 | 3.21 | 3.36 | 2.2 | 0.527 | 0.56 | 0.61 | 2.77 | 2.01 | 2 | 0.534 | 0.531 | 0.535 | 2.09 | 2.19 | -3.11 | Poor_DGA | 8372.6 | 16352.9 | 1.936 | 0.546 | 2.4 | 0.61 | 3.36 | 0.5071 | 0.8912 | 0.8504 | 0.8828 | 1 | 0.8834 | 0.7571 | 0.7829 | 0.7829 | Fair | 1 | 1 | DGA | 0 |  | C2H2
676 | 869.2 | 507.9 | 106.3 | 123.5 | 19.5 | 861.2 | 5633.1 | 45.3 | 32.3 | 88.2 | 90.8 | 80 | 97 | 38.7 | 22.9 | 7532.3 | 5914.2 | 6502.1 | 13031.7 | 9277.9 | 10266.9 | 1.73 | 1.569 | 1.579 | 0.737 | 0.727 | 0.715 | 5.22 | 6.41 | 6.16 | 0.65 | 0.669 | 0.624 | 4.71 | 5.3 | 4.4 | 0.602 | 0.652 | 0.695 | -4.25 | 4.71 | 4.02 | 0.648 | 0.679 | 0.587 | 6.35 | -4.49 | -4.7 | Poor_Mixed | 5914.2 | 9277.9 | 1.569 | 0.737 | 6.41 | 0.695 | 6.35 | 0.4162 | 0.7666 | 0.5553 | 0.6518 | 1 | 0.4136 | 0.5201 | 0.5957 | 0.5957 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
677 | 823 | 500.2 | 105.5 | 110.4 | 16.7 | 805.3 | 5173.5 | 45.3 | 32.7 | 92.8 | 89.4 | 80.9 | 101.2 | 38.2 | 25.9 | 5148.4 | 5605.1 | 6322.2 | 8195.8 | 8916.4 | 10143.3 | 1.592 | 1.591 | 1.604 | 0.693 | 0.738 | 0.729 | 5.3 | 5.87 | 5.75 | 0.689 | 0.741 | 0.718 | 4.42 | 5.38 | -3.67 | 0.656 | 0.695 | 0.641 | 4 | -4.54 | 6.05 | 0.609 | 0.602 | 0.65 | 3.48 | 5.41 | 6.03 | Poor_Mixed | 5148.4 | 8195.8 | 1.591 | 0.738 | 5.87 | 0.741 | 6.05 | 0.4632 | 0.7617 | 0.5104 | 0.5478 | 1 | 0.4353 | 0.4934 | 0.5954 | 0.5954 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
678 | 115.9 | 217 | 71.2 | 64.7 | 1 | 465.1 | 3086.9 | 53.7 | 27 | 75 | 75 | 71.5 | 80 | 35 | 12.6 | 7688.3 | 8767 | 9111.2 | 13449 | 17189.7 | 16923.3 | 1.749 | 1.961 | 1.857 | 0.54 | 0.532 | 0.55 | 2.27 | 3.74 | -3.56 | 0.509 | 0.516 | 0.572 | -2 | 2 | 2.49 | 0.506 | 0.5 | 0.554 | 2.53 | 2 | -2.15 | 0.506 | 0.5 | 0.514 | 2.07 | 2 | 2.92 | Fair_Oil | 7688.3 | 13449 | 1.749 | 0.55 | 3.74 | 0.572 | 2.92 | 0.9276 | 0.8382 | 0.9818 | 0.953 | 1 | 0.792 | 0.8901 | 0.9094 | 0.9094 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
679 | 1075.1 | 577.1 | 107 | 118.5 | 21.8 | 826.5 | 5868.6 | 45 | 34.9 | 88.4 | 92 | 79.7 | 96.2 | 39.8 | 23.9 | 6509 | 5394.7 | 6336.2 | 10935.3 | 8478.2 | 9763.2 | 1.68 | 1.572 | 1.541 | 0.76 | 0.741 | 0.799 | 6.53 | 5.19 | 6.93 | 0.615 | 0.747 | 0.69 | 4.04 | 5.48 | 6.25 | 0.676 | 0.694 | 0.668 | 4.82 | -4.24 | 5.43 | 0.703 | 0.65 | 0.651 | -5.39 | 5.74 | 4.71 | Poor_Mixed | 5394.7 | 8478.2 | 1.541 | 0.799 | 6.93 | 0.747 | 6.25 | 0.3854 | 0.7356 | 0.5453 | 0.6177 | 1 | 0.3641 | 0.4657 | 0.5648 | 0.5648 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
680 | 446.3 | 225.9 | 67.4 | 151.7 | 3.5 | 426.9 | 3886 | 51.5 | 28.7 | 107 | 109.3 | 97.8 | 119.2 | 45.4 | 14 | 7425.5 | 254.8 | 7668.3 | 13154.9 | 374.7 | 13823.7 | 1.772 | 1.471 | 1.803 | 0.52 | 0.536 | 0.539 | -2.09 | 2.63 | 3.16 | 0.508 | 0.5 | 0.5 | -2.19 | 2.92 | 2.35 | 0.534 | 0.5 | 0.518 | -2 | 2.03 | -2.16 | 0.5 | 0.537 | 0.511 | 2.05 | 2.8 | 2.45 | Critical_Thermal | 254.8 | 374.7 | 1.471 | 0.539 | 3.16 | 0.537 | 2.92 | 0.7055 | 0.8136 | 0.0714 | 0.9194 | 0.85 | 0.8474 | 0.9123 | 0.746 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H4
681 | 245.8 | 188.2 | 76.7 | 60.7 | 1 | 422.8 | 3133.1 | 33 | 46.7 | 113.4 | 80.8 | 74.6 | 85.7 | 36.2 | 12.7 | 5889.9 | 5232.1 | 5126.5 | 8923.7 | 8106.2 | 7854.1 | 1.515 | 1.549 | 1.532 | 0.671 | 0.683 | 0.685 | 4.2 | 4.73 | 4.19 | 0.58 | 0.595 | 0.53 | -3.02 | -3.3 | 2.18 | 0.559 | 0.519 | 0.555 | 2.73 | -3.08 | 2.5 | 0.579 | 0.564 | 0.5 | -2.57 | 2.43 | 3.37 | Critical_Oil | 5126.5 | 7854.1 | 1.515 | 0.685 | 4.73 | 0.595 | 3.37 | 0.9262 | 0.6137 | 0.6071 | 0.9507 | 1 | 0.545 | 0.7641 | 0.7873 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature | Moisture_PPM
682 | 876.9 | 538.9 | 105.9 | 129.5 | 15 | 895.6 | 5577.9 | 47.2 | 31.8 | 92.7 | 95.1 | 84.6 | 99.4 | 38.4 | 24.1 | 5182.2 | 5847.2 | 4875.1 | 7641.7 | 9034 | 7089.8 | 1.475 | 1.545 | 1.454 | 0.715 | 0.73 | 0.72 | -6.66 | 5.56 | 5.35 | 0.632 | 0.645 | 0.532 | 5.55 | 4.96 | 4.01 | 0.691 | 0.64 | 0.677 | 3.77 | -4.98 | -4.75 | 0.764 | 0.674 | 0.745 | 5.42 | 5.45 | 4.28 | Poor_Mixed | 4875.1 | 7089.8 | 1.454 | 0.73 | 6.66 | 0.764 | 5.55 | 0.4318 | 0.7728 | 0.4589 | 0.6108 | 1 | 0.4218 | 0.498 | 0.5858 | 0.5858 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
683 | 525.3 | 390.1 | 88.8 | 89.1 | 12.3 | 631.1 | 4214.7 | 58.8 | 20.6 | 75 | 79.8 | 70 | 80 | 35.1 | 11.7 | 9538 | 9675.8 | 10000 | 18540.1 | 18997 | 19368.4 | 1.944 | 1.963 | 1.937 | 0.544 | 0.532 | 0.577 | 2.67 | 2.51 | -3.16 | 0.511 | 0.514 | 0.516 | 2.67 | 2.4 | 2.52 | 0.56 | 0.55 | 0.536 | 2.49 | 2.46 | 2.88 | 0.502 | 0.583 | 0.578 | -2.15 | -2.96 | 2.33 | Fair_DGA | 9538 | 18540.1 | 1.937 | 0.577 | 3.16 | 0.583 | 2.96 | 0.5975 | 0.9672 | 0.9434 | 0.9724 | 1 | 0.8023 | 0.8086 | 0.8263 | 0.8263 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
684 | 483.8 | 290.8 | 84 | 87.9 | 1.2 | 573.5 | 3451.3 | 56.9 | 22.7 | 78.1 | 77.2 | 70 | 83.6 | 35.1 | 17.5 | 8911.6 | 9347.1 | 10000 | 16573.8 | 18064.6 | 19782.9 | 1.86 | 1.933 | 1.978 | 1.732 | 0.588 | 0.563 | 2.72 | 2.77 | -2.86 | 0.584 | 0.566 | 0.597 | 3.59 | 3.31 | 2.99 | 0.521 | 0.604 | 0.532 | 3 | 3.54 | 3.15 | 0.544 | 0.92 | 0.603 | 3.52 | -8.5 | 2.93 | Critical_Bushing_TD_Cap | 8911.6 | 16573.8 | 1.86 | 1.732 | 2.86 | 0.92 | 8.5 | 0.7944 | 0.9129 | 0.9098 | 0.8232 | 1 | 0.6425 | 0.6379 | 0.8051 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_HV_TanDelta_pct
685 | 123.4 | 144.9 | 69.1 | 54.4 | 2.3 | 350 | 2561.1 | 60 | 21.9 | 77.4 | 79.3 | 73 | 84.2 | 35.9 | 13.8 | 8937.8 | 9316.2 | 9564.7 | 17438.7 | 17676.8 | 18938.4 | 1.951 | 1.897 | 1.98 | 0.51 | 0.5 | 0.5 | 2 | 2.55 | -2.52 | 0.58 | 0.529 | 0.521 | 2 | 2.21 | -2.81 | 0.519 | 0.53 | 0.523 | 2 | 2.85 | 2.44 | 0.531 | 0.5 | 0.542 | -2.98 | -2.21 | 2.58 | Good_Mixed | 8937.8 | 17438.7 | 1.897 | 0.51 | 2.55 | 0.58 | 2.98 | 0.906 | 0.9307 | 0.8585 | 0.9244 | 1 | 0.9519 | 0.8332 | 0.9135 | 0.9135 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
686 | 896 | 550.8 | 107.9 | 132.8 | 20.2 | 907.7 | 5508.6 | 47.4 | 35.9 | 92 | 93.6 | 84.2 | 99.5 | 39.5 | 27.2 | 5473.8 | 5262.4 | 6704.1 | 8653.2 | 8208.4 | 10819.1 | 1.581 | 1.56 | 1.614 | 0.677 | 0.676 | 0.653 | -5.35 | 4.95 | 5.04 | 0.734 | 0.687 | 0.622 | -4.93 | -5.25 | -4.05 | 0.603 | 0.68 | 0.68 | 6.36 | 3.86 | -5.17 | 0.709 | 0.776 | 0.731 | 3.9 | 5.09 | 5.55 | Poor_Mixed | 5262.4 | 8208.4 | 1.56 | 0.677 | 5.35 | 0.776 | 6.36 | 0.3909 | 0.7242 | 0.4679 | 0.5011 | 1 | 0.5129 | 0.4586 | 0.5708 | 0.5708 | Poor | 0 | 1 | DGA | 0 |  | C2H2
687 | 363.4 | 257.7 | 76.9 | 147.2 | 4.1 | 508.3 | 3428.8 | 54.8 | 67.5 | 105.4 | 106.2 | 95.1 | 118.9 | 45.7 | 13 | 8750.3 | 9340.6 | 8330.1 | 15279 | 17845.5 | 14940.7 | 1.746 | 1.911 | 1.794 | 0.547 | 0.617 | 0.567 | 3.68 | 3.63 | 3.01 | 0.578 | 0.563 | 0.543 | 3.11 | 2.82 | 2.86 | 0.599 | 0.547 | 0.603 | 3.04 | 3.28 | 3.44 | 0.604 | 0.655 | 0.596 | 4.26 | 3.37 | 4.07 | Critical_Thermal | 8330.1 | 14940.7 | 1.746 | 0.617 | 3.68 | 0.655 | 4.26 | 0.6878 | 0.5833 | 0.1111 | 0.9438 | 1 | 0.7209 | 0.6641 | 0.6807 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
688 | 1712 | 977 | 143.3 | 197 | 34.3 | 1379 | 8755.5 | 56.3 | 23.4 | 77.3 | 75.8 | 70 | 82 | 35.3 | 14.8 | 8566.7 | 116.4 | 8705.5 | 15864.8 | 167.6 | 15340.7 | 1.852 | 1.44 | 1.762 | 0.551 | 0.574 | 0.625 | 3 | 3.06 | 3.39 | 0.612 | 0.666 | 0.56 | 4.23 | -4.63 | 4.17 | 0.573 | 0.579 | 0.551 | -2.72 | 3.2 | 4.72 | 0.562 | 0.627 | 0.567 | 3.26 | 4.14 | 3.48 | Critical_DGA | 116.4 | 167.6 | 1.44 | 0.625 | 3.39 | 0.666 | 4.72 | 0.0391 | 0.8988 | 0.9419 | 0.8988 | 0.85 | 0.731 | 0.6433 | 0.6109 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
689 | 143.7 | 213.8 | 74.4 | 54.3 | 3 | 400.6 | 2744.8 | 58.7 | 21.7 | 78.9 | 79.4 | 71.2 | 82.8 | 35.2 | 13.7 | 10000 | 9824.4 | 8389 | 19182.6 | 19348.7 | 15616.6 | 1.918 | 1.969 | 1.862 | 0.745 | 0.696 | 0.62 | -6.1 | 5.8 | 3.69 | 0.554 | 0.511 | 0.5 | 2 | -2 | -2.51 | 0.514 | 0.5 | 0.547 | -3.02 | 3.34 | 2.27 | 0.527 | 0.555 | 0.579 | 2.71 | 2.13 | -2.48 | Fair_Winding_TD_Cap | 8389 | 15616.6 | 1.862 | 0.745 | 6.1 | 0.579 | 3.34 | 0.8633 | 0.9355 | 0.8692 | 0.9269 | 1 | 0.4948 | 0.8388 | 0.8416 | 0.8416 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
690 | 1618.3 | 888.4 | 135.3 | 180.4 | 32.4 | 1260 | 8081.1 | 31.1 | 47.6 | 104.2 | 102 | 93.3 | 112.8 | 43.4 | 33.3 | 690 | 1583.3 | 1992.8 | 1200 | 1829.8 | 2092.4 | 1.739 | 1.156 | 1.05 | 0.968 | 0.94 | 0.928 | 9.41 | 9.54 | 8.86 | 0.848 | 0.771 | 0.946 | 8.43 | 8.97 | 5.84 | 0.842 | 0.799 | 0.798 | 6.2 | -7.74 | 7.8 | 0.801 | 0.878 | 0.762 | 6.91 | 7.18 | -7.76 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.968 | 9.54 | 0.946 | 8.97 | 0.1053 | 0.6053 | 0.1987 | 0.2709 | 1 | 0.0723 | 0.2281 | 0.3436 | 0.3436 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
691 | 118.1 | 142.5 | 65.5 | 53.6 | 3 | 350 | 2500 | 60 | 21.1 | 77.1 | 76.7 | 70 | 80.5 | 35 | 13.5 | 9889.6 | 10000 | 9609.5 | 19448.2 | 20000 | 18473.8 | 1.967 | 2 | 1.922 | 0.533 | 0.508 | 0.537 | 2.74 | 2.22 | 2.91 | 0.539 | 0.527 | 0.535 | -2.86 | 2.21 | 2.3 | 0.535 | 0.519 | 0.5 | -2.64 | 2 | 2.76 | 0.546 | 0.576 | 0.55 | -2.41 | 2.34 | 2.05 | Good_Mixed | 9609.5 | 18473.8 | 1.922 | 0.537 | 2.91 | 0.576 | 2.86 | 0.8946 | 0.9514 | 0.9413 | 0.9318 | 1 | 0.8605 | 0.8203 | 0.9067 | 0.9067 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
692 | 485.8 | 286.8 | 83.6 | 75.4 | 72.4 | 531.9 | 3929.7 | 32.4 | 49.4 | 81.1 | 85 | 72.3 | 85.6 | 37.1 | 12.3 | 4218.7 | 5233.4 | 4643.6 | 5807.1 | 7468.9 | 7286.6 | 1.377 | 1.427 | 1.569 | 0.702 | 0.679 | 0.641 | 5.3 | 3.88 | 5.17 | 0.556 | 0.6 | 0.543 | 3.25 | 3.26 | -3.03 | 0.624 | 0.588 | 0.551 | -3.71 | 3.77 | 2.87 | 0.606 | 0.581 | 0.548 | 3.16 | 2.36 | -3.82 | Critical_Oil | 4218.7 | 5807.1 | 1.377 | 0.702 | 5.3 | 0.624 | 3.82 | 0.524 | 0.5888 | 0.7718 | 0.9597 | 1 | 0.5278 | 0.686 | 0.6842 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
693 | 931.7 | 508.2 | 105.8 | 112.7 | 18.7 | 779.4 | 5641.2 | 47.9 | 32.2 | 90.2 | 89.8 | 81.7 | 98.3 | 40 | 22.6 | 7846 | 5240.1 | 5105 | 13638.5 | 7852.5 | 7579.2 | 1.738 | 1.499 | 1.485 | 0.789 | 0.774 | 0.75 | 5.59 | 5.78 | 5.4 | 0.672 | 0.606 | 0.612 | 4.93 | 4.62 | 3.35 | 0.679 | 0.622 | 0.607 | 4.4 | 4.64 | -4.08 | 0.621 | 0.72 | 0.748 | -4.07 | 3.72 | -3.69 | Poor_Mixed | 5105 | 7579.2 | 1.485 | 0.789 | 5.78 | 0.748 | 4.93 | 0.4371 | 0.7678 | 0.5227 | 0.6619 | 1 | 0.3943 | 0.533 | 0.5979 | 0.5979 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
694 | 765.4 | 476.4 | 95 | 105.1 | 16.1 | 725.8 | 4810.3 | 57.6 | 21.3 | 76.9 | 75.2 | 72.7 | 83.4 | 35.3 | 17.6 | 10000 | 9637 | 9567.4 | 20000 | 19002.7 | 19095.2 | 2 | 1.972 | 1.996 | 0.627 | 0.607 | 0.688 | 4.21 | 4.43 | 4.03 | 0.56 | 0.549 | 0.5 | -2.46 | -2.86 | -3.47 | 0.5 | 0.568 | 0.523 | 2.13 | 2.36 | 2.38 | 0.567 | 0.533 | 0.5 | 2.94 | -2 | 2 | Poor_DGA | 9567.4 | 19002.7 | 1.972 | 0.688 | 4.43 | 0.568 | 3.47 | 0.501 | 0.9458 | 0.9196 | 0.8203 | 1 | 0.5951 | 0.8401 | 0.7663 | 0.7663 | Fair | 1 | 1 | DGA | 0 |  | C2H2
695 | 100 | 178.9 | 68.5 | 80.1 | 1 | 448.8 | 3090.7 | 57.7 | 23.3 | 83.2 | 78.5 | 76 | 88.8 | 37.5 | 11.6 | 10000 | 8841.6 | 9824.4 | 19777 | 16997.5 | 19206.5 | 1.978 | 1.922 | 1.955 | 0.513 | 0.521 | 0.538 | 2 | -2.72 | 2.32 | 0.507 | 0.503 | 0.5 | 2 | -2 | 2.39 | 0.536 | 0.502 | 0.525 | 2.3 | 2.15 | 3.25 | 0.519 | 0.538 | 0.5 | 2 | 2.88 | -2.43 | Fair_Thermal | 8841.6 | 16997.5 | 1.922 | 0.538 | 2.72 | 0.538 | 3.25 | 0.9191 | 0.9008 | 0.7605 | 0.9744 | 1 | 0.8853 | 0.8959 | 0.9078 | 0.9078 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
696 | 100 | 183.7 | 65.6 | 51.7 | 1 | 350 | 2872.4 | 54.1 | 21.3 | 79.6 | 77 | 71.7 | 83.1 | 35.9 | 18.8 | 9283.9 | 9113.4 | 9100.9 | 17668.3 | 17936.4 | 17946.2 | 1.903 | 1.968 | 1.972 | 0.548 | 0.594 | 0.546 | 2.54 | -3.2 | 2 | 0.568 | 0.549 | 0.561 | 2.59 | 2.85 | 2.42 | 0.521 | 0.522 | 0.5 | -2.36 | -2.28 | 2.35 | 0.533 | 0.516 | 0.552 | 2.36 | 2.24 | 2.19 | Fair_Age | 9100.9 | 17668.3 | 1.903 | 0.594 | 3.2 | 0.568 | 2.85 | 0.9846 | 0.9458 | 0.8772 | 0.7841 | 1 | 0.8015 | 0.8217 | 0.9067 | 0.9067 | Good | 1 | 0 | No_Anomaly | 0 |  | Age_Years
697 | 174.2 | 220.7 | 69.2 | 69.3 | 49.4 | 357.4 | 2507 | 53.8 | 25.7 | 80.7 | 82.9 | 72.9 | 87 | 36.2 | 13.6 | 2059 | 1587.7 | 872.6 | 2383.7 | 1805.8 | 890.1 | 1.158 | 1.137 | 1.02 | 0.743 | 0.753 | 0.731 | 5.11 | 5.09 | -5.58 | 0.545 | 0.594 | 0.594 | -2.99 | 3.63 | -2.34 | 0.542 | 0.529 | 0.544 | 2.58 | -2.99 | 3.18 | 0.532 | 0.5 | 0.569 | 3.44 | 3.78 | 2.66 | Critical_IR_PI | 872.6 | 890.1 | 1.02 | 0.753 | 5.58 | 0.594 | 3.78 | 0.6185 | 0.8584 | 0.7834 | 0.9294 | 0.925 | 0.4368 | 0.7585 | 0.7281 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
698 | 1529.5 | 821.6 | 138.6 | 168.8 | 28.9 | 1195.6 | 7907.1 | 33.9 | 45 | 106.4 | 105.6 | 93.2 | 116.6 | 43.3 | 30.4 | 2321.4 | 1756.7 | 2725.5 | 2738.7 | 2097 | 3123 | 1.18 | 1.194 | 1.146 | 0.935 | 0.939 | 0.922 | 8.66 | 8.85 | 9.17 | 0.841 | 0.872 | 0.83 | 5.54 | 7.35 | 7.99 | 0.833 | 0.752 | 0.928 | 7.03 | 7.76 | 8.67 | 0.763 | 0.728 | 0.754 | 5.89 | 5.17 | 8.88 | Very Poor_Mixed | 1756.7 | 2097 | 1.146 | 0.939 | 9.17 | 0.928 | 8.88 | 0.1514 | 0.6299 | 0.1485 | 0.3825 | 1 | 0.1002 | 0.2537 | 0.3671 | 0.3671 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
699 | 410.3 | 285.7 | 78 | 72.8 | 4.8 | 481.1 | 3411.2 | 32.4 | 45.9 | 84.8 | 83 | 75.9 | 87.5 | 37.1 | 16.2 | 174 | 5923.7 | 4902 | 282.1 | 9275.2 | 7000.9 | 1.621 | 1.566 | 1.428 | 0.654 | 0.651 | 0.672 | 4.17 | 4.03 | 5.41 | 0.531 | 0.534 | 0.5 | -2.37 | -2 | -2.04 | 0.535 | 0.523 | 0.5 | -2 | 2.34 | 2.36 | 0.506 | 0.5 | 0.5 | -2 | 2.36 | -2.15 | Critical_Oil | 174 | 282.1 | 1.428 | 0.672 | 5.41 | 0.535 | 2.37 | 0.7502 | 0.6213 | 0.7197 | 0.8607 | 0.85 | 0.5565 | 0.9133 | 0.7554 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
700 | 983.1 | 550.7 | 109.9 | 125.3 | 18.7 | 903.1 | 5403.4 | 60 | 20.2 | 79.1 | 79.8 | 73.2 | 84.7 | 36.2 | 11.6 | 9727.8 | 9647.4 | 10000 | 19103.8 | 18903.9 | 20000 | 1.964 | 1.959 | 2 | 0.573 | 0.63 | 0.555 | 2.95 | 4.36 | 2.76 | 0.574 | 0.509 | 0.505 | 3.16 | 2.03 | -2.53 | 0.514 | 0.538 | 0.532 | -2.43 | 2.96 | 2.28 | 0.5 | 0.516 | 0.516 | 2.4 | -3.3 | 2.48 | Poor_DGA | 9647.4 | 18903.9 | 1.959 | 0.63 | 4.36 | 0.574 | 3.3 | 0.4002 | 0.984 | 0.8319 | 0.9744 | 1 | 0.7156 | 0.8505 | 0.7633 | 0.7633 | Fair | 1 | 1 | DGA | 0 |  | C2H2
701 | 1447.1 | 854.3 | 136.9 | 177.3 | 29.1 | 1261.5 | 7465.4 | 36.2 | 44 | 105.3 | 109.2 | 90.2 | 114.6 | 43.3 | 31.4 | 2839 | 2439.6 | 2182.7 | 3457 | 2751.3 | 2582.6 | 1.218 | 1.128 | 1.183 | 0.862 | 0.88 | 0.967 | 8.04 | 8.28 | 8.92 | 0.784 | 0.789 | 0.745 | 7.31 | 6.56 | 6.46 | 0.717 | 0.741 | 0.833 | 6.3 | 6.12 | 8.18 | 0.723 | 0.808 | 0.77 | 7.73 | 5.62 | 6.84 | Very Poor_Mixed | 2182.7 | 2582.6 | 1.128 | 0.967 | 8.92 | 0.833 | 8.18 | 0.1454 | 0.6396 | 0.162 | 0.3444 | 1 | 0.1454 | 0.306 | 0.3819 | 0.3819 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
702 | 440.1 | 233.7 | 72.5 | 112 | 3.3 | 426.4 | 3273.4 | 57.5 | 24.4 | 95.5 | 98.5 | 87.5 | 104 | 40.9 | 15.8 | 8963.6 | 8550.4 | 9075.2 | 17378.4 | 16510.5 | 17078.7 | 1.939 | 1.931 | 1.882 | 0.584 | 0.549 | 0.707 | -2.88 | 3.92 | 4.47 | 0.524 | 0.515 | 0.508 | -3.14 | 2.42 | 2.55 | 0.513 | 0.56 | 0.55 | 2.37 | 2.68 | 2.3 | 0.537 | 0.545 | 0.57 | 2.14 | 3.09 | 2.26 | Poor_Thermal | 8550.4 | 16510.5 | 1.882 | 0.707 | 4.47 | 0.57 | 3.14 | 0.7477 | 0.8804 | 0.3646 | 0.8718 | 1 | 0.6625 | 0.8096 | 0.7711 | 0.7711 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
703 | 357 | 225.1 | 72.2 | 69.6 | 1.2 | 423.3 | 2972.2 | 56 | 22.9 | 77.5 | 77.8 | 74.1 | 84.2 | 36.4 | 12.2 | 4491.6 | 4560.4 | 4909 | 6309.5 | 6744.5 | 6895.8 | 1.405 | 1.479 | 1.405 | 0.608 | 0.677 | 0.592 | 3.89 | 4.68 | 2.91 | 0.5 | 0.544 | 0.5 | 2.16 | 2.18 | 2.17 | 0.527 | 0.524 | 0.531 | 2.1 | 2.16 | 2 | 0.514 | 0.512 | 0.5 | 2.46 | 2.16 | 3.04 | Poor_IR_PI | 4491.6 | 6309.5 | 1.405 | 0.677 | 4.68 | 0.544 | 3.04 | 0.8701 | 0.9088 | 0.8603 | 0.9618 | 1 | 0.6375 | 0.8932 | 0.8707 | 0.8707 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
704 | 668.9 | 470.8 | 95.9 | 97 | 15.6 | 726.2 | 4137.9 | 49.4 | 28.8 | 91 | 91.2 | 79.2 | 97 | 38.7 | 22.9 | 5928.2 | 6638.2 | 5680.3 | 9479.4 | 10745.2 | 8969.5 | 1.599 | 1.619 | 1.579 | 0.719 | 0.76 | 0.704 | 6.05 | -5.2 | 4.75 | 0.61 | 0.636 | 0.611 | 4.1 | 4.61 | 5.25 | 0.654 | 0.691 | 0.628 | 3.73 | 4.55 | 4.17 | 0.579 | 0.629 | 0.7 | 5.4 | 5.49 | -5.04 | Poor_Mixed | 5680.3 | 8969.5 | 1.579 | 0.76 | 6.05 | 0.7 | 5.49 | 0.5267 | 0.8123 | 0.5394 | 0.6518 | 1 | 0.446 | 0.5333 | 0.6341 | 0.6341 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
705 | 363.2 | 319.3 | 86.1 | 83.9 | 60.5 | 595.9 | 3910.3 | 56.4 | 23.8 | 82.2 | 81.4 | 73.4 | 87.1 | 36.9 | 17.2 | 8325.9 | 7817 | 7111.4 | 14348.8 | 14244.7 | 11817.3 | 1.723 | 1.822 | 1.662 | 0.917 | 0.961 | 0.902 | 8.45 | 9.19 | 8.75 | 0.64 | 0.617 | 0.635 | 2.93 | 2.39 | -2.89 | 0.569 | 0.6 | 0.609 | 3.97 | 3.07 | 4.14 | 0.582 | 0.533 | 0.678 | 3.5 | 4.15 | -3.96 | Critical_Winding_TD_Cap | 7111.4 | 11817.3 | 1.662 | 0.961 | 9.19 | 0.678 | 4.15 | 0.5102 | 0.8912 | 0.7748 | 0.832 | 1 | 0.109 | 0.6313 | 0.6425 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
706 | 868 | 487.5 | 98.6 | 125.7 | 19.1 | 872.8 | 6044.2 | 46.9 | 33.8 | 92.9 | 90.4 | 83.7 | 99.4 | 40 | 25.3 | 6142.7 | 5329.7 | 5238.1 | 9495.8 | 8098.5 | 7974.6 | 1.546 | 1.52 | 1.522 | 0.738 | 0.757 | 0.769 | 5.78 | -5.81 | -6.03 | 0.691 | 0.655 | 0.762 | -4.98 | 4.74 | 5.44 | 0.625 | 0.703 | 0.735 | 5.96 | -5.67 | -4.81 | 0.712 | 0.677 | 0.743 | -4.41 | 4.26 | 4.6 | Poor_Mixed | 5238.1 | 7974.6 | 1.52 | 0.769 | 6.03 | 0.762 | 5.96 | 0.4185 | 0.7485 | 0.4832 | 0.569 | 1 | 0.3921 | 0.4431 | 0.5659 | 0.5659 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
707 | 235.5 | 159.7 | 71.7 | 60.3 | 2.3 | 422.3 | 2500 | 57.9 | 23.3 | 76.7 | 76.7 | 72 | 82.7 | 36.7 | 14.9 | 9691.7 | 10000 | 8784.9 | 19383.5 | 20000 | 16337.1 | 2 | 2 | 1.86 | 0.541 | 0.531 | 0.555 | -2.99 | 2.21 | 3.65 | 0.535 | 0.581 | 0.588 | -2 | 2.28 | 2 | 0.56 | 0.5 | 0.515 | -3.55 | 3.07 | 2.89 | 0.577 | 0.819 | 0.507 | -2.51 | 6.78 | 2.22 | Poor_Bushing_TD_Cap | 8784.9 | 16337.1 | 1.86 | 0.555 | 3.65 | 0.819 | 6.78 | 0.8636 | 0.9008 | 0.9045 | 0.8962 | 1 | 0.8054 | 0.7407 | 0.8653 | 0.8653 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
708 | 248.7 | 216.8 | 68.5 | 58.1 | 1 | 486.6 | 2706.1 | 53.9 | 25.1 | 78.5 | 76.5 | 70 | 80.2 | 35 | 14 | 9320.7 | 8806.1 | 8787.9 | 17504.7 | 16764.2 | 16077.6 | 1.878 | 1.904 | 1.83 | 0.586 | 0.559 | 0.567 | 3.52 | 3.43 | -2.72 | 0.843 | 0.535 | 0.565 | -8.22 | -2.28 | 2.52 | 0.523 | 0.569 | 0.61 | 2.67 | 3.05 | 3.12 | 0.549 | 0.602 | 0.536 | 2.92 | 3.18 | 3.94 | Poor_Bushing_TD_Cap | 8787.9 | 16077.6 | 1.83 | 0.586 | 3.52 | 0.843 | 8.22 | 0.9226 | 0.8683 | 0.931 | 0.9194 | 1 | 0.7414 | 0.6715 | 0.8586 | 0.8586 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
709 | 290.7 | 253.5 | 78.1 | 70.8 | 1.1 | 496.3 | 3648.8 | 22.5 | 23.6 | 83.5 | 82.8 | 78.8 | 90.9 | 37.1 | 13.7 | 7274.8 | 9655.5 | 7358.3 | 12982.5 | 17579.5 | 12844.5 | 1.785 | 1.821 | 1.746 | 0.624 | 0.632 | 0.618 | 3.49 | 4.11 | 3.77 | 0.567 | 0.563 | 0.5 | 2.24 | -2.46 | 3.01 | 0.5 | 0.581 | 0.673 | 2.75 | 3.19 | -2 | 0.556 | 0.913 | 0.597 | 3.16 | 8.6 | 3.61 | Critical_Bushing_TD_Cap | 7274.8 | 12844.5 | 1.746 | 0.632 | 4.11 | 0.913 | 8.6 | 0.8597 | 0.3117 | 0.6935 | 0.9269 | 1 | 0.6374 | 0.6835 | 0.7403 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
710 | 877.4 | 491.9 | 105.4 | 108.2 | 15.9 | 869.2 | 5290.7 | 43.4 | 34.4 | 89.7 | 89.6 | 81.8 | 95.6 | 40 | 24.7 | 5798.3 | 5670 | 5616.7 | 8966.1 | 9246.5 | 8413.2 | 1.546 | 1.631 | 1.498 | 0.682 | 0.667 | 0.773 | 5.72 | 4.7 | 6.03 | 0.721 | 0.703 | 0.727 | 4.26 | 4.67 | 4.43 | 0.684 | 0.772 | 0.707 | 4.62 | 4.63 | 4.57 | 0.793 | 0.708 | 0.587 | -3.66 | 5.86 | 5.32 | Poor_Mixed | 5616.7 | 8413.2 | 1.498 | 0.773 | 6.03 | 0.793 | 5.86 | 0.4582 | 0.7414 | 0.5402 | 0.59 | 1 | 0.4573 | 0.4443 | 0.591 | 0.591 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
711 | 1027.4 | 608.3 | 107.1 | 136.5 | 24.2 | 952.1 | 6023.2 | 56 | 24.6 | 81.6 | 84.7 | 74.1 | 87 | 37 | 11.7 | 9446.8 | 9556.9 | 8830.9 | 18323.7 | 18550.5 | 16740.3 | 1.94 | 1.941 | 1.896 | 0.624 | 0.656 | 0.601 | 3.43 | 4.44 | -3.78 | 0.541 | 0.503 | 0.505 | 2.22 | 2.63 | 3.29 | 0.523 | 0.554 | 0.513 | 3.08 | 2.78 | 3.44 | 0.553 | 0.556 | 0.5 | 2.26 | 2.87 | -2.49 | Poor_DGA | 8830.9 | 16740.3 | 1.896 | 0.656 | 4.44 | 0.556 | 3.44 | 0.3386 | 0.8768 | 0.7484 | 0.9724 | 1 | 0.6301 | 0.8302 | 0.711 | 0.711 | Fair | 1 | 1 | DGA | 0 |  | C2H2
712 | 472.6 | 306.8 | 79.1 | 85 | 1 | 527.6 | 3741.1 | 30.9 | 49.4 | 81.8 | 82.5 | 74.4 | 87.1 | 36.8 | 18.2 | 5036.8 | 6096.3 | 5449.7 | 7600.1 | 9337.9 | 8488.9 | 1.509 | 1.532 | 1.558 | 0.69 | 0.634 | 1.883 | 4.81 | 4 | 4.58 | 0.6 | 0.555 | 0.535 | -2.92 | -2.66 | 2.49 | 0.549 | 0.562 | 0.554 | -2.93 | 3.37 | 2.72 | 0.536 | 0.579 | 0.562 | 3.58 | 2.76 | -2.91 | Critical_Oil | 5036.8 | 7600.1 | 1.509 | 1.883 | 4.81 | 0.6 | 3.58 | 0.8364 | 0.5888 | 0.7617 | 0.8024 | 1 | 0.4701 | 0.7334 | 0.7539 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | Moisture_PPM
713 | 1023.7 | 556.7 | 109.2 | 123.5 | 23 | 841.2 | 5086.2 | 50.3 | 32.1 | 90.9 | 88.2 | 80.6 | 98.5 | 38.8 | 25.6 | 6094.3 | 6479.5 | 5572.5 | 9498.9 | 10045.6 | 8010.7 | 1.559 | 1.55 | 1.438 | 0.664 | 0.726 | 0.718 | 4.88 | 5.52 | 5.84 | 0.616 | 0.672 | 0.649 | -3.56 | 5.73 | 3.74 | 0.703 | 0.681 | 0.657 | 4.38 | -3.95 | -4.59 | 0.658 | 0.737 | 0.74 | 6.2 | -4.58 | -5.67 | Poor_Mixed | 5572.5 | 8010.7 | 1.438 | 0.726 | 5.84 | 0.74 | 6.2 | 0.3849 | 0.7691 | 0.5426 | 0.5584 | 1 | 0.4642 | 0.479 | 0.5819 | 0.5819 | Poor | 0 | 1 | DGA | 0 |  | C2H2
714 | 329.9 | 179.4 | 76.4 | 63.5 | 1.4 | 416.9 | 3290.2 | 54.4 | 27.8 | 83.7 | 82.9 | 76.2 | 87.1 | 38.3 | 12 | 7590 | 8983.4 | 9178.8 | 14139.4 | 16048.7 | 17825.3 | 1.863 | 1.786 | 1.942 | 0.633 | 0.658 | 0.623 | -17.2 | -3.89 | 4.04 | 0.562 | 0.54 | 0.53 | -3.7 | -4.5 | 3.47 | 0.634 | 0.99 | 0.606 | 2.52 | 9.51 | -4.56 | 0.575 | 0.549 | 0.624 | 3.86 | -3.35 | 4.27 | Critical_Bushing_TD_Cap | 7590 | 14139.4 | 1.786 | 0.658 | 17.2 | 0.99 | 9.51 | 0.8718 | 0.8264 | 0.7217 | 0.9661 | 1 | 0.5043 | 0.5956 | 0.7754 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_HV_CapChange_pct
715 | 330 | 254.7 | 77.8 | 65 | 4.8 | 515.6 | 2968.6 | 56.6 | 21.6 | 76.6 | 80.4 | 72.4 | 80.2 | 35.9 | 15.6 | 9204.6 | 9560.6 | 8171.7 | 18155.7 | 18466.3 | 15033.4 | 1.972 | 1.932 | 1.84 | 0.551 | 0.539 | 0.531 | -2.96 | 2.39 | -2.54 | 0.543 | 0.536 | 0.501 | 2.44 | 2 | 2.83 | 0.527 | 0.53 | 0.551 | 2 | 3.03 | -2 | 0.542 | 0.5 | 0.55 | 3.03 | 3 | 2.03 | Good_Mixed | 8171.7 | 15033.4 | 1.84 | 0.551 | 2.96 | 0.551 | 3.03 | 0.7692 | 0.938 | 0.8828 | 0.8773 | 1 | 0.8292 | 0.8345 | 0.8633 | 0.8633 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
716 | 1525.5 | 856.7 | 133.7 | 177.9 | 30.9 | 1274.1 | 7917.5 | 32.5 | 46.8 | 109.3 | 108.3 | 96.1 | 119.2 | 45.6 | 34 | 907.4 | 792.8 | 1979.1 | 1200 | 1200 | 2181.5 | 1.322 | 1.514 | 1.102 | 0.97 | 0.963 | 0.989 | -9.55 | 9.23 | 9.46 | 0.869 | 0.722 | 0.734 | -6.41 | -8.37 | 7.12 | 0.787 | 0.899 | 0.865 | -6.54 | -7.44 | 6.99 | 0.849 | 0.759 | 0.824 | 7.11 | -7.43 | -5.79 | Very Poor_Mixed | 792.8 | 1200 | 1.102 | 0.989 | 9.55 | 0.899 | 8.37 | 0.1261 | 0.6128 | 0.0721 | 0.2434 | 1 | 0.046 | 0.2561 | 0.337 | 0.337 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
717 | 224.4 | 205.5 | 68.9 | 61.5 | 2 | 369.8 | 3487.2 | 60 | 20.7 | 76.3 | 77.3 | 70 | 80 | 35 | 11.5 | 9771.5 | 10000 | 9553.4 | 18695.7 | 19689.4 | 18322.5 | 1.913 | 1.969 | 1.918 | 0.563 | 0.517 | 0.554 | 3.92 | 2.32 | 3.22 | 0.582 | 0.504 | 0.512 | 2.47 | 2.74 | 2 | 0.509 | 0.5 | 0.513 | 2.42 | 2.36 | 2.23 | 0.527 | 0.518 | 0.504 | 2 | 2 | -2.23 | Good_Mixed | 9553.4 | 18322.5 | 1.913 | 0.563 | 3.92 | 0.582 | 2.74 | 0.8724 | 0.9638 | 0.9464 | 0.9764 | 1 | 0.7907 | 0.8849 | 0.9072 | 0.9072 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
718 | 1361.7 | 712.3 | 122 | 164.1 | 25.2 | 1018.5 | 7161.7 | 38 | 41.7 | 99.7 | 100.6 | 88.2 | 110.3 | 43.2 | 35.6 | 143.5 | 2417.5 | 2057.6 | 240.8 | 3117.2 | 2409.3 | 1.678 | 1.289 | 1.171 | 0.905 | 0.807 | 0.854 | 7.75 | 7.23 | 7.98 | 0.7 | 0.742 | 0.774 | 7.3 | 5.97 | 6.38 | 0.799 | 0.779 | 0.853 | -7.35 | 5.51 | 6.99 | 0.768 | 0.76 | 0.836 | -4.1 | 7.62 | 7.12 | Critical_Mixed | 143.5 | 240.8 | 1.171 | 0.905 | 7.98 | 0.853 | 7.62 | 0.2402 | 0.6624 | 0.2757 | 0.1798 | 0.85 | 0.2187 | 0.306 | 0.3978 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
719 | 1076.3 | 515.3 | 108.6 | 106.7 | 17.8 | 834.8 | 5780.9 | 44.4 | 33.8 | 89.7 | 89.7 | 80.3 | 100 | 40.7 | 26 | 5278.6 | 5527.5 | 6266.3 | 8512.3 | 8588.3 | 10045.8 | 1.613 | 1.554 | 1.603 | 0.676 | 0.744 | 0.691 | 5.48 | 6.13 | 6.22 | 0.623 | 0.668 | 0.686 | 4.53 | 5.61 | 5.07 | 0.671 | 0.662 | 0.702 | 4.63 | 5.88 | -4.46 | 0.671 | 0.651 | 0.591 | 3.97 | 4.24 | 5.18 | Poor_Mixed | 5278.6 | 8512.3 | 1.554 | 0.744 | 6.22 | 0.702 | 5.88 | 0.4262 | 0.7485 | 0.5228 | 0.5442 | 1 | 0.4339 | 0.4996 | 0.5865 | 0.5865 | Poor | 0 | 1 | DGA | 0 |  | C2H2
720 | 1586.1 | 865.5 | 131.4 | 177.7 | 28.9 | 1263.5 | 7730.1 | 35.5 | 44 | 107.3 | 105.8 | 94.1 | 114.1 | 43.2 | 32 | 3502.4 | 1978.8 | 2259 | 4395.7 | 2461.9 | 2707.6 | 1.255 | 1.244 | 1.199 | 0.912 | 0.846 | 0.942 | 8.68 | 7.87 | -8.78 | 0.827 | 0.834 | 0.716 | 8.15 | 8.71 | -5.6 | 0.93 | 0.872 | 0.771 | 8.71 | 8.1 | -7.21 | 0.763 | 0.776 | 0.858 | 9.1 | 8.58 | 7.41 | Very Poor_Mixed | 1978.8 | 2461.9 | 1.199 | 0.942 | 8.78 | 0.93 | 9.1 | 0.1356 | 0.6396 | 0.1507 | 0.3214 | 1 | 0.1458 | 0.2222 | 0.3622 | 0.3622 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
721 | 1730.9 | 943.5 | 147.7 | 197 | 33.4 | 1319.1 | 8863.1 | 31.5 | 48.5 | 104.7 | 108.1 | 94.9 | 114.3 | 44.7 | 32.8 | 2528.5 | 1453.7 | 1269.9 | 3158.2 | 1543.3 | 1367.5 | 1.249 | 1.062 | 1.077 | 0.978 | 0.981 | 0.99 | 8.6 | -9.83 | -9.83 | 0.92 | 0.756 | 0.852 | 6.28 | -7.02 | -9.35 | 0.783 | 0.722 | 0.798 | -6.61 | 6.92 | 9.31 | 0.694 | 0.848 | 0.746 | 5.79 | 5.77 | 8.86 | Very Poor_Mixed | 1269.9 | 1367.5 | 1.062 | 0.99 | 9.83 | 0.92 | 9.35 | 0.0467 | 0.597 | 0.1361 | 0.2904 | 1 | 0.04 | 0.2682 | 0.3253 | 0.3253 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
722 | 1506.5 | 799.1 | 140.2 | 180.1 | 28.8 | 1233.3 | 7273.1 | 33.1 | 47.2 | 105.8 | 104.1 | 93.4 | 115.5 | 44.9 | 34.1 | 1153.5 | 1537.7 | 690 | 1250 | 1614.6 | 1200 | 1.084 | 1.05 | 1.739 | 0.929 | 0.916 | 0.914 | 8.37 | -8.95 | -8.69 | 0.745 | 0.929 | 0.738 | 7.87 | 6.07 | -6.31 | 0.903 | 0.918 | 0.833 | 6.84 | 8.83 | 6.83 | 0.916 | 0.735 | 0.827 | 8.61 | 7.35 | 6.88 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.929 | 8.95 | 0.929 | 8.83 | 0.1491 | 0.609 | 0.153 | 0.2395 | 1 | 0.12 | 0.2244 | 0.3548 | 0.3548 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
723 | 816.2 | 495.1 | 98.7 | 107.6 | 13.9 | 688.1 | 5074.1 | 46.5 | 33.4 | 92.4 | 90.6 | 82 | 96.1 | 39.7 | 24.6 | 6103.3 | 5605.6 | 6319 | 9107.5 | 8928.9 | 10204.7 | 1.492 | 1.593 | 1.615 | 0.791 | 0.717 | 0.769 | 6.8 | 6.14 | 6.63 | 0.69 | 0.7 | 0.651 | 5.35 | 5.7 | 5.08 | 0.733 | 0.659 | 0.724 | 4.84 | 6.32 | 3.56 | 0.684 | 0.689 | 0.682 | -4.06 | 5.61 | 4.56 | Poor_Mixed | 5605.6 | 8928.9 | 1.492 | 0.791 | 6.8 | 0.733 | 6.32 | 0.5073 | 0.7532 | 0.5142 | 0.5935 | 1 | 0.3537 | 0.4531 | 0.5894 | 0.5894 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
724 | 1545.6 | 945.4 | 139.2 | 191.2 | 34.3 | 1251.6 | 8312.3 | 30.6 | 48.4 | 106.1 | 107.6 | 95.8 | 115.6 | 43.7 | 34.5 | 1015.6 | 1598.6 | 1713.9 | 1200 | 1678.5 | 1799.6 | 1.182 | 1.05 | 1.05 | 0.99 | 0.99 | 0.966 | -9.09 | 8.72 | 9.49 | 0.86 | 0.841 | 0.798 | -8.53 | 5.45 | 6.83 | 0.814 | 0.762 | 0.758 | 6.56 | 7.52 | 7.46 | 0.882 | 0.791 | 0.783 | 8.05 | 7.65 | 5.7 | Very Poor_Mixed | 1015.6 | 1200 | 1.05 | 0.99 | 9.49 | 0.882 | 8.53 | 0.082 | 0.5979 | 0.1269 | 0.2237 | 1 | 0.0565 | 0.255 | 0.3299 | 0.3299 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
725 | 852.5 | 533.1 | 105.3 | 124.5 | 18.2 | 876 | 5673.3 | 47.6 | 32.7 | 90.7 | 87.1 | 81 | 97.4 | 40.6 | 25.2 | 4109.9 | 4639.6 | 4163.3 | 5544.9 | 6664.5 | 6129.2 | 1.349 | 1.436 | 1.472 | 0.735 | 0.754 | 0.81 | -5.5 | 6.37 | 6.44 | 0.715 | 0.667 | 0.78 | 4.7 | 5.3 | 5.16 | 0.591 | 0.671 | 0.668 | 5.25 | -5.22 | -3.67 | 0.638 | 0.703 | 0.605 | -4.2 | -4.86 | 5.51 | Poor_Mixed | 4109.9 | 5544.9 | 1.349 | 0.81 | 6.44 | 0.78 | 5.51 | 0.4201 | 0.7617 | 0.543 | 0.5725 | 1 | 0.3705 | 0.4853 | 0.5786 | 0.5786 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
726 | 1660.4 | 929.3 | 140.8 | 193.2 | 34.1 | 1289.7 | 8981.9 | 32.9 | 46.4 | 105.2 | 101.7 | 92 | 113.8 | 44.5 | 33.6 | 1026.1 | 2192.3 | 1419.1 | 1200 | 2335.9 | 1731.7 | 1.169 | 1.066 | 1.22 | 0.973 | 0.96 | 0.926 | 9.63 | -8.78 | 8.74 | 0.847 | 0.777 | 0.881 | 7.19 | 8.73 | -5.54 | 0.748 | 0.916 | 0.87 | 6.27 | -7.74 | 6.41 | 0.868 | 0.948 | 0.928 | 5.3 | 9.5 | 6.45 | Very Poor_Mixed | 1026.1 | 1200 | 1.066 | 0.973 | 9.63 | 0.948 | 9.5 | 0.0604 | 0.6166 | 0.1893 | 0.2591 | 1 | 0.0783 | 0.2084 | 0.3295 | 0.3295 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
727 | 871.9 | 472.6 | 90.7 | 93 | 13.7 | 656.5 | 4270.9 | 56.2 | 24.1 | 81.3 | 78.6 | 73 | 86.1 | 35.2 | 11.4 | 9015.4 | 9146.2 | 9399.6 | 16931.7 | 17283.6 | 18674.7 | 1.878 | 1.89 | 1.987 | 0.5 | 0.526 | 0.537 | 2 | 2.48 | 2 | 0.537 | 0.525 | 0.505 | 2.47 | 2.69 | 2.64 | 0.5 | 0.539 | 0.543 | 2.6 | 2.5 | -2.63 | 0.527 | 0.568 | 0.54 | 2.3 | -3.02 | 2.54 | Fair_DGA | 9015.4 | 16931.7 | 1.878 | 0.537 | 2.48 | 0.568 | 3.02 | 0.5395 | 0.8857 | 0.8227 | 0.9783 | 1 | 0.9181 | 0.8226 | 0.809 | 0.809 | Good | 1 | 1 | DGA | 0 |  | C2H2
728 | 265.2 | 120 | 67.3 | 56.1 | 1 | 464.7 | 2539 | 56 | 27 | 75 | 75.1 | 72.6 | 80.7 | 35.8 | 12.4 | 5817.7 | 4378.9 | 5073.9 | 8930 | 6851.2 | 7621.1 | 1.535 | 1.565 | 1.502 | 0.646 | 0.628 | 0.665 | 4.31 | -4.93 | 4.44 | 0.567 | 0.546 | 0.52 | -2.67 | 2.36 | 2.9 | 0.504 | 0.534 | 0.549 | 2.17 | 2.13 | 2.25 | 0.531 | 0.507 | 0.512 | 2.68 | 2.38 | -2.46 | Poor_IR_PI | 4378.9 | 6851.2 | 1.502 | 0.665 | 4.93 | 0.567 | 2.9 | 0.9414 | 0.8382 | 0.9622 | 0.9575 | 1 | 0.5679 | 0.8319 | 0.8693 | 0.8693 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
729 | 903.6 | 483.6 | 97.8 | 117.5 | 15.7 | 819.2 | 5519.8 | 46.3 | 33.8 | 88.4 | 87.8 | 80.3 | 96.8 | 39.7 | 23.3 | 5665.9 | 6078.8 | 6569.6 | 8836.7 | 9622.5 | 11403 | 1.56 | 1.583 | 1.736 | 0.711 | 0.791 | 0.74 | 6.03 | 7.05 | 5.81 | 0.639 | 0.69 | 0.614 | -4.63 | 5.67 | 4.79 | 0.57 | 0.628 | 0.754 | 3.95 | 5.11 | -3.45 | 0.689 | 0.651 | 0.582 | 4.78 | 4.99 | 3.45 | Poor_Mixed | 5665.9 | 8836.7 | 1.56 | 0.791 | 7.05 | 0.754 | 5.67 | 0.4584 | 0.7485 | 0.5669 | 0.6382 | 1 | 0.3761 | 0.5312 | 0.6013 | 0.6013 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
730 | 514.9 | 394.8 | 92.1 | 152 | 62.7 | 640.7 | 3533.8 | 59.4 | 21.9 | 101.9 | 104.2 | 90.5 | 108.7 | 43 | 16.9 | 7950.6 | 7709.4 | 7906 | 14135.5 | 13894.2 | 14314.9 | 1.778 | 1.802 | 1.811 | 0.562 | 0.582 | 0.591 | 2.82 | 2.65 | -3.97 | 0.572 | 0.6 | 0.53 | 2.43 | 3.5 | -4.21 | 0.578 | 0.55 | 0.635 | 3.58 | 2.92 | 2.85 | 0.601 | 0.522 | 0.517 | -3.28 | 3.6 | 3.31 | Critical_Thermal | 7709.4 | 13894.2 | 1.778 | 0.591 | 3.97 | 0.635 | 4.21 | 0.4131 | 0.9307 | 0.2385 | 0.8407 | 1 | 0.7367 | 0.7093 | 0.6717 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
731 | 1671.2 | 973.2 | 141.7 | 180.1 | 36 | 1253 | 8635.3 | 55.1 | 24.6 | 83.8 | 86.8 | 78.3 | 90.7 | 37.6 | 18 | 8171.8 | 7772.4 | 9021.7 | 14878.3 | 13825.5 | 17121.8 | 1.821 | 1.779 | 1.898 | 0.611 | 0.544 | 0.571 | 3.63 | 2.86 | 3.49 | 0.5 | 0.519 | 0.529 | 2 | 2.65 | 3.04 | 0.504 | 0.504 | 0.528 | 2.34 | 2 | 2.05 | 0.5 | 0.5 | 0.574 | -2.46 | -2.17 | 2.89 | Critical_DGA | 7772.4 | 13825.5 | 1.779 | 0.611 | 3.63 | 0.574 | 3.04 | 0.0698 | 0.8768 | 0.6634 | 0.8084 | 1 | 0.7304 | 0.8919 | 0.6522 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
732 | 1458.6 | 781.5 | 128.4 | 171.4 | 33.3 | 1215.1 | 7952.7 | 34.2 | 45.7 | 103.9 | 107.1 | 90.9 | 113.3 | 43 | 30.1 | 1766.6 | 3313.9 | 2484.2 | 2075.6 | 4307.3 | 2666.3 | 1.175 | 1.3 | 1.073 | 0.945 | 0.936 | 0.881 | 8.64 | 9.06 | -8.27 | 0.816 | 0.835 | 0.766 | 5.98 | 6.38 | -5.93 | 0.882 | 0.79 | 0.672 | 5.62 | -4.91 | -7.76 | 0.852 | 0.799 | 0.735 | 6.46 | 7.98 | 5.41 | Very Poor_Mixed | 1766.6 | 2075.6 | 1.073 | 0.945 | 9.06 | 0.882 | 7.98 | 0.1441 | 0.6232 | 0.1858 | 0.3938 | 1 | 0.1202 | 0.2993 | 0.3798 | 0.3798 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
733 | 214.7 | 183.6 | 66.6 | 57.5 | 1.2 | 440.3 | 3565.1 | 56.9 | 22.9 | 76.2 | 76.3 | 70.7 | 80 | 35.5 | 10.4 | 8331.3 | 9342.1 | 9166.8 | 15781.1 | 17525.8 | 17199.7 | 1.894 | 1.876 | 1.876 | 0.676 | 0.682 | 0.677 | -4.97 | 4.55 | 4.6 | 0.514 | 0.5 | 0.559 | 2.12 | 2 | 2 | 0.5 | 0.501 | 0.5 | 2.19 | 2 | 2 | 0.5 | 0.523 | 0.5 | -2.16 | 2.36 | 2.83 | Fair_Winding_TD_Cap | 8331.3 | 15781.1 | 1.876 | 0.682 | 4.97 | 0.559 | 2.83 | 0.9029 | 0.9088 | 0.9473 | 0.9955 | 1 | 0.5267 | 0.9357 | 0.8815 | 0.8815 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
734 | 1603.4 | 914.2 | 144.1 | 179.6 | 27.3 | 1268.5 | 7871 | 31.2 | 47.1 | 108.9 | 107.4 | 95.1 | 117.4 | 44.5 | 33.2 | 2017.6 | 2506.4 | 1833.5 | 2301.5 | 2955.7 | 2189.2 | 1.141 | 1.179 | 1.194 | 0.966 | 0.969 | 0.976 | 8.7 | 9.46 | -9.84 | 0.894 | 0.915 | 0.923 | 6.83 | 4.96 | 6.56 | 0.904 | 0.789 | 0.766 | 6.36 | -8.21 | -8.01 | 0.792 | 0.737 | 0.915 | -6.25 | 6.36 | 6.56 | Very Poor_Mixed | 1833.5 | 2189.2 | 1.141 | 0.976 | 9.84 | 0.923 | 8.21 | 0.1227 | 0.61 | 0.1018 | 0.2748 | 1 | 0.0525 | 0.2346 | 0.3374 | 0.3374 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
735 | 1509.7 | 876.4 | 137.1 | 177.8 | 27.9 | 1270.6 | 8096.9 | 34.5 | 45.3 | 104.2 | 105.2 | 91.2 | 113.3 | 44.5 | 30.7 | 2106.9 | 2085.6 | 2009.3 | 2575 | 2594.7 | 2421.4 | 1.222 | 1.244 | 1.205 | 0.962 | 0.857 | 0.93 | -8.65 | -7.7 | 9.48 | 0.727 | 0.752 | 0.758 | -9.37 | -7.43 | 6.68 | 0.885 | 0.841 | 0.703 | -7.27 | 7.02 | 7.43 | 0.796 | 0.732 | 0.757 | 6.36 | -6.3 | 6.53 | Very Poor_Mixed | 2009.3 | 2421.4 | 1.205 | 0.962 | 9.48 | 0.885 | 9.37 | 0.1346 | 0.627 | 0.1821 | 0.3711 | 1 | 0.1262 | 0.2906 | 0.3756 | 0.3756 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
736 | 729.3 | 417.9 | 91.7 | 96 | 12.1 | 662.8 | 4625.8 | 53.2 | 28.6 | 83.8 | 87.9 | 78.2 | 94.9 | 37.7 | 18.6 | 7763.8 | 5922.6 | 6852.7 | 13215.8 | 9702.6 | 11506.1 | 1.702 | 1.638 | 1.679 | 0.617 | 0.612 | 0.657 | 3.42 | 3.8 | 4.8 | 0.612 | 0.56 | 0.565 | 3.01 | -3.82 | 2.92 | 0.632 | 0.623 | 0.588 | 3.31 | -3.28 | 2.81 | 0.591 | 0.606 | 0.62 | 3.58 | -3.22 | 2.66 | Fair_Mixed | 5922.6 | 9702.6 | 1.638 | 0.657 | 4.8 | 0.632 | 3.82 | 0.5612 | 0.815 | 0.6348 | 0.7902 | 1 | 0.6208 | 0.6495 | 0.7049 | 0.7049 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
737 | 192.2 | 217.5 | 72.9 | 54.7 | 4.4 | 414.3 | 2831.5 | 53.3 | 26.8 | 77.7 | 75 | 70.3 | 80 | 35 | 10 | 8443.5 | 8873.8 | 9663 | 15763.8 | 16407.8 | 18501.8 | 1.867 | 1.849 | 1.915 | 0.565 | 0.545 | 0.533 | 3.06 | 2.65 | 2 | 0.521 | 0.547 | 0.535 | 2.19 | -2.26 | 2.35 | 0.502 | 0.556 | 0.515 | 2.28 | 2.18 | 3.11 | 0.5 | 0.52 | 0.5 | 2 | 3.08 | -2.18 | Fair_Oil | 8443.5 | 15763.8 | 1.849 | 0.565 | 3.06 | 0.556 | 3.11 | 0.8303 | 0.8412 | 0.9584 | 1 | 1 | 0.8243 | 0.87 | 0.8864 | 0.8864 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
738 | 283.7 | 215.6 | 77.4 | 109.6 | 4.1 | 489.7 | 3565.3 | 55.7 | 24.4 | 98.4 | 97.5 | 89.3 | 108 | 42.1 | 15.1 | 10000 | 8697.3 | 8926 | 20000 | 15657.4 | 16670.8 | 2 | 1.8 | 1.868 | 0.545 | 0.523 | 0.553 | 2 | 2.19 | 3.43 | 0.561 | 0.573 | 0.609 | 3.04 | -3.08 | 2.44 | 0.57 | 0.554 | 0.553 | 2.81 | 3.38 | 2.47 | 0.543 | 0.569 | 0.61 | 2.09 | 3.99 | 2 | Poor_Thermal | 8697.3 | 15657.4 | 1.8 | 0.553 | 3.43 | 0.61 | 3.99 | 0.7376 | 0.8804 | 0.3144 | 0.8908 | 1 | 0.841 | 0.7175 | 0.7729 | 0.7729 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
739 | 414.5 | 367.6 | 81.8 | 84.2 | 2.5 | 536.8 | 4211.2 | 33.3 | 58.8 | 82.2 | 83.3 | 72.9 | 86.5 | 36.4 | 14.7 | 5242.1 | 4878.7 | 4749.7 | 7505.8 | 6571.8 | 7147.8 | 1.432 | 1.347 | 1.505 | 0.703 | 0.691 | 0.7 | 4.93 | 4.31 | 5.13 | 0.568 | 0.529 | 0.538 | 3.27 | 2.82 | 3.22 | 0.525 | 0.507 | 0.522 | -2.91 | 2.46 | -2 | 0.546 | 0.546 | 0.549 | -2.43 | -3.12 | 2.9 | Critical_Oil | 4749.7 | 6571.8 | 1.347 | 0.703 | 5.13 | 0.568 | 3.27 | 0.7499 | 0.5833 | 0.7695 | 0.9014 | 1 | 0.5033 | 0.7934 | 0.7528 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
740 | 589.2 | 367.3 | 92 | 98 | 78.2 | 629.4 | 4459.4 | 56.5 | 22.7 | 87 | 82.1 | 78.9 | 94.2 | 38.3 | 13.6 | 7272.7 | 6834.9 | 7957.8 | 12170.6 | 10942.5 | 14295.9 | 1.673 | 1.601 | 1.796 | 0.99 | 0.931 | 0.958 | 9.2 | 9.61 | -9.84 | 0.535 | 0.516 | 0.547 | 2.52 | -3.01 | 3.09 | 0.531 | 0.516 | 0.577 | 3.23 | -2.86 | -2.17 | 0.563 | 0.581 | 0.557 | 3.5 | 2.7 | 2.43 | Critical_Winding_TD_Cap | 6834.9 | 10942.5 | 1.601 | 0.99 | 9.84 | 0.581 | 3.5 | 0.4558 | 0.9129 | 0.6495 | 0.9294 | 1 | 0.0489 | 0.7675 | 0.6399 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
741 | 851.6 | 538.2 | 101.5 | 106.7 | 17.9 | 784.4 | 4877.5 | 44.9 | 35.7 | 91.1 | 95.5 | 82.1 | 98.6 | 39.6 | 25.2 | 5864 | 5441.9 | 6296.2 | 8391.8 | 8549.8 | 10609.9 | 1.431 | 1.571 | 1.685 | 0.739 | 0.718 | 0.728 | 5.33 | 5.66 | 5.94 | 0.67 | 0.726 | 0.768 | 4.71 | -4.41 | -6.11 | 0.617 | 0.7 | 0.704 | 3.43 | -4.03 | 5.89 | 0.729 | 0.727 | 0.665 | 6.13 | 4.62 | 5.55 | Poor_Mixed | 5441.9 | 8391.8 | 1.431 | 0.739 | 5.94 | 0.768 | 6.13 | 0.4612 | 0.7265 | 0.479 | 0.5725 | 1 | 0.4275 | 0.4435 | 0.5787 | 0.5787 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
742 | 1403.7 | 875.4 | 132.5 | 171 | 29.3 | 1225.2 | 7542.8 | 35.6 | 42 | 105.5 | 102.9 | 91.6 | 111.9 | 44.1 | 32.5 | 2439.7 | 1722.1 | 2937.3 | 2765.1 | 2022.4 | 3276.5 | 1.133 | 1.174 | 1.115 | 0.898 | 0.963 | 0.937 | 9.08 | 9.15 | -9.11 | 0.745 | 0.812 | 0.76 | 7.42 | -8.64 | 6.89 | 0.814 | 0.764 | 0.891 | -6.08 | 8.63 | 8.1 | 0.764 | 0.831 | 0.725 | 7.7 | -6.59 | 6.58 | Very Poor_Mixed | 1722.1 | 2022.4 | 1.115 | 0.963 | 9.15 | 0.891 | 8.64 | 0.1571 | 0.6594 | 0.1954 | 0.302 | 1 | 0.0889 | 0.2647 | 0.3731 | 0.3731 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
743 | 330.3 | 268 | 82.1 | 79.5 | 9.2 | 534 | 3231.3 | 54.2 | 25.8 | 81 | 84.4 | 74.2 | 87.6 | 37.2 | 14.3 | 8395 | 9143.1 | 8671.9 | 15483 | 17668.5 | 16294.6 | 1.844 | 1.932 | 1.879 | 0.558 | 0.551 | 0.504 | 3.23 | 3.48 | 2.77 | 0.505 | 0.568 | 0.551 | -3.06 | 3.31 | 3.78 | 0.546 | 0.514 | 0.586 | -2.67 | 2.77 | 2.76 | 0.546 | 0.554 | 0.562 | 2.72 | 3.08 | 2.4 | Fair_Mixed | 8395 | 15483 | 1.844 | 0.558 | 3.48 | 0.586 | 3.78 | 0.6923 | 0.8568 | 0.7506 | 0.9118 | 1 | 0.8062 | 0.762 | 0.8066 | 0.8066 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
744 | 235.3 | 120 | 65 | 58.8 | 2.1 | 422.2 | 2524.6 | 60 | 20 | 76 | 76.9 | 70.1 | 80.5 | 35 | 14.6 | 8193.4 | 9930.8 | 9957.2 | 16177.2 | 19807.8 | 19857 | 1.974 | 1.995 | 1.994 | 0.5 | 0.5 | 0.522 | 2.67 | 2.08 | 2.43 | 0.514 | 0.521 | 0.535 | 2 | 2 | 2 | 0.508 | 0.5 | 0.507 | 2 | 2.49 | -2 | 0.508 | 0.537 | 0.554 | 2 | 2.5 | 3.13 | Good_Mixed | 8193.4 | 16177.2 | 1.974 | 0.522 | 2.67 | 0.554 | 3.13 | 0.8798 | 1 | 0.9499 | 0.904 | 1 | 0.9378 | 0.8785 | 0.9296 | 0.9296 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
745 | 115 | 120 | 65 | 58 | 1 | 350 | 2709 | 56.1 | 23.5 | 77.8 | 79.3 | 70.9 | 84.6 | 35.4 | 11.2 | 8491.5 | 7833.9 | 8525.5 | 15874.2 | 14367.2 | 15405.1 | 1.869 | 1.834 | 1.807 | 0.562 | 0.556 | 0.564 | 2.51 | -2.49 | 2.94 | 0.5 | 0.5 | 0.513 | 2.7 | 2 | -2.12 | 0.545 | 0.52 | 0.522 | 2.57 | 2.66 | -2.54 | 0.534 | 0.507 | 0.512 | 2 | 2 | 2 | Fair_IR_PI | 7833.9 | 14367.2 | 1.807 | 0.564 | 2.94 | 0.545 | 2.7 | 0.9791 | 0.8969 | 0.8741 | 0.9821 | 1 | 0.7945 | 0.8882 | 0.92 | 0.92 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
746 | 1589.2 | 852.9 | 137.2 | 172.2 | 31.5 | 1185.4 | 8181.5 | 36.3 | 45.9 | 104.1 | 107.5 | 95.5 | 114 | 43.8 | 31.4 | 2298.9 | 690 | 690 | 2746.1 | 1200 | 1200 | 1.195 | 1.739 | 1.739 | 0.931 | 0.968 | 0.989 | -8.71 | 9.55 | -9.76 | 0.931 | 0.735 | 0.765 | -6.86 | -6.02 | -5.51 | 0.787 | 0.815 | 0.742 | 8.77 | 7.67 | 5.91 | 0.878 | 0.933 | 0.848 | 6.13 | 8.13 | -9.02 | Very Poor_Mixed | 690 | 1200 | 1.195 | 0.989 | 9.76 | 0.933 | 9.02 | 0.1276 | 0.6213 | 0.1475 | 0.3444 | 1 | 0.0574 | 0.2413 | 0.3499 | 0.3499 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
747 | 1463.9 | 815.2 | 125.2 | 163.8 | 32 | 1175.4 | 7128.8 | 36.8 | 45.4 | 100.6 | 102.8 | 91.5 | 109 | 42.8 | 36.4 | 2595.6 | 394.3 | 2651.4 | 3124.7 | 669.6 | 3431.9 | 1.204 | 1.698 | 1.294 | 0.887 | 0.808 | 0.89 | 7.48 | 7.55 | 8.52 | 0.899 | 0.85 | 0.882 | 6.38 | 6.73 | 6.03 | 0.769 | 0.747 | 0.867 | 6.37 | -6.28 | -4.7 | 0.848 | 0.814 | 0.841 | -6.38 | 5.39 | -6.69 | Critical_Mixed | 394.3 | 669.6 | 1.204 | 0.89 | 8.52 | 0.899 | 6.73 | 0.1694 | 0.6261 | 0.2481 | 0.1477 | 0.85 | 0.2038 | 0.2641 | 0.3617 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
748 | 199.2 | 142.3 | 67 | 55 | 1 | 385.6 | 2530.6 | 58.7 | 22.6 | 75.5 | 77.2 | 70 | 82.2 | 35.2 | 13.9 | 10000 | 10000 | 10000 | 18912.4 | 20000 | 20000 | 1.891 | 2 | 2 | 0.507 | 0.531 | 0.5 | 2.53 | -2.09 | 2 | 0.5 | 0.52 | 0.562 | -2.28 | 2.1 | -2.42 | 0.52 | 0.525 | 0.5 | -2 | 2.2 | 2.43 | 0.508 | 0.536 | 0.53 | 2.07 | 2 | -2 | Good_Mixed | 10000 | 18912.4 | 1.891 | 0.531 | 2.53 | 0.562 | 2.43 | 0.9618 | 0.915 | 0.9467 | 0.9219 | 1 | 0.9337 | 0.8789 | 0.9399 | 0.9399 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
749 | 1124.2 | 547.6 | 106.3 | 125.7 | 18.8 | 932 | 5716.6 | 58.4 | 20.4 | 82.9 | 82.7 | 77.2 | 90.4 | 37.2 | 12.1 | 7642.7 | 9006.7 | 8615.1 | 13673.4 | 17228.3 | 16275.5 | 1.789 | 1.913 | 1.889 | 0.529 | 0.555 | 0.545 | 2.85 | 2.52 | 3.42 | 0.559 | 0.546 | 0.516 | -2.96 | 2.34 | 2.92 | 0.598 | 0.57 | 0.51 | 2.01 | 2.5 | 2.73 | 0.532 | 0.582 | 0.512 | 2.91 | -2 | -2.73 | Poor_DGA | 7642.7 | 13673.4 | 1.789 | 0.555 | 3.42 | 0.598 | 2.96 | 0.3847 | 0.9748 | 0.712 | 0.964 | 1 | 0.8043 | 0.7861 | 0.7466 | 0.7466 | Fair | 1 | 1 | DGA | 0 |  | C2H2
750 | 1070.7 | 597.1 | 116 | 133.1 | 21.6 | 819.4 | 5228.5 | 45.4 | 37.2 | 92.6 | 88.3 | 83 | 99.2 | 40.1 | 25.9 | 5283.9 | 4807.3 | 5267.8 | 7610.8 | 7216 | 8070.8 | 1.44 | 1.501 | 1.532 | 0.794 | 0.761 | 0.726 | 7.39 | 6.2 | 5.59 | 0.626 | 0.71 | 0.732 | 3.14 | -4.77 | 5.14 | 0.726 | 0.667 | 0.698 | 5.6 | 4.93 | 4.52 | 0.687 | 0.621 | 0.573 | -5.47 | 4.36 | 6.54 | Poor_Mixed | 4807.3 | 7216 | 1.44 | 0.794 | 7.39 | 0.732 | 6.54 | 0.3717 | 0.7098 | 0.5039 | 0.5478 | 1 | 0.3599 | 0.4832 | 0.5532 | 0.5532 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
751 | 1517.6 | 881.7 | 139.4 | 173.3 | 34.3 | 1221.3 | 8485.4 | 34.1 | 46.5 | 104.1 | 104.3 | 92.6 | 114.3 | 44.4 | 32.1 | 1116.8 | 1841.7 | 1119.1 | 1231.5 | 2050.8 | 1200 | 1.103 | 1.114 | 1.072 | 0.923 | 0.898 | 0.974 | 8.62 | -8.71 | -9.74 | 0.892 | 0.722 | 0.79 | 8.6 | -7.77 | 7.92 | 0.911 | 0.72 | 0.844 | 7.77 | 7.58 | 7.02 | 0.848 | 0.887 | 0.882 | 6.33 | 7.64 | 7.2 | Very Poor_Mixed | 1116.8 | 1200 | 1.072 | 0.974 | 9.74 | 0.911 | 8.6 | 0.1066 | 0.6156 | 0.1755 | 0.3175 | 1 | 0.0943 | 0.2203 | 0.3468 | 0.3468 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
752 | 1548.3 | 907.7 | 146.4 | 193.6 | 34.3 | 1267.1 | 8029.2 | 32.1 | 49.1 | 103.1 | 100.3 | 91.5 | 111.4 | 43.7 | 33.2 | 2218.6 | 690 | 851.2 | 2550.4 | 1200 | 1200 | 1.15 | 1.739 | 1.41 | 0.95 | 0.927 | 0.948 | 8.8 | 9.08 | -9.26 | 0.92 | 0.848 | 0.864 | 6.81 | -8.65 | 7.21 | 0.845 | 0.747 | 0.804 | 8.52 | -5.93 | 6.76 | 0.805 | 0.733 | 0.759 | 8.5 | 9.37 | 7.13 | Very Poor_Mixed | 690 | 1200 | 1.15 | 0.95 | 9.26 | 0.92 | 9.37 | 0.0802 | 0.5915 | 0.2297 | 0.2748 | 1 | 0.0859 | 0.2338 | 0.3419 | 0.3419 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
753 | 213.9 | 120 | 68.7 | 56.1 | 2 | 423 | 2721.1 | 59 | 22.7 | 77.9 | 75 | 71.2 | 81.6 | 35 | 11.3 | 8661 | 10000 | 10000 | 16663.3 | 20000 | 19877 | 1.924 | 2 | 1.988 | 0.578 | 0.526 | 0.515 | 2.43 | 3.17 | 2.03 | 0.503 | 0.531 | 0.5 | 2 | -2.17 | -2.64 | 0.536 | 0.541 | 0.538 | 2 | 2.67 | -2.21 | 0.5 | 0.529 | 0.519 | -2.03 | 2.72 | 2.28 | Good_Mixed | 8661 | 16663.3 | 1.924 | 0.578 | 3.17 | 0.541 | 2.72 | 0.8871 | 0.9129 | 0.9382 | 0.9802 | 1 | 0.8449 | 0.8727 | 0.9095 | 0.9095 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
754 | 982.2 | 693.5 | 112.9 | 131.3 | 23.3 | 937.1 | 6111.1 | 58.4 | 21.3 | 75.2 | 79.8 | 71.3 | 81.5 | 36 | 16.1 | 8779.4 | 8257.9 | 9531.2 | 16945.5 | 14789.3 | 18087.5 | 1.93 | 1.791 | 1.898 | 0.539 | 0.6 | 0.592 | 2.17 | 3.6 | 2.9 | 0.541 | 0.5 | 0.511 | 2.88 | 2.96 | -2 | 0.563 | 0.545 | 0.539 | 2.03 | -2.4 | 2.27 | 0.518 | 0.551 | 0.531 | 2.97 | 2 | 2.91 | Poor_DGA | 8257.9 | 14789.3 | 1.791 | 0.6 | 3.6 | 0.563 | 2.97 | 0.3387 | 0.9458 | 0.9108 | 0.8635 | 1 | 0.7593 | 0.8251 | 0.7473 | 0.7473 | Fair | 1 | 1 | DGA | 0 |  | C2H2
755 | 907.4 | 538.9 | 106.6 | 125.6 | 18.6 | 932 | 5574.5 | 46 | 35.3 | 91.1 | 88 | 81.2 | 97.9 | 39.7 | 25.7 | 5003.3 | 5408.1 | 5979.1 | 7314.1 | 8478.9 | 9296.4 | 1.462 | 1.568 | 1.555 | 0.751 | 0.715 | 0.722 | 5.83 | 5.52 | 5.24 | 0.657 | 0.683 | 0.707 | -4.53 | -3.83 | 3.85 | 0.697 | 0.755 | 0.715 | 3.97 | 6.22 | 4.46 | 0.616 | 0.645 | 0.574 | 3.9 | 5.07 | 5.13 | Poor_Mixed | 5003.3 | 7314.1 | 1.462 | 0.751 | 5.83 | 0.755 | 6.22 | 0.4049 | 0.731 | 0.5361 | 0.5549 | 1 | 0.433 | 0.4962 | 0.5802 | 0.5802 | Poor | 0 | 1 | DGA | 0 |  | C2H2
756 | 935.2 | 522.1 | 101.2 | 111.4 | 20.2 | 848 | 5851.2 | 48.3 | 34.4 | 90.9 | 89.9 | 81 | 98.1 | 40.3 | 24.3 | 5327.2 | 5806 | 5746.5 | 7827.7 | 9031.7 | 8706 | 1.469 | 1.556 | 1.515 | 0.744 | 0.736 | 0.693 | -5.22 | 5.28 | 5.8 | 0.691 | 0.701 | 0.69 | 4.65 | -3.79 | 4.34 | 0.671 | 0.684 | 0.694 | 4.49 | 5.58 | -3.54 | 0.687 | 0.627 | 0.635 | 4.73 | 5.65 | 3.84 | Poor_Mixed | 5327.2 | 7827.7 | 1.469 | 0.744 | 5.8 | 0.701 | 5.65 | 0.4201 | 0.7414 | 0.5211 | 0.6039 | 1 | 0.4431 | 0.4894 | 0.5864 | 0.5864 | Poor | 0 | 1 | DGA | 0 |  | C2H2
757 | 265.6 | 132 | 78.3 | 64.6 | 1.3 | 384.3 | 2523.9 | 47.2 | 35.8 | 79.2 | 76.4 | 73.5 | 87.1 | 36.5 | 15.5 | 7750.8 | 6898.6 | 7591.1 | 13357.5 | 12100.9 | 13138.3 | 1.723 | 1.754 | 1.731 | 0.59 | 0.563 | 0.57 | 3.52 | 3.18 | 2.52 | 0.581 | 0.529 | 0.568 | 3.6 | -3.18 | -3.35 | 0.564 | 0.555 | 0.555 | 2.43 | 3.2 | 3.12 | 0.618 | 0.563 | 0.568 | -2.14 | 2 | 2.48 | Poor_Oil | 6898.6 | 12100.9 | 1.723 | 0.59 | 3.52 | 0.618 | 3.6 | 0.8968 | 0.7253 | 0.849 | 0.88 | 1 | 0.7465 | 0.7252 | 0.8352 | 0.8352 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
758 | 631.9 | 371.1 | 85.6 | 97.4 | 4.2 | 539.6 | 4735.8 | 50.4 | 28.6 | 82.8 | 129.6 | 75.6 | 89.5 | 38.4 | 15 | 8728.6 | 8167.5 | 9861.8 | 16338.1 | 15087.8 | 19723.6 | 1.872 | 1.847 | 2 | 0.659 | 0.602 | 0.641 | 3.94 | 4.07 | 3.43 | 0.695 | 0.552 | 0.602 | 2.93 | 3.83 | 3.56 | 0.545 | 0.53 | 0.516 | -2.51 | 3.64 | 3.48 | 0.538 | 0.988 | 0.5 | 3.08 | -9.62 | 2.95 | Critical_Bushing_TD_Cap | 8167.5 | 15087.8 | 1.847 | 0.659 | 4.07 | 0.988 | 9.62 | 0.6766 | 0.815 | 0.5523 | 0.8935 | 1 | 0.6266 | 0.6625 | 0.7338 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | C2H2
759 | 504.5 | 357.9 | 91.2 | 90.7 | 5.9 | 565 | 3731.6 | 53.5 | 29.1 | 81.7 | 85.2 | 75.2 | 87.5 | 37.3 | 16.7 | 8769.6 | 7534.1 | 7425.2 | 15940.3 | 13263.4 | 12886.1 | 1.818 | 1.76 | 1.735 | 0.634 | 0.674 | 0.587 | 4.53 | -4.49 | 3.81 | 0.576 | 0.549 | 0.551 | -3.64 | -3.18 | 3.11 | 0.62 | 0.578 | 0.552 | 2.99 | 3.34 | 2.91 | 0.512 | 0.552 | 0.511 | 2.96 | 3.01 | -3.45 | Fair_Mixed | 7425.2 | 12886.1 | 1.735 | 0.674 | 4.53 | 0.62 | 3.64 | 0.674 | 0.8081 | 0.7312 | 0.8465 | 1 | 0.6023 | 0.7362 | 0.7578 | 0.7578 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
760 | 355.4 | 157.6 | 72.1 | 66.6 | 1.8 | 495.2 | 3031.2 | 49.7 | 31 | 75 | 76.1 | 71.3 | 81.1 | 35 | 12.4 | 8202.3 | 7659.9 | 7974.1 | 14689.7 | 13307 | 13557.6 | 1.791 | 1.737 | 1.7 | 0.594 | 0.585 | 0.543 | 4.56 | 3.01 | 2.98 | 0.508 | 0.525 | 0.626 | 2.19 | -2.6 | 2 | 0.502 | 0.546 | 0.5 | 2.84 | 2 | 2 | 0.566 | 0.549 | 0.505 | 3.31 | 2.81 | 2 | Fair_Oil | 7659.9 | 13307 | 1.7 | 0.594 | 4.56 | 0.626 | 3.31 | 0.8427 | 0.7829 | 0.9596 | 0.9575 | 1 | 0.7205 | 0.838 | 0.8602 | 0.8602 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
761 | 857.7 | 504.3 | 101.1 | 112.2 | 20.3 | 828 | 5196.4 | 47 | 35 | 89.9 | 88.7 | 81.2 | 96.8 | 39.3 | 24.3 | 6436.7 | 6681.7 | 5772.7 | 10200.2 | 10765.2 | 8684.8 | 1.585 | 1.611 | 1.504 | 0.689 | 0.684 | 0.706 | -5.53 | 5.04 | 5.6 | 0.67 | 0.675 | 0.656 | 5.23 | 4.16 | -4.74 | 0.634 | 0.677 | 0.617 | 4.66 | 4.51 | 4.03 | 0.713 | 0.652 | 0.662 | 5.28 | 4.77 | 4.44 | Poor_Mixed | 5772.7 | 8684.8 | 1.504 | 0.706 | 5.6 | 0.713 | 5.28 | 0.4362 | 0.7345 | 0.5473 | 0.6039 | 1 | 0.4738 | 0.5013 | 0.5987 | 0.5987 | Poor | 0 | 1 | DGA | 0 |  | C2H2
762 | 972.4 | 519.8 | 110.3 | 124.5 | 19.1 | 944.8 | 6268.1 | 46.8 | 34 | 90.4 | 87.9 | 81.4 | 95.2 | 38.4 | 25.6 | 4581.3 | 4603.2 | 5196.2 | 6456.6 | 6507.4 | 8681 | 1.409 | 1.414 | 1.671 | 0.768 | 0.682 | 0.682 | 6.95 | 4.85 | 5.54 | 0.642 | 0.732 | 0.691 | 5.35 | 4.51 | -5.57 | 0.686 | 0.653 | 0.678 | 4.64 | 4.16 | -4 | 0.677 | 0.642 | 0.662 | 4.91 | 4.48 | 4.7 | Poor_Mixed | 4581.3 | 6456.6 | 1.409 | 0.768 | 6.95 | 0.732 | 5.57 | 0.3882 | 0.7461 | 0.5616 | 0.5584 | 1 | 0.4377 | 0.4842 | 0.5791 | 0.5791 | Poor | 0 | 1 | DGA | 0 |  | C2H2
763 | 193.4 | 120 | 65 | 65.7 | 1 | 377.1 | 2500 | 59.4 | 20.6 | 83.6 | 79.2 | 74.3 | 87.3 | 37 | 13.7 | 9798.3 | 9429.2 | 9392.3 | 19596.5 | 18858.3 | 18784.6 | 2 | 2 | 2 | 0.503 | 0.507 | 0.543 | -2 | 2 | -2 | 0.5 | 0.549 | 0.567 | 2 | -2.55 | 2.08 | 0.563 | 0.53 | 0.5 | 2.4 | 2 | 2.69 | 0.522 | 0.526 | 0.537 | 2.74 | -2 | 2 | Fair_Thermal | 9392.3 | 18784.6 | 2 | 0.543 | 2 | 0.567 | 2.74 | 0.9512 | 0.9672 | 0.7741 | 0.9269 | 1 | 0.9369 | 0.8459 | 0.921 | 0.921 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_HV
764 | 1618.3 | 865.5 | 137.5 | 189.2 | 34.3 | 1282.9 | 8338.8 | 35.6 | 46.3 | 107 | 108.5 | 96.7 | 119.2 | 44.9 | 33.6 | 1156.7 | 978.9 | 690 | 1214.6 | 1200 | 1200 | 1.05 | 1.226 | 1.739 | 0.958 | 0.977 | 0.966 | 9.05 | 9.25 | 9.84 | 0.81 | 0.734 | 0.889 | 7.57 | 8.58 | -6.52 | 0.882 | 0.829 | 0.758 | 6.22 | 6.07 | -8.06 | 0.869 | 0.856 | 0.842 | 8.17 | 5.05 | -7.65 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.977 | 9.84 | 0.889 | 8.58 | 0.0847 | 0.6175 | 0.0854 | 0.2591 | 1 | 0.0523 | 0.2365 | 0.3267 | 0.3267 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
765 | 1341.1 | 827.4 | 128.5 | 164.8 | 27.5 | 1135.4 | 7460 | 36.1 | 43.1 | 103 | 107.8 | 91.9 | 111.5 | 43.5 | 33.3 | 3926.9 | 2602.5 | 2768.6 | 5083.4 | 3306.9 | 3270 | 1.295 | 1.271 | 1.181 | 0.897 | 0.852 | 1.029 | 8.67 | 7.83 | 7.2 | 0.81 | 0.839 | 0.853 | 5.54 | -5.76 | 6.56 | 0.735 | 0.809 | 0.785 | -6.48 | 5.93 | 6.22 | 0.648 | 0.833 | 0.737 | 3.93 | 6.94 | 7.34 | Critical_Mixed | 2602.5 | 3270 | 1.181 | 1.029 | 8.67 | 0.853 | 7.34 | 0.1949 | 0.6484 | 0.1868 | 0.2709 | 1 | 0.1631 | 0.3173 | 0.3987 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
766 | 983.2 | 528.8 | 107.1 | 116.8 | 16.2 | 804 | 5287.1 | 47.2 | 33.2 | 90.1 | 89.6 | 82 | 95.1 | 40.3 | 27.3 | 5414.4 | 5180.4 | 4877.7 | 8635.6 | 7677.6 | 7207.5 | 1.595 | 1.482 | 1.478 | 0.798 | 0.716 | 0.751 | -6.23 | 5.01 | 5.68 | 0.667 | 0.719 | 0.729 | 6.32 | 6.46 | 5.76 | 0.664 | 0.802 | 0.641 | 5.45 | 6.57 | 3.73 | 0.691 | 0.663 | 0.677 | 5.31 | 4.16 | 5.56 | Poor_Mixed | 4877.7 | 7207.5 | 1.478 | 0.798 | 6.23 | 0.802 | 6.57 | 0.4422 | 0.7556 | 0.5369 | 0.4975 | 1 | 0.4056 | 0.4327 | 0.5745 | 0.5745 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
767 | 1195.8 | 620.3 | 112.7 | 144.4 | 22 | 957.1 | 6513.9 | 58.5 | 23.7 | 80.2 | 82.2 | 73.7 | 86.4 | 36.8 | 11.7 | 8667 | 9172.5 | 8814 | 16125 | 17626.5 | 16092 | 1.861 | 1.922 | 1.826 | 0.555 | 0.593 | 0.59 | 2.96 | -2.86 | 3.71 | 0.577 | 0.552 | 0.524 | 2.42 | 2.81 | 3.89 | 0.571 | 0.5 | 0.602 | 2.9 | 2.08 | -2.89 | 0.529 | 0.539 | 0.613 | -3.86 | 3.44 | 2.9 | Poor_DGA | 8667 | 16092 | 1.826 | 0.593 | 3.71 | 0.613 | 3.89 | 0.3189 | 0.8931 | 0.7865 | 0.9724 | 1 | 0.7331 | 0.7504 | 0.7119 | 0.7119 | Fair | 1 | 1 | DGA | 0 |  | C2H2
768 | 1038.2 | 589.7 | 111.1 | 132.3 | 15.6 | 918 | 5590.6 | 44 | 34.4 | 95.8 | 91 | 82.6 | 97.5 | 41.2 | 25.7 | 5595.5 | 5386.7 | 5537.4 | 8252.1 | 7774.5 | 8489.6 | 1.475 | 1.443 | 1.533 | 0.766 | 0.807 | 0.753 | 5.92 | 6.44 | -5.55 | 0.658 | 0.708 | 0.635 | 5.12 | 2.85 | 5.42 | 0.662 | 0.634 | 0.615 | 5.37 | 4.52 | -5.09 | 0.673 | 0.609 | 0.636 | -4.31 | 5.04 | 4.91 | Poor_Mixed | 5386.7 | 7774.5 | 1.443 | 0.807 | 6.44 | 0.708 | 5.42 | 0.4002 | 0.7414 | 0.4697 | 0.5549 | 1 | 0.37 | 0.5174 | 0.5687 | 0.5687 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
769 | 1564.3 | 881.5 | 131 | 185.6 | 29.1 | 1181.9 | 7757.3 | 36.5 | 45 | 105.9 | 104.8 | 91.4 | 111.6 | 44.4 | 32.3 | 3131.4 | 1284.9 | 2326.5 | 3749.7 | 1462 | 2674.2 | 1.197 | 1.138 | 1.149 | 0.915 | 0.894 | 0.862 | 8.68 | -8.59 | 8.04 | 0.836 | 0.78 | 0.716 | 6.56 | 6.5 | 6.96 | 0.884 | 0.789 | 0.805 | 5.3 | -7.91 | 6.73 | 0.75 | 0.786 | 0.887 | -7.05 | -6.12 | 5.31 | Very Poor_Mixed | 1284.9 | 1462 | 1.138 | 0.915 | 8.68 | 0.887 | 7.91 | 0.1369 | 0.6299 | 0.183 | 0.3098 | 1 | 0.1525 | 0.2814 | 0.3756 | 0.3756 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
770 | 413.1 | 227.8 | 80.4 | 82.3 | 7.1 | 562.5 | 4099.8 | 54.8 | 26.9 | 85.3 | 85.9 | 77.7 | 93.5 | 38.5 | 18.7 | 7190 | 7791.9 | 8246.8 | 12423 | 14183 | 13984 | 1.728 | 1.82 | 1.696 | 0.573 | 0.622 | 0.65 | 3.84 | 4.26 | 3.7 | 0.572 | 0.593 | 0.605 | -4.23 | 4.11 | -3.98 | 0.597 | 0.574 | 0.566 | 3.74 | 3.28 | 5.03 | 0.614 | 0.554 | 0.572 | -3.07 | 4.1 | -4.03 | Fair_Mixed | 7190 | 12423 | 1.696 | 0.65 | 4.26 | 0.614 | 5.03 | 0.6975 | 0.8397 | 0.6436 | 0.7872 | 1 | 0.6417 | 0.6445 | 0.7447 | 0.7447 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
771 | 111.1 | 152 | 65 | 50 | 3.3 | 418.4 | 2500 | 58.8 | 22.7 | 75 | 75 | 71.2 | 80 | 35.2 | 10.6 | 9305.4 | 8862.2 | 10000 | 17247 | 17724.4 | 20000 | 1.853 | 2 | 2 | 0.542 | 0.519 | 0.586 | 3.26 | -2.43 | 3.03 | 0.518 | 0.512 | 0.505 | 2.02 | 2.34 | 2 | 0.5 | 0.5 | 0.5 | 2.3 | -2 | -2.63 | 0.5 | 0.515 | 0.514 | 2 | 2 | 2.25 | Good_Mixed | 8862.2 | 17247 | 1.853 | 0.586 | 3.26 | 0.518 | 2.63 | 0.8828 | 0.9129 | 0.9842 | 0.9925 | 1 | 0.8002 | 0.9373 | 0.919 | 0.919 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
772 | 155.1 | 120 | 65.1 | 59 | 1 | 407.4 | 2806.7 | 60 | 20 | 75 | 75 | 70.2 | 81.3 | 36.2 | 10 | 9541.5 | 7861.8 | 9233.3 | 18192.1 | 13953.2 | 18466.7 | 1.907 | 1.775 | 2 | 0.529 | 0.5 | 0.507 | 2.69 | 2.14 | 2.48 | 0.541 | 0.533 | 0.539 | -2 | 2.05 | -2.96 | 0.546 | 0.551 | 0.503 | 2.67 | 2.85 | 2.14 | 0.586 | 0.57 | 0.5 | -2.11 | -2.27 | -2 | Good_Mixed | 7861.8 | 13953.2 | 1.775 | 0.529 | 2.69 | 0.586 | 2.96 | 0.9582 | 1 | 0.985 | 1 | 1 | 0.9155 | 0.8187 | 0.9436 | 0.9436 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_TV_R_TanDelta_pct
773 | 183 | 127.9 | 68.5 | 60.9 | 2.2 | 432.2 | 2500 | 58.5 | 23.1 | 75 | 79.1 | 71.7 | 80.4 | 35 | 15 | 10000 | 9580.4 | 9446.2 | 19443 | 17609.1 | 18540.9 | 1.944 | 1.838 | 1.963 | 0.535 | 0.541 | 0.589 | 2.27 | 2 | 3.39 | 0.548 | 0.58 | 0.557 | 2.75 | 2.42 | 2.28 | 0.56 | 0.543 | 0.546 | -2.72 | -2.87 | 2.36 | 0.538 | 0.54 | 0.512 | 2 | -2.82 | 2.44 | Good_Mixed | 9446.2 | 17609.1 | 1.838 | 0.589 | 3.39 | 0.58 | 2.87 | 0.8749 | 0.9047 | 0.9278 | 0.8935 | 1 | 0.8169 | 0.7806 | 0.8796 | 0.8796 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
774 | 168.1 | 210.9 | 72.3 | 68.6 | 1.5 | 475.3 | 2807.1 | 59.2 | 21 | 76.5 | 77.6 | 70.6 | 82.1 | 36 | 11.1 | 6605.9 | 6967.1 | 6205.9 | 10392.9 | 11942.9 | 10119.4 | 1.573 | 1.714 | 1.631 | 0.539 | 0.555 | 0.5 | 2.72 | 3.18 | 2.95 | 0.558 | 0.547 | 0.507 | 2.35 | 2.93 | 2.16 | 0.532 | 0.536 | 0.548 | -2.05 | 2 | -3 | 0.575 | 0.552 | 0.543 | 2.44 | 3.38 | 2.01 | Fair_IR_PI | 6205.9 | 10119.4 | 1.573 | 0.555 | 3.18 | 0.575 | 3.38 | 0.8678 | 0.9543 | 0.9178 | 0.984 | 1 | 0.8382 | 0.7921 | 0.8924 | 0.8924 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
775 | 896.2 | 546.4 | 111.3 | 128.3 | 18.9 | 853.6 | 5232.3 | 48.4 | 31.2 | 89 | 86.5 | 82.8 | 99.1 | 40.5 | 25.6 | 6015.7 | 5143 | 6693.8 | 9551 | 8088.1 | 10626.9 | 1.588 | 1.573 | 1.588 | 0.701 | 0.712 | 0.719 | -5.78 | -5.4 | 6.88 | 0.759 | 0.724 | 0.672 | 3.58 | -5.39 | 5.93 | 0.738 | 0.703 | 0.634 | 3.53 | 3.86 | 5.92 | 0.707 | 0.659 | 0.687 | 5.31 | 5.76 | 4.4 | Poor_Mixed | 5143 | 8088.1 | 1.573 | 0.719 | 6.88 | 0.759 | 5.93 | 0.4102 | 0.7804 | 0.5391 | 0.5584 | 1 | 0.4228 | 0.451 | 0.5784 | 0.5784 | Poor | 0 | 1 | DGA | 0 |  | C2H2
776 | 855.9 | 437.2 | 108.5 | 113.9 | 13.8 | 789.7 | 5369 | 47.3 | 33.7 | 90.7 | 91.8 | 82.7 | 99.2 | 39.4 | 22.2 | 5643.5 | 5652.6 | 5912.6 | 9110.7 | 8790.5 | 9023.7 | 1.614 | 1.555 | 1.526 | 0.682 | 0.711 | 0.717 | 5.07 | 5.16 | -5.6 | 0.619 | 0.704 | 0.728 | -5.41 | -4.48 | 6.07 | 0.593 | 0.633 | 0.691 | 3.44 | 4.37 | -3.7 | 0.69 | 0.723 | 0.619 | -4.72 | -4.07 | 3.95 | Poor_Mixed | 5643.5 | 8790.5 | 1.526 | 0.717 | 5.6 | 0.728 | 6.07 | 0.4818 | 0.7497 | 0.4993 | 0.6753 | 1 | 0.4706 | 0.5054 | 0.611 | 0.611 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
777 | 657.8 | 363.5 | 87.2 | 95.4 | 3.9 | 664.6 | 4386.3 | 28.1 | 24.9 | 76.3 | 79.6 | 74.6 | 82.9 | 36.2 | 19.9 | 8249.7 | 8255.6 | 8197.4 | 14619.3 | 15046.6 | 14146.3 | 1.772 | 1.823 | 1.726 | 0.55 | 0.594 | 0.593 | 2.9 | 3.01 | 3.71 | 0.578 | 0.533 | 0.596 | 3.24 | -3.26 | 2.38 | 0.5 | 0.639 | 0.962 | 2.44 | -3.72 | -9.28 | 0.589 | 0.583 | 0.571 | 2.39 | -4.21 | 4.17 | Critical_Bushing_TD_Cap | 8197.4 | 14146.3 | 1.726 | 0.594 | 3.71 | 0.962 | 9.28 | 0.6666 | 0.2883 | 0.8603 | 0.7499 | 1 | 0.732 | 0.636 | 0.7018 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
778 | 335.9 | 238.2 | 78.6 | 72.8 | 2 | 527.6 | 3444.7 | 57.4 | 21.2 | 80.6 | 77.5 | 73.9 | 86.4 | 37.4 | 11.9 | 6974.3 | 6295.3 | 6436.5 | 11470.9 | 10096.8 | 10573.9 | 1.645 | 1.604 | 1.643 | 0.591 | 0.633 | 0.603 | -3.29 | -3.47 | 3.24 | 0.505 | 0.542 | 0.558 | -2.43 | 3.25 | 2.85 | 0.524 | 0.549 | 0.523 | 2.65 | 2.13 | 2.04 | 0.509 | 0.524 | 0.581 | 2.62 | 2.47 | 2.5 | Poor_IR_PI | 6295.3 | 10096.8 | 1.604 | 0.633 | 3.47 | 0.581 | 3.25 | 0.8087 | 0.9486 | 0.82 | 0.9682 | 1 | 0.6847 | 0.8139 | 0.8488 | 0.8488 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
779 | 1491.9 | 859.2 | 138.5 | 174.4 | 34.3 | 1273.3 | 8353 | 31.4 | 47.7 | 105.9 | 107.6 | 94.1 | 114.7 | 44.7 | 32.9 | 1530.3 | 2833.6 | 2306.9 | 1642.3 | 3397 | 2709.5 | 1.073 | 1.199 | 1.175 | 0.896 | 0.86 | 0.949 | -7.97 | -8.68 | 8.88 | 0.762 | 0.752 | 0.833 | 5.4 | 7.45 | 6.79 | 0.713 | 0.821 | 0.728 | 6.38 | 5.13 | 6.05 | 0.873 | 0.747 | 0.743 | 6.3 | -4.77 | 7.52 | Very Poor_Mixed | 1530.3 | 1642.3 | 1.073 | 0.949 | 8.88 | 0.873 | 7.52 | 0.1068 | 0.6044 | 0.1346 | 0.2865 | 1 | 0.1411 | 0.3201 | 0.3644 | 0.3644 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
780 | 1022.3 | 506.2 | 109.7 | 129.6 | 21.7 | 870.5 | 5516.8 | 56 | 23 | 78.4 | 77.4 | 72.7 | 83.3 | 35.7 | 12.4 | 8399.2 | 9522.7 | 8049.1 | 16172.1 | 18079.1 | 15079.9 | 1.925 | 1.899 | 1.873 | 0.543 | 0.532 | 0.5 | 2 | 3.22 | 2 | 0.508 | 0.556 | 0.5 | 2.4 | 2.39 | 2.43 | 0.522 | 0.525 | 0.5 | 2 | -2 | 2 | 0.5 | 0.566 | 0.512 | 2.68 | 2 | -2 | Poor_DGA | 8049.1 | 15079.9 | 1.873 | 0.543 | 3.22 | 0.566 | 2.68 | 0.3837 | 0.9067 | 0.8748 | 0.9575 | 1 | 0.8934 | 0.8903 | 0.7854 | 0.7854 | Fair | 1 | 1 | DGA | 0 |  | C2H2
781 | 594.4 | 294.8 | 84.5 | 83.3 | 11.2 | 545.6 | 4348.1 | 54.2 | 25.8 | 82.1 | 80.4 | 75.1 | 86.8 | 37 | 15.8 | 8563.7 | 8658.5 | 8859.7 | 16097.1 | 15631.9 | 17016.2 | 1.88 | 1.805 | 1.921 | 0.62 | 0.589 | 0.621 | 3.8 | -3.98 | -3.6 | 0.578 | 0.549 | 0.599 | 3.34 | 2.79 | 3.6 | 0.561 | 0.604 | 0.549 | 3.74 | -2.88 | 4 | 0.601 | 0.535 | 0.59 | 3.87 | 3.58 | 3.03 | Fair_Mixed | 8563.7 | 15631.9 | 1.805 | 0.621 | 3.98 | 0.604 | 4 | 0.632 | 0.8568 | 0.7715 | 0.8718 | 1 | 0.6543 | 0.684 | 0.7563 | 0.7563 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
782 | 103.1 | 120 | 65.6 | 50 | 1.5 | 367.9 | 2500 | 60 | 21.4 | 75 | 77.9 | 70 | 80.4 | 36 | 10 | 9729.1 | 9718.9 | 9244.5 | 19183.4 | 18984 | 17576.2 | 1.972 | 1.953 | 1.901 | 0.505 | 0.506 | 0.54 | 2.59 | -2.38 | 2.4 | 0.574 | 0.539 | 0.612 | 2.13 | -3.29 | 2.68 | 0.557 | 0.526 | 0.535 | 2.37 | -3.12 | 2.12 | 0.564 | 0.523 | 0.55 | 2.9 | 2.86 | 2.76 | Good_Mixed | 9244.5 | 17576.2 | 1.901 | 0.54 | 2.59 | 0.612 | 3.29 | 0.9458 | 0.9432 | 0.9555 | 1 | 1 | 0.8963 | 0.7603 | 0.9175 | 0.9175 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
783 | 446.9 | 327.8 | 85.4 | 155.2 | 2.7 | 577.5 | 3643.7 | 55.1 | 88 | 109.3 | 109.3 | 93.8 | 119.2 | 45.6 | 12.4 | 7853.5 | 8096.1 | 7791.1 | 13740.4 | 14848.3 | 14482.7 | 1.75 | 1.834 | 1.859 | 0.608 | 0.569 | 0.6 | 3.41 | 3.19 | -3.32 | 0.57 | 0.548 | 0.549 | 2.86 | 2.7 | 3.26 | 0.511 | 0.54 | 0.57 | 3.2 | 2.54 | -3.21 | 0.534 | 0.525 | 0.535 | 3.4 | 2.47 | 3.05 | Critical_Thermal | 7791.1 | 13740.4 | 1.75 | 0.608 | 3.41 | 0.57 | 3.4 | 0.6735 | 0.5833 | 0.0794 | 0.9575 | 1 | 0.7069 | 0.7697 | 0.6917 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
784 | 230.5 | 188.2 | 81.6 | 66 | 3.5 | 463 | 3294.7 | 59.5 | 22 | 81.1 | 79.3 | 70.8 | 86.2 | 36.7 | 13 | 7604.6 | 10000 | 8968.8 | 13865.4 | 19284.8 | 17004.1 | 1.823 | 1.928 | 1.896 | 0.775 | 0.749 | 0.782 | 6.45 | 5.74 | 5.84 | 0.514 | 0.51 | 0.57 | 2.41 | 2 | 2 | 0.519 | 0.533 | 0.5 | 2.68 | 2.56 | 2.17 | 0.532 | 0.541 | 0.5 | 2.96 | 2.58 | 2.22 | Poor_Winding_TD_Cap | 7604.6 | 13865.4 | 1.823 | 0.782 | 6.45 | 0.57 | 2.96 | 0.8101 | 0.9283 | 0.8313 | 0.9438 | 1 | 0.3731 | 0.8613 | 0.8115 | 0.8115 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
785 | 100 | 150.4 | 65 | 50 | 1 | 406.1 | 2500 | 59.8 | 20.4 | 75.4 | 75 | 70 | 80 | 35.4 | 10.9 | 9240.5 | 9325.4 | 10000 | 17959.5 | 18650.8 | 19328.6 | 1.944 | 2 | 1.933 | 0.575 | 0.5 | 0.503 | 3.14 | -2.18 | 2.21 | 0.531 | 0.511 | 0.527 | 2.11 | 2.32 | 2.36 | 0.517 | 0.502 | 0.5 | 2.08 | 2.03 | 2 | 0.505 | 0.5 | 0.501 | -2 | 2.03 | -2.22 | Good_Mixed | 9240.5 | 17959.5 | 1.933 | 0.575 | 3.14 | 0.531 | 2.36 | 0.9825 | 0.9748 | 0.99 | 0.9875 | 1 | 0.8918 | 0.9235 | 0.9621 | 0.9621 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
786 | 388 | 253.8 | 82.3 | 92.6 | 3.5 | 534.2 | 4398.3 | 28.2 | 25.5 | 80.5 | 84.4 | 76.1 | 88.1 | 37 | 13.6 | 7730.5 | 6968.6 | 7473.9 | 13529 | 12485.9 | 13261.2 | 1.75 | 1.792 | 1.774 | 0.544 | 0.565 | 0.573 | 2.59 | 2.38 | 3.54 | 0.582 | 0.606 | 0.562 | -2.83 | -3.24 | -3.24 | 0.58 | 0.594 | 0.557 | 3.64 | -2.99 | 2.75 | 0.542 | 0.537 | 0.985 | 4.11 | 2.82 | 9.5 | Critical_Bushing_TD_Cap | 6968.6 | 12485.9 | 1.75 | 0.573 | 3.54 | 0.985 | 9.5 | 0.7343 | 0.2783 | 0.739 | 0.9294 | 1 | 0.783 | 0.6258 | 0.7196 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
787 | 370.8 | 178.6 | 76.9 | 69.8 | 2.6 | 485.1 | 3452.9 | 49.8 | 31.4 | 80.1 | 80.5 | 72.4 | 86.1 | 36.7 | 10 | 8139.7 | 7283.2 | 8348.3 | 15049.9 | 12970.2 | 14937.8 | 1.849 | 1.781 | 1.789 | 0.573 | 0.592 | 0.5 | 2.94 | 3.8 | 2.42 | 0.544 | 0.518 | 0.5 | 3.43 | -2.01 | 2.04 | 0.59 | 0.5 | 0.5 | 2.56 | 2.05 | -3.2 | 0.527 | 0.518 | 0.503 | 2.73 | 2.8 | 2.74 | Fair_Oil | 7283.2 | 12970.2 | 1.781 | 0.592 | 3.8 | 0.59 | 3.43 | 0.8087 | 0.7778 | 0.8143 | 1 | 1 | 0.7978 | 0.8679 | 0.8549 | 0.8549 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
788 | 797.3 | 527.3 | 108.4 | 124.1 | 18.4 | 889.7 | 5450.7 | 47.2 | 33 | 90.5 | 90.1 | 83.2 | 99.6 | 40.1 | 26.1 | 4573.1 | 5456.7 | 5366.8 | 6585.9 | 8276.1 | 7822.4 | 1.44 | 1.517 | 1.458 | 0.707 | 0.72 | 0.71 | 5.37 | 4.88 | 4.86 | 0.66 | 0.645 | 0.709 | 6.01 | 4.14 | 5.02 | 0.719 | 0.65 | 0.735 | 3.86 | 5.34 | 5.91 | 0.711 | 0.69 | 0.703 | 4.14 | 3.83 | 5.03 | Poor_Mixed | 4573.1 | 6585.9 | 1.44 | 0.72 | 5.37 | 0.735 | 6.01 | 0.4227 | 0.7581 | 0.5021 | 0.5407 | 1 | 0.4759 | 0.4596 | 0.5832 | 0.5832 | Poor | 0 | 1 | DGA | 0 |  | C2H2
789 | 736.2 | 505.9 | 100.2 | 110.2 | 17.6 | 754 | 5201.2 | 46.2 | 32.9 | 90 | 91.4 | 81 | 96.9 | 40.6 | 25.6 | 5333.3 | 4760.7 | 5740.6 | 8055.7 | 7089.5 | 8215.5 | 1.51 | 1.489 | 1.431 | 0.742 | 0.786 | 0.808 | -6.16 | -6.86 | 5.9 | 0.677 | 0.705 | 0.602 | 5.01 | 5.17 | 4 | 0.753 | 0.621 | 0.621 | 5.87 | -4.4 | -4.23 | 0.696 | 0.635 | 0.677 | 4.56 | -4.55 | -4.37 | Poor_Mixed | 4760.7 | 7089.5 | 1.431 | 0.808 | 6.86 | 0.753 | 5.87 | 0.474 | 0.7593 | 0.5212 | 0.5584 | 1 | 0.3491 | 0.4981 | 0.5882 | 0.5882 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
790 | 811.9 | 471.7 | 99.6 | 114.4 | 18.6 | 780.9 | 5001.6 | 49.2 | 33 | 88.6 | 89.3 | 83.2 | 98.2 | 39.7 | 24 | 6692.9 | 5854.1 | 6076.3 | 11218.7 | 9096.2 | 9758.1 | 1.676 | 1.554 | 1.606 | 0.739 | 0.728 | 0.7 | -5.3 | 6.35 | 5.5 | 0.631 | 0.673 | 0.746 | -4.41 | 4.3 | 4.1 | 0.677 | 0.699 | 0.653 | 4.66 | -5.86 | -5.07 | 0.678 | 0.633 | 0.684 | 5.78 | 5.22 | 5.22 | Poor_Mixed | 5854.1 | 9096.2 | 1.554 | 0.739 | 6.35 | 0.746 | 5.86 | 0.4604 | 0.7581 | 0.5297 | 0.6143 | 1 | 0.429 | 0.474 | 0.5951 | 0.5951 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
791 | 344 | 228.4 | 73.6 | 74.6 | 3.5 | 470.3 | 4008.5 | 58.1 | 21.7 | 75.7 | 75.1 | 70.9 | 80.8 | 35 | 12.3 | 9827.5 | 8298.2 | 9428.8 | 19180.9 | 15697.1 | 18819.9 | 1.952 | 1.892 | 1.996 | 0.535 | 0.557 | 0.543 | 2 | 3.24 | -2.73 | 0.5 | 0.534 | 0.519 | 2.01 | 2.49 | -2.43 | 0.505 | 0.5 | 0.547 | -2.06 | 2.29 | 2 | 0.5 | 0.552 | 0.542 | 2.13 | 2 | -2 | Good_Mixed | 8298.2 | 15697.1 | 1.892 | 0.557 | 3.24 | 0.552 | 2.49 | 0.7811 | 0.9355 | 0.9675 | 0.9597 | 1 | 0.8223 | 0.8885 | 0.8873 | 0.8873 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
792 | 228.5 | 177.1 | 71.5 | 65.3 | 2.2 | 395.2 | 2612.6 | 56.7 | 21 | 81.4 | 82.7 | 74.2 | 87.2 | 36.9 | 12.6 | 8735.1 | 8743.2 | 9250.7 | 16335 | 16086.6 | 17578.1 | 1.87 | 1.84 | 1.9 | 0.571 | 0.5 | 0.509 | 3.07 | 2 | -2.49 | 0.766 | 0.527 | 0.515 | 6.06 | -3.16 | 2.17 | 0.5 | 0.506 | 0.565 | 2.28 | 3.24 | 2.71 | 0.61 | 0.513 | 0.532 | -2.43 | -2.35 | 2.65 | Poor_Bushing_TD_Cap | 8735.1 | 16086.6 | 1.84 | 0.571 | 3.07 | 0.766 | 6.06 | 0.8623 | 0.9543 | 0.7639 | 0.953 | 1 | 0.8862 | 0.7715 | 0.8771 | 0.8771 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
793 | 424.3 | 271.7 | 80.4 | 68 | 3.2 | 509.7 | 2925 | 32.5 | 45.3 | 80.6 | 78.7 | 73 | 86.4 | 35 | 18.9 | 5060.2 | 4961 | 4834.9 | 7400.7 | 3432.9 | 7499.9 | 1.463 | 0.692 | 1.551 | 0.68 | 0.704 | 0.662 | -4.57 | 4.71 | 4.28 | 0.604 | 0.616 | 0.512 | 2.7 | 2.97 | -3.74 | 0.575 | 0.581 | 0.549 | 3.47 | 2.83 | -3.07 | 0.524 | 0.593 | 0.613 | 2.7 | 2.77 | 2.89 | Critical_Oil | 4834.9 | 3432.9 | 0.692 | 0.704 | 4.71 | 0.616 | 3.74 | 0.7799 | 0.627 | 0.8267 | 0.7811 | 0.8187 | 0.5343 | 0.7078 | 0.7251 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
794 | 1381.6 | 801.9 | 128.1 | 167.1 | 26.6 | 1175.3 | 7941 | 35.9 | 44.9 | 103.1 | 105.9 | 94.2 | 112.5 | 43.5 | 29.8 | 2433.4 | 2337.6 | 2289.2 | 2827.2 | 2861 | 2753.2 | 1.162 | 1.224 | 1.203 | 0.91 | 0.927 | 0.861 | -8.65 | 7.32 | 8.3 | 0.811 | 0.765 | 0.751 | 6.48 | -5.67 | 6.75 | 0.876 | 0.744 | 0.837 | 8.13 | -8.52 | 5.62 | 0.755 | 0.852 | 0.716 | 7.27 | 7.04 | 6.28 | Very Poor_Mixed | 2289.2 | 2753.2 | 1.162 | 0.927 | 8.65 | 0.876 | 8.52 | 0.1869 | 0.6309 | 0.1788 | 0.4051 | 1 | 0.1642 | 0.2828 | 0.3945 | 0.3945 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
795 | 124.1 | 220.3 | 69.7 | 67.2 | 1 | 426.5 | 3079.8 | 58.3 | 23.3 | 77.5 | 79 | 73.3 | 82.4 | 36 | 12.7 | 7563.5 | 8188.9 | 6898.1 | 13657 | 14343.5 | 11627.8 | 1.806 | 1.752 | 1.686 | 0.582 | 0.567 | 0.541 | 3.28 | 2.97 | 2.8 | 0.5 | 0.552 | 0.525 | 2.14 | 2 | 2.38 | 0.525 | 0.522 | 0.514 | 2.33 | 2 | 2 | 0.509 | 0.531 | 0.554 | 2.02 | 2 | 2.33 | Fair_IR_PI | 6898.1 | 11627.8 | 1.686 | 0.582 | 3.28 | 0.554 | 2.38 | 0.9301 | 0.9008 | 0.8662 | 0.9507 | 1 | 0.7662 | 0.8649 | 0.8977 | 0.8977 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
796 | 394.8 | 295.9 | 80.9 | 81 | 9.6 | 637.7 | 3891.7 | 51.6 | 29.2 | 86.4 | 86.3 | 78 | 91.6 | 39 | 18.5 | 7028.2 | 7814.1 | 7444.4 | 12713.1 | 14155.8 | 12635.8 | 1.809 | 1.812 | 1.697 | 0.595 | 0.644 | 0.643 | -4.05 | 4.06 | 4.17 | 0.621 | 0.578 | 0.558 | -4.12 | 4.6 | 3.28 | 0.612 | 0.647 | 0.632 | 4.37 | 4.39 | 3.75 | 0.624 | 0.578 | 0.614 | 4.13 | 3.5 | 2.48 | Fair_Mixed | 7028.2 | 12635.8 | 1.697 | 0.644 | 4.17 | 0.647 | 4.6 | 0.6587 | 0.8067 | 0.6372 | 0.7933 | 1 | 0.6167 | 0.611 | 0.7212 | 0.7212 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
797 | 679.3 | 466.5 | 102.9 | 113.7 | 18.5 | 804.3 | 5751.7 | 46.4 | 35.6 | 92.9 | 93.9 | 81.9 | 95.9 | 40.9 | 25.1 | 5080.8 | 6453.5 | 6579 | 7846.6 | 10721.8 | 10867.4 | 1.544 | 1.661 | 1.652 | 0.732 | 0.716 | 0.768 | 5.74 | 5.79 | 6.52 | 0.61 | 0.583 | 0.737 | 4.58 | 4.97 | -5.08 | 0.658 | 0.631 | 0.614 | 4.45 | 5.13 | 4.5 | 0.646 | 0.72 | 0.699 | 4.34 | 5.88 | 5.54 | Poor_Mixed | 5080.8 | 7846.6 | 1.544 | 0.768 | 6.52 | 0.737 | 5.88 | 0.46 | 0.7276 | 0.4837 | 0.576 | 1 | 0.3982 | 0.5023 | 0.5856 | 0.5856 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
798 | 568.5 | 328.4 | 80.7 | 86.8 | 12.6 | 645.7 | 3935.3 | 52.6 | 28.6 | 85.6 | 83.6 | 77.1 | 91.9 | 38.1 | 18.5 | 7984.3 | 8510.2 | 8368.1 | 14371.1 | 15087.3 | 15418 | 1.8 | 1.773 | 1.842 | 0.591 | 0.607 | 0.671 | 3.6 | 4.64 | 4.35 | 0.562 | 0.606 | 0.59 | 3.25 | -2.74 | 3.05 | 0.616 | 0.636 | 0.558 | 2.86 | 4.21 | 3.34 | 0.599 | 0.585 | 0.603 | 2.64 | 3.95 | -3.31 | Fair_Mixed | 7984.3 | 14371.1 | 1.773 | 0.671 | 4.64 | 0.636 | 4.21 | 0.6067 | 0.815 | 0.673 | 0.7933 | 1 | 0.6168 | 0.6538 | 0.7205 | 0.7205 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
799 | 856.4 | 551.9 | 101.7 | 131.9 | 15.2 | 913.3 | 5107.5 | 43.8 | 33.5 | 92.9 | 88.4 | 83.6 | 97.5 | 39.7 | 25 | 4688.7 | 6042.8 | 4522.7 | 6886.6 | 9606.8 | 6464.7 | 1.469 | 1.59 | 1.429 | 0.758 | 0.725 | 0.676 | 5.79 | -6.45 | -5.3 | 0.623 | 0.675 | 0.733 | 4.38 | 4.91 | 3.98 | 0.624 | 0.655 | 0.653 | 5.43 | 4.77 | 4.23 | 0.647 | 0.712 | 0.647 | 3.88 | 4.22 | -3.28 | Poor_Mixed | 4522.7 | 6464.7 | 1.429 | 0.758 | 6.45 | 0.733 | 5.43 | 0.434 | 0.752 | 0.5086 | 0.5796 | 1 | 0.425 | 0.5122 | 0.5903 | 0.5903 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
800 | 721.8 | 417.4 | 93.9 | 105.9 | 15 | 713 | 4310 | 50 | 32.9 | 87.8 | 90.3 | 80.8 | 93.9 | 39.5 | 20.4 | 6702.3 | 7590.3 | 5793.4 | 10913.2 | 13071.5 | 8920.1 | 1.628 | 1.722 | 1.54 | 0.671 | 0.659 | 0.689 | 4.76 | -4.4 | 5.04 | 0.611 | 0.629 | 0.596 | 4.08 | 5.15 | 3.81 | 0.657 | 0.689 | 0.639 | 4.72 | 4.39 | -5.08 | 0.625 | 0.64 | 0.724 | 4.24 | 4.28 | 4.12 | Poor_Mixed | 5793.4 | 8920.1 | 1.54 | 0.689 | 5.04 | 0.724 | 5.15 | 0.5249 | 0.7593 | 0.5666 | 0.734 | 1 | 0.5305 | 0.5323 | 0.6458 | 0.6458 | Fair | 1 | 1 | DGA | 0 |  | C2H2
801 | 1592.8 | 824.4 | 137.9 | 181.9 | 34.1 | 1308.9 | 7972.6 | 31.8 | 48.5 | 106.4 | 107.9 | 94.5 | 115.8 | 43.7 | 33.8 | 2589.4 | 1427.4 | 2089.5 | 2990.5 | 1593.7 | 2446.2 | 1.155 | 1.117 | 1.171 | 0.925 | 0.968 | 0.939 | 8.35 | 9.74 | 9.33 | 0.792 | 0.862 | 0.876 | 7.25 | 6.52 | 7.81 | 0.889 | 0.845 | 0.839 | 4.72 | 8.04 | -5.57 | 0.85 | 0.874 | 0.8 | 5.61 | 6.97 | 8.35 | Very Poor_Mixed | 1427.4 | 1593.7 | 1.117 | 0.968 | 9.74 | 0.889 | 8.35 | 0.0995 | 0.597 | 0.1298 | 0.2513 | 1 | 0.0799 | 0.2306 | 0.3347 | 0.3347 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
802 | 1592.4 | 886.2 | 129.7 | 176.6 | 34.3 | 1308.4 | 8361.2 | 32.2 | 47.9 | 104.1 | 105.5 | 92.3 | 114.9 | 43.6 | 31.5 | 2146.6 | 690 | 2253.4 | 2568.8 | 1200 | 2461.8 | 1.197 | 1.739 | 1.092 | 0.966 | 0.971 | 0.895 | -7.92 | 9.3 | -9.27 | 0.883 | 0.949 | 0.945 | -8.76 | 5.24 | 7.81 | 0.916 | 0.861 | 0.817 | -7.46 | 5.95 | 5.52 | 0.751 | 0.933 | 0.766 | 6.55 | 8.3 | 8.14 | Very Poor_Mixed | 690 | 1200 | 1.092 | 0.971 | 9.3 | 0.949 | 8.76 | 0.0978 | 0.6025 | 0.1733 | 0.3406 | 1 | 0.0959 | 0.203 | 0.3411 | 0.3411 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
803 | 1766 | 947.9 | 145.1 | 197 | 33.8 | 1379 | 9042.9 | 25.8 | 29 | 81 | 82.2 | 77.8 | 85.9 | 37.2 | 17.4 | 8651.6 | 9018.3 | 8105.6 | 15800.9 | 16620.3 | 14900.5 | 1.826 | 1.843 | 1.838 | 0.616 | 0.643 | 0.606 | -4.68 | 3.91 | -3.79 | 0.591 | 0.583 | 0.565 | -3.12 | -3.97 | 3.83 | 0.556 | 0.566 | 0.629 | -3.63 | -3.2 | 3.26 | 0.637 | 0.622 | 0.54 | -3.7 | 4.96 | 3.72 | Critical_DGA | 8105.6 | 14900.5 | 1.826 | 0.643 | 4.68 | 0.637 | 4.96 | 0.0352 | 0.2262 | 0.7495 | 0.8262 | 1 | 0.6208 | 0.6494 | 0.516 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
804 | 188 | 154.2 | 68.2 | 114.4 | 4.2 | 398.3 | 3088.3 | 56.4 | 23.9 | 92.2 | 95.3 | 84.1 | 98.7 | 39.8 | 14.3 | 9585.3 | 8684.9 | 8848.8 | 18802.3 | 16488.2 | 16432.8 | 1.962 | 1.898 | 1.857 | 0.559 | 0.583 | 0.575 | -3.34 | -3.57 | -3.44 | 0.539 | 0.5 | 0.563 | 2.23 | -2 | -2.6 | 0.516 | 0.524 | 0.526 | 2.35 | 3.52 | -2.47 | 0.523 | 0.545 | 0.597 | 2.75 | 2.34 | 2.62 | Poor_Thermal | 8684.9 | 16432.8 | 1.857 | 0.583 | 3.57 | 0.597 | 3.52 | 0.7729 | 0.8894 | 0.4588 | 0.9118 | 1 | 0.7238 | 0.8146 | 0.7994 | 0.7994 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
805 | 770.8 | 512.3 | 105.5 | 138 | 17.2 | 847.8 | 5298.9 | 56 | 23.6 | 80.3 | 80.2 | 75.2 | 87.3 | 36.7 | 13.3 | 8250.4 | 9981.6 | 9338.2 | 15654.7 | 19236.5 | 17905.1 | 1.897 | 1.927 | 1.917 | 0.543 | 0.586 | 0.63 | -3.42 | 3.09 | 4.1 | 0.543 | 0.512 | 0.524 | 2 | 2 | 2.66 | 0.518 | 0.5 | 0.507 | -3.32 | 2.14 | 2.62 | 0.5 | 0.538 | 0.5 | -2.79 | 2.38 | -2 | Poor_DGA | 8250.4 | 15654.7 | 1.897 | 0.63 | 4.1 | 0.543 | 3.32 | 0.4298 | 0.895 | 0.7864 | 0.9367 | 1 | 0.7037 | 0.8902 | 0.7591 | 0.7591 | Fair | 1 | 1 | DGA | 0 |  | C2H2
806 | 350.7 | 264.6 | 82.1 | 70.4 | 3.7 | 542.6 | 4009.8 | 58.9 | 20.9 | 79.9 | 77.7 | 75.6 | 84.3 | 36.8 | 11 | 10000 | 9136.2 | 9346 | 20000 | 17709.1 | 17662.8 | 2 | 1.938 | 1.89 | 0.771 | 0.803 | 0.803 | 5.9 | 7.09 | 6.64 | 0.577 | 0.5 | 0.541 | 2 | 2.57 | 2.73 | 0.529 | 0.558 | 0.5 | -2.69 | -2.2 | -2 | 0.592 | 0.594 | 0.538 | 2.24 | 2.98 | -2.28 | Poor_Winding_TD_Cap | 9136.2 | 17662.8 | 1.89 | 0.803 | 7.09 | 0.594 | 2.98 | 0.7616 | 0.9574 | 0.8246 | 0.9858 | 1 | 0.3251 | 0.8061 | 0.7876 | 0.7876 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
807 | 861.9 | 484.5 | 103.7 | 114.9 | 20.3 | 820.6 | 6070.5 | 45.2 | 33.8 | 94.8 | 90.5 | 83.7 | 96.1 | 40.8 | 26.8 | 5009.7 | 5747.4 | 5180.7 | 7905.3 | 8813.6 | 8023.8 | 1.578 | 1.533 | 1.549 | 0.742 | 0.754 | 0.763 | 5.48 | 6.28 | 6.76 | 0.65 | 0.608 | 0.584 | -3.4 | -4.04 | 5.85 | 0.68 | 0.705 | 0.686 | -3.92 | 3.48 | -4.03 | 0.663 | 0.637 | 0.678 | 3.84 | 4.04 | 4.77 | Poor_Mixed | 5009.7 | 7905.3 | 1.533 | 0.763 | 6.76 | 0.705 | 5.85 | 0.4252 | 0.7485 | 0.4819 | 0.5156 | 1 | 0.3773 | 0.5318 | 0.5786 | 0.5786 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
808 | 783.2 | 542.2 | 106.1 | 118.8 | 16.4 | 885.6 | 5806.7 | 48.9 | 34 | 89.4 | 91.8 | 82.8 | 99.8 | 39.8 | 25.6 | 6478.9 | 4696.4 | 5152.7 | 10333.4 | 6790.6 | 7754.6 | 1.595 | 1.446 | 1.505 | 0.756 | 0.699 | 0.777 | 6.03 | 5.79 | 6.46 | 0.639 | 0.653 | 0.627 | -3.8 | 5.01 | 4.96 | 0.722 | 0.617 | 0.59 | 3.4 | 4.92 | 4.6 | 0.677 | 0.621 | 0.639 | 4.86 | -4.7 | 5.44 | Poor_Mixed | 4696.4 | 6790.6 | 1.446 | 0.777 | 6.46 | 0.722 | 5.44 | 0.4383 | 0.7461 | 0.5017 | 0.5584 | 1 | 0.3899 | 0.5286 | 0.5869 | 0.5869 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
809 | 496.8 | 324.1 | 85.1 | 84.2 | 1.6 | 572.6 | 3677.2 | 50.1 | 28.9 | 87.6 | 82.1 | 79.6 | 91.1 | 38 | 13.2 | 7019.4 | 8464.7 | 8522 | 12099.7 | 14594 | 15062.4 | 1.724 | 1.724 | 1.767 | 0.975 | 0.984 | 0.94 | 9.03 | 9.45 | 12.07 | 0.558 | 0.613 | 0.595 | -2.69 | 3.1 | -2.77 | 0.522 | 0.581 | 0.582 | -3.21 | 2.78 | 3.29 | 0.605 | 0.593 | 0.588 | 3.51 | 2.45 | 2.86 | Critical_Winding_TD_Cap | 7019.4 | 12099.7 | 1.724 | 0.984 | 12.07 | 0.613 | 3.51 | 0.7711 | 0.8109 | 0.6579 | 0.939 | 1 | 0.0472 | 0.691 | 0.6938 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_LV_TanDelta_pct
810 | 203.4 | 161.6 | 71.2 | 50.2 | 1 | 350 | 2500 | 53.8 | 23.8 | 77.9 | 80.3 | 70 | 83.5 | 35.9 | 11.8 | 8910.9 | 9579.9 | 8161.5 | 16776.3 | 19009.6 | 14596 | 1.883 | 1.984 | 1.788 | 0.5 | 0.5 | 0.523 | 2.37 | -2.94 | 2.05 | 0.584 | 0.534 | 0.532 | 2 | 2.47 | 2.55 | 0.5 | 0.5 | 0.551 | 2.36 | 2.02 | 2.22 | 0.508 | 0.553 | 0.533 | 2.11 | 2 | 2.76 | Fair_Oil | 8161.5 | 14596 | 1.788 | 0.523 | 2.94 | 0.584 | 2.76 | 0.9775 | 0.8912 | 0.8798 | 0.9703 | 1 | 0.9334 | 0.8473 | 0.931 | 0.931 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
811 | 875.8 | 564.1 | 112.2 | 117.2 | 14.3 | 877.5 | 5213 | 54.2 | 25.3 | 76.2 | 79.2 | 72.6 | 84.7 | 35.6 | 16.2 | 8772.9 | 9403.7 | 9474.6 | 16102.7 | 18488.3 | 18135.1 | 1.836 | 1.966 | 1.914 | 0.545 | 0.615 | 0.604 | 2.78 | 2.97 | 3.91 | 0.56 | 0.526 | 0.518 | 2 | 2.85 | 2.07 | 0.531 | 0.539 | 0.507 | 3.37 | 2.29 | -3.02 | 0.561 | 0.516 | 0.528 | 2.54 | 2 | -2.91 | Poor_DGA | 8772.9 | 16102.7 | 1.836 | 0.615 | 3.91 | 0.561 | 3.37 | 0.447 | 0.865 | 0.8752 | 0.8607 | 1 | 0.7214 | 0.8196 | 0.7546 | 0.7546 | Fair | 1 | 1 | DGA | 0 |  | C2H2
812 | 852.8 | 501.8 | 104.3 | 117.7 | 15.6 | 768.8 | 5228.8 | 41.7 | 38.4 | 89.9 | 93.4 | 83.7 | 98.9 | 40.3 | 28.5 | 6893.8 | 5813.5 | 4975.7 | 11282.4 | 9022.2 | 7684.3 | 1.637 | 1.552 | 1.544 | 0.698 | 0.794 | 0.725 | 4.83 | -6.82 | -5.65 | 0.696 | 0.646 | 0.631 | 5.01 | 3.15 | -3.68 | 0.713 | 0.674 | 0.659 | 3.69 | -3.42 | -3.59 | 0.682 | 0.734 | 0.659 | 5.35 | -5.02 | 3.85 | Poor_Mixed | 4975.7 | 7684.3 | 1.544 | 0.794 | 6.82 | 0.734 | 5.35 | 0.4656 | 0.6968 | 0.4839 | 0.4535 | 1 | 0.4131 | 0.5047 | 0.5798 | 0.5798 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
813 | 588.6 | 376.9 | 86.2 | 90.3 | 1.8 | 605.8 | 4657.4 | 55.7 | 23.4 | 118 | 85.1 | 77.8 | 90.4 | 36.9 | 15.2 | 690 | 1379.7 | 690 | 727.6 | 1504.3 | 736.4 | 1.054 | 1.09 | 1.067 | 0.698 | 0.709 | 0.722 | -6.02 | 5.29 | -5.81 | 0.582 | 0.567 | 0.538 | -3.57 | 3.16 | 3.83 | 0.577 | 0.556 | 0.67 | 3.05 | 2.83 | -3.23 | 0.573 | 0.604 | 0.635 | 3.5 | 2.95 | 2.57 | Critical_IR_PI | 690 | 727.6 | 1.054 | 0.722 | 6.02 | 0.67 | 3.83 | 0.7293 | 0.8988 | 0.5231 | 0.8882 | 0.85 | 0.4407 | 0.6702 | 0.7052 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature; IR_Min_10min<1000 Mohm: critical insulation resistance | WTI_HV
814 | 300.6 | 154.3 | 78.2 | 64.4 | 2.3 | 474.8 | 3060.3 | 53.3 | 65 | 82.2 | 84.1 | 77.4 | 89.6 | 36.9 | 11.8 | 2731.5 | 1197.4 | 2342.3 | 3544.6 | 1400 | 2929 | 1.298 | 1.169 | 1.25 | 0.593 | 0.681 | 0.709 | -3.98 | 5.32 | 5.27 | 0.5 | 0.525 | 0.566 | 2.58 | 2 | -2.52 | 0.528 | 0.51 | 0.514 | -3.22 | -3.02 | -2.53 | 0.54 | 0.518 | 0.538 | 2.21 | -2.34 | 2.3 | Critical_IR_PI | 1197.4 | 1400 | 1.169 | 0.709 | 5.32 | 0.566 | 3.22 | 0.8365 | 0.5833 | 0.711 | 0.9703 | 1 | 0.5392 | 0.8406 | 0.7855 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
815 | 919.9 | 473.8 | 98.4 | 109 | 17.8 | 843.9 | 4447.3 | 48.3 | 33 | 89 | 91.5 | 80.2 | 96.3 | 38.9 | 25.5 | 6328.5 | 5706.2 | 5227.5 | 9948 | 8800.6 | 8327.2 | 1.572 | 1.542 | 1.593 | 0.701 | 0.684 | 0.66 | 4.46 | 4.35 | 4.01 | 0.673 | 0.611 | 0.627 | 3.95 | 4.53 | 3.9 | 0.609 | 0.616 | 0.621 | 3.33 | 3.26 | 4.61 | 0.623 | 0.57 | 0.629 | 3.44 | 3.35 | 4.74 | Poor_Mixed | 5227.5 | 8327.2 | 1.542 | 0.701 | 4.46 | 0.673 | 4.74 | 0.4601 | 0.7581 | 0.5463 | 0.562 | 1 | 0.5492 | 0.5883 | 0.6315 | 0.6315 | Fair | 1 | 1 | DGA | 0 |  | C2H2
816 | 951.9 | 605.7 | 117.9 | 131.2 | 19.8 | 942.7 | 6144.2 | 59.5 | 22.5 | 77.1 | 77.2 | 70 | 81.8 | 35.4 | 15 | 8229.5 | 8089.1 | 7657.3 | 14395 | 14393.4 | 14011.8 | 1.749 | 1.779 | 1.83 | 0.593 | 0.544 | 0.563 | 2.62 | 2.46 | -3.1 | 0.536 | 0.522 | 0.577 | 3.28 | 3.04 | 2.98 | 0.554 | 0.582 | 0.537 | 3.36 | 3.81 | -2.34 | 0.5 | 0.513 | 0.552 | 2.63 | 3.02 | -3.03 | Poor_DGA | 7657.3 | 14011.8 | 1.749 | 0.593 | 3.1 | 0.582 | 3.81 | 0.3657 | 0.9171 | 0.928 | 0.8935 | 1 | 0.7819 | 0.7783 | 0.7485 | 0.7485 | Fair | 1 | 1 | DGA | 0 |  | C2H2
817 | 1681.3 | 913.1 | 138.6 | 172.9 | 31.4 | 1196.8 | 8227.6 | 34.5 | 45.8 | 103.3 | 103.7 | 93.3 | 111.9 | 45.4 | 32.2 | 2233.9 | 2299.2 | 1917.2 | 2698.1 | 2704.6 | 2147.7 | 1.208 | 1.176 | 1.12 | 0.909 | 0.877 | 0.88 | 8.74 | 7.9 | 7.89 | 0.907 | 0.878 | 0.775 | 5.75 | -7.38 | 5.98 | 0.76 | 0.787 | 0.931 | -6.66 | 7.24 | 6.23 | 0.903 | 0.742 | 0.68 | 7.72 | -5.56 | 8.15 | Very Poor_Mixed | 1917.2 | 2147.7 | 1.12 | 0.909 | 8.74 | 0.931 | 8.15 | 0.1114 | 0.6222 | 0.1841 | 0.3137 | 1 | 0.167 | 0.2621 | 0.3672 | 0.3672 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
818 | 270.3 | 269.3 | 77.4 | 60.9 | 1 | 501.5 | 2856.8 | 58.6 | 23.4 | 77.9 | 79.9 | 71.4 | 85.6 | 36.4 | 15.3 | 3795.8 | 5029.7 | 5146.2 | 5038.8 | 7089.4 | 7720.9 | 1.327 | 1.41 | 1.5 | 0.653 | 0.62 | 0.695 | 5.24 | 3.76 | 5.13 | 0.514 | 0.554 | 0.553 | 2.99 | 2.05 | 2.41 | 0.506 | 0.552 | 0.551 | 3.25 | -2.64 | 2 | 0.547 | 0.515 | 0.529 | 2.3 | -2.49 | 2.37 | Poor_IR_PI | 3795.8 | 5038.8 | 1.327 | 0.695 | 5.24 | 0.554 | 3.25 | 0.9016 | 0.8988 | 0.8531 | 0.8855 | 1 | 0.5507 | 0.8128 | 0.8462 | 0.8462 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
819 | 1601.3 | 861.1 | 144.2 | 190.9 | 34.3 | 1322.1 | 8618.9 | 31 | 46.8 | 104.7 | 104.1 | 95 | 114.9 | 45 | 33.2 | 2428 | 708.2 | 2460.3 | 2862.1 | 1200 | 3036.1 | 1.179 | 1.694 | 1.234 | 0.97 | 0.942 | 0.932 | 9.74 | -8.83 | 9.54 | 0.93 | 0.891 | 0.786 | 5.95 | 8.5 | -5.93 | 0.871 | 0.792 | 0.855 | 8.76 | 7.59 | 7.91 | 0.726 | 0.752 | 0.746 | 7.28 | -6.29 | -6.39 | Very Poor_Mixed | 708.2 | 1200 | 1.179 | 0.97 | 9.74 | 0.93 | 8.76 | 0.0717 | 0.6128 | 0.1525 | 0.2748 | 1 | 0.0656 | 0.2476 | 0.3342 | 0.3342 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
820 | 562.8 | 342 | 91.5 | 78.7 | 1.8 | 693.3 | 4329.8 | 54.8 | 25.7 | 83.8 | 84.1 | 79.1 | 91.5 | 37.7 | 14.2 | 8166.9 | 163.3 | 9088.1 | 14762.8 | 254.8 | 16845.8 | 1.808 | 1.56 | 1.854 | 0.929 | 0.954 | 0.957 | 8.85 | -9.84 | 8.89 | 0.519 | 0.529 | 0.551 | 3.8 | 2.85 | 2.92 | 0.571 | 0.5 | 0.569 | -2.65 | 2.67 | 3.04 | 0.544 | 0.5 | 0.521 | 2.45 | 2.19 | 2.27 | Critical_Winding_TD_Cap | 163.3 | 254.8 | 1.56 | 0.957 | 9.84 | 0.571 | 3.8 | 0.7363 | 0.8584 | 0.6729 | 0.9144 | 0.85 | 0.0753 | 0.8176 | 0.6938 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_TV_TanDelta_pct
821 | 740.2 | 551.3 | 100.9 | 114.6 | 18.5 | 826.2 | 6161.7 | 48.7 | 32.8 | 87.9 | 93.8 | 81.7 | 98.4 | 40.1 | 23.9 | 5262.4 | 5722.8 | 6288.8 | 8199.3 | 7816.2 | 9788.7 | 1.558 | 1.366 | 1.557 | 0.755 | 0.701 | 0.698 | 5.87 | 5.15 | 4.82 | 0.72 | 0.683 | 0.669 | 4.69 | -4.55 | 5.94 | 0.681 | 0.665 | 0.715 | -5.05 | 3.72 | -4.65 | 0.652 | 0.759 | 0.634 | 4.54 | 5.91 | -6.36 | Poor_Mixed | 5262.4 | 7816.2 | 1.366 | 0.755 | 5.87 | 0.759 | 6.36 | 0.4388 | 0.7605 | 0.5113 | 0.6177 | 1 | 0.4576 | 0.4572 | 0.5893 | 0.5893 | Poor | 0 | 1 | DGA | 0 |  | C2H2
822 | 100 | 120 | 66.7 | 75.5 | 2.2 | 410.3 | 2500 | 60 | 20.3 | 83.9 | 81.9 | 78.2 | 88.5 | 37.8 | 11 | 8642.5 | 10000 | 10000 | 16878.8 | 19090 | 19546 | 1.953 | 1.909 | 1.955 | 0.5 | 0.539 | 0.506 | -2 | -2 | 2.45 | 0.522 | 0.5 | 0.5 | -3.19 | 2 | -2.43 | 0.548 | 0.516 | 0.5 | 2.73 | 2 | -2 | 0.531 | 0.5 | 0.53 | 2.6 | 2 | 2 | Fair_Thermal | 8642.5 | 16878.8 | 1.909 | 0.539 | 2.45 | 0.548 | 3.19 | 0.8717 | 0.9791 | 0.7098 | 0.9858 | 1 | 0.9354 | 0.8999 | 0.9086 | 0.9086 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
823 | 972.2 | 453.1 | 110.9 | 122 | 16.7 | 757.3 | 5489.4 | 47.5 | 34.4 | 89.6 | 91.4 | 82 | 98.9 | 38.6 | 25.1 | 5159.6 | 4770.5 | 6487.2 | 7973.8 | 7153.8 | 9905 | 1.545 | 1.5 | 1.527 | 0.748 | 0.664 | 0.746 | -5.99 | 4.06 | 6.54 | 0.674 | 0.691 | 0.641 | -4.91 | 4.97 | 4.66 | 0.635 | 0.759 | 0.66 | 2.81 | 3.01 | 4.73 | 0.661 | 0.671 | 0.701 | 5.42 | 5.32 | 4.98 | Poor_Mixed | 4770.5 | 7153.8 | 1.5 | 0.748 | 6.54 | 0.759 | 5.42 | 0.4443 | 0.7414 | 0.52 | 0.576 | 1 | 0.4445 | 0.4883 | 0.591 | 0.591 | Poor | 0 | 1 | DGA | 0 |  | C2H2
824 | 204.8 | 150.8 | 71 | 53.6 | 1 | 350 | 2885.4 | 18.6 | 25.7 | 86.1 | 86.7 | 78.7 | 92.7 | 38.5 | 13.9 | 1133.7 | 1292.7 | 1081.3 | 1167.1 | 1325.6 | 1103 | 1.029 | 1.025 | 1.02 | 0.772 | 0.762 | 0.672 | 6.2 | 6.33 | 5.99 | 0.519 | 0.568 | 0.515 | -2 | 2.43 | 2.08 | 0.534 | 0.5 | 0.539 | 2.19 | -2.33 | 2.15 | 0.55 | 0.561 | 0.57 | 2.62 | 2.08 | 3.31 | Critical_IR_PI | 1081.3 | 1103 | 1.02 | 0.772 | 6.33 | 0.57 | 3.31 | 0.9687 | 0.2751 | 0.6292 | 0.9219 | 1 | 0.3937 | 0.8176 | 0.7465 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
825 | 740.1 | 388.8 | 85.7 | 103.8 | 1.8 | 2785.5 | 21899.4 | 55 | 24.5 | 81.5 | 81.6 | 74.8 | 85.8 | 37.4 | 13.7 | 8442.5 | 8816.1 | 8908.3 | 16222.7 | 16470.2 | 16190.3 | 1.922 | 1.868 | 1.817 | 0.979 | 0.964 | 0.908 | 9.31 | 9.44 | -8.75 | 0.549 | 0.571 | 0.521 | -2.56 | 2 | 2.82 | 0.527 | 0.587 | 0.511 | 2 | 2 | 2.34 | 0.53 | 0.548 | 0.568 | 2.73 | 2.98 | -2.36 | Critical_Winding_TD_Cap | 8442.5 | 16190.3 | 1.817 | 0.979 | 9.44 | 0.587 | 2.98 | 0.5414 | 0.8786 | 0.7715 | 0.9269 | 1 | 0.0744 | 0.7934 | 0.6775 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
826 | 879.4 | 529.7 | 105 | 123.5 | 19.5 | 851.3 | 5150.7 | 46.8 | 33.6 | 89.1 | 90.2 | 82.7 | 94.3 | 38.5 | 25.6 | 5845 | 7212.8 | 5808 | 8928.3 | 11573.7 | 8818.8 | 1.528 | 1.605 | 1.518 | 0.777 | 0.73 | 0.742 | 6.25 | 5.69 | 5.45 | 0.703 | 0.702 | 0.706 | -5.41 | 3.67 | 3.5 | 0.718 | 0.597 | 0.676 | -5.33 | 4.9 | 4.19 | 0.7 | 0.697 | 0.613 | 6.63 | 3.66 | 4.94 | Poor_Mixed | 5808 | 8818.8 | 1.518 | 0.777 | 6.25 | 0.718 | 6.63 | 0.4201 | 0.7509 | 0.5504 | 0.5584 | 1 | 0.4008 | 0.4809 | 0.5807 | 0.5807 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
827 | 1626 | 914.3 | 140.8 | 185.4 | 32.9 | 1231.4 | 8129.2 | 33.8 | 45.5 | 104.3 | 106.3 | 92.4 | 113.2 | 44.2 | 33.1 | 1503.2 | 2070.3 | 2380.3 | 1708.1 | 2355.1 | 2832.3 | 1.136 | 1.138 | 1.19 | 0.879 | 0.908 | 0.968 | 8.17 | 8.44 | -9.71 | 0.805 | 0.745 | 0.874 | 6.37 | 6.01 | -9.3 | 0.83 | 0.911 | 0.784 | 8.39 | -6.24 | 7.95 | 0.861 | 0.839 | 0.799 | 6.37 | -7.36 | 8.17 | Very Poor_Mixed | 1503.2 | 1708.1 | 1.136 | 0.968 | 9.71 | 0.911 | 9.3 | 0.0938 | 0.6251 | 0.1714 | 0.2787 | 1 | 0.1163 | 0.23 | 0.3472 | 0.3472 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
828 | 912.7 | 487.7 | 103.8 | 108.9 | 17 | 872 | 5385.8 | 58.4 | 23 | 75.7 | 75 | 70 | 81.8 | 35 | 13.1 | 9952.8 | 8399.2 | 9421.3 | 19721.2 | 16240 | 17658.5 | 1.981 | 1.934 | 1.874 | 0.593 | 0.597 | 0.613 | 3.4 | -3.19 | -4.06 | 0.566 | 0.542 | 0.511 | 2.98 | 2.87 | 2 | 0.585 | 0.514 | 0.508 | 2.95 | 2.03 | 2.22 | 0.61 | 0.554 | 0.578 | -3.2 | 2.81 | 2.88 | Poor_DGA | 8399.2 | 16240 | 1.874 | 0.613 | 4.06 | 0.61 | 3.2 | 0.4478 | 0.9067 | 0.9777 | 0.9414 | 1 | 0.6803 | 0.7736 | 0.7601 | 0.7601 | Fair | 1 | 1 | DGA | 0 |  | C2H2
829 | 208.6 | 132.3 | 77 | 63.8 | 1.4 | 421.5 | 3519.9 | 58.1 | 24.6 | 75 | 75 | 71.6 | 80 | 35 | 11.9 | 5891.4 | 6549 | 6081.7 | 8998 | 10881.7 | 9708 | 1.527 | 1.662 | 1.596 | 0.571 | 0.598 | 0.632 | -3.75 | 4.02 | -3.68 | 0.506 | 0.576 | 0.529 | -2 | 2.16 | -2.78 | 0.589 | 0.552 | 0.557 | 2.49 | 2.42 | 3.23 | 0.524 | 0.529 | 0.562 | 2.4 | -3.19 | -2.5 | Fair_IR_PI | 5891.4 | 8998 | 1.527 | 0.632 | 4.02 | 0.589 | 3.23 | 0.8866 | 0.8768 | 0.9808 | 0.9682 | 1 | 0.6655 | 0.783 | 0.8675 | 0.8675 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
830 | 114.4 | 166.1 | 71.6 | 58.3 | 1.6 | 443.9 | 2747.6 | 57.7 | 22.8 | 77.5 | 78.4 | 73.1 | 84 | 35.4 | 11.1 | 9063.9 | 9084.5 | 8502 | 17288.2 | 18169.1 | 15624.1 | 1.907 | 2 | 1.838 | 0.5 | 0.505 | 0.601 | -2.38 | 2.27 | 3.73 | 0.669 | 0.558 | 0.549 | 5.72 | 2.78 | 2 | 0.517 | 0.52 | 0.5 | 2.54 | 2.68 | 3.97 | 0.535 | 0.561 | 0.522 | 3.72 | -3.54 | 3.35 | Poor_Bushing_TD_Cap | 8502 | 15624.1 | 1.838 | 0.601 | 3.73 | 0.669 | 5.72 | 0.897 | 0.9108 | 0.8681 | 0.984 | 1 | 0.8579 | 0.7606 | 0.8866 | 0.8866 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
831 | 1530.9 | 894.1 | 141.9 | 180.2 | 33.2 | 1245.3 | 8268.8 | 34.8 | 44.5 | 106.7 | 106.5 | 95.6 | 117.3 | 45.6 | 31.9 | 3154 | 2827.9 | 1440.1 | 3939 | 3612.5 | 1648.2 | 1.249 | 1.277 | 1.145 | 0.878 | 0.95 | 0.919 | 8 | -9.04 | -8.81 | 0.824 | 0.744 | 0.892 | 6.5 | 8.18 | -6.76 | 0.782 | 0.877 | 0.812 | 7.18 | -6.91 | 5.75 | 0.765 | 0.922 | 0.843 | 7 | -6.34 | -7.3 | Very Poor_Mixed | 1440.1 | 1648.2 | 1.145 | 0.95 | 9.04 | 0.922 | 8.18 | 0.1016 | 0.6347 | 0.1083 | 0.3252 | 1 | 0.1258 | 0.2443 | 0.3502 | 0.3502 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
832 | 1567.8 | 781.5 | 138.7 | 174.6 | 34.3 | 1215.5 | 8098 | 33 | 46.8 | 104.1 | 105.3 | 95.4 | 114.4 | 45 | 33.2 | 690 | 1110.9 | 1346.3 | 1200 | 1200 | 1538.2 | 1.739 | 1.08 | 1.143 | 0.901 | 0.93 | 0.884 | -8.48 | -9.12 | 8.68 | 0.907 | 0.81 | 0.916 | 8.6 | -7.02 | 5.45 | 0.784 | 0.692 | 0.892 | 8.68 | 6.59 | -7.07 | 0.821 | 0.889 | 0.756 | -7.35 | 7.21 | 6.52 | Very Poor_Mixed | 690 | 1200 | 1.08 | 0.93 | 9.12 | 0.916 | 8.68 | 0.1192 | 0.6128 | 0.1494 | 0.2748 | 1 | 0.1257 | 0.2361 | 0.3521 | 0.3521 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
833 | 1554.2 | 801.8 | 138.7 | 178 | 33 | 1294.6 | 7723.6 | 33 | 46.7 | 104.6 | 100.8 | 91.8 | 110.2 | 43.4 | 33.2 | 1702.9 | 2288.6 | 755 | 1860.6 | 2673.4 | 1200 | 1.093 | 1.168 | 1.589 | 0.901 | 0.933 | 0.892 | 8.84 | -8.66 | -8.24 | 0.759 | 0.893 | 0.841 | 7.94 | 6.75 | 6.62 | 0.812 | 0.84 | 0.866 | 7.91 | 6.89 | 7.04 | 0.842 | 0.811 | 0.777 | 6.11 | 7.25 | -6.02 | Very Poor_Mixed | 755 | 1200 | 1.093 | 0.933 | 8.84 | 0.893 | 7.94 | 0.1168 | 0.6137 | 0.2249 | 0.2748 | 1 | 0.1323 | 0.243 | 0.3613 | 0.3613 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
834 | 113.3 | 121.9 | 69.6 | 50 | 1 | 401.9 | 2500 | 59 | 20.8 | 77.6 | 77.1 | 71.6 | 80.8 | 36.9 | 10 | 9144.8 | 9069 | 8822.1 | 16706.2 | 17973.7 | 16645.8 | 1.827 | 1.982 | 1.887 | 0.541 | 0.5 | 0.5 | 2.97 | 2 | 2 | 0.521 | 0.541 | 0.5 | 2.04 | 2.26 | 2.13 | 0.5 | 0.5 | 0.5 | -2.14 | 2.14 | 2 | 0.501 | 0.5 | 0.5 | 2 | 2.63 | -2 | Good_Mixed | 8822.1 | 16645.8 | 1.827 | 0.541 | 2.97 | 0.541 | 2.63 | 0.9827 | 0.9605 | 0.9026 | 1 | 1 | 0.9344 | 0.9533 | 0.9636 | 0.9636 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
835 | 869.6 | 509.4 | 95.6 | 119.3 | 16.5 | 836.1 | 4959.9 | 46.5 | 33.8 | 91.2 | 93 | 82.4 | 97.2 | 39.8 | 24 | 6999.6 | 6221.7 | 5876.6 | 11413.2 | 9604 | 9185.6 | 1.631 | 1.544 | 1.563 | 0.693 | 0.695 | 0.668 | 5.51 | 5.15 | 4.93 | 0.71 | 0.691 | 0.65 | -5.31 | 3.88 | 5.77 | 0.674 | 0.621 | 0.598 | 5.31 | 5.1 | -5.31 | 0.627 | 0.673 | 0.6 | 3.85 | 4.19 | -5.64 | Poor_Mixed | 5876.6 | 9185.6 | 1.544 | 0.695 | 5.51 | 0.71 | 5.77 | 0.4563 | 0.7485 | 0.4978 | 0.6143 | 1 | 0.492 | 0.5092 | 0.6049 | 0.6049 | Fair | 1 | 1 | DGA | 0 |  | C2H2
836 | 457 | 316.6 | 82.6 | 87.6 | 1.2 | 557.5 | 3690.8 | 33.8 | 47.7 | 77.9 | 78.3 | 71.4 | 83.3 | 35.7 | 15.5 | 333.6 | 4798.7 | 5228 | 350.6 | 7349.3 | 7448.5 | 1.051 | 1.532 | 1.425 | 0.702 | 0.675 | 0.676 | 4.73 | -4.4 | -4.51 | 0.564 | 0.572 | 0.507 | -2.61 | 3.2 | -3.19 | 0.543 | 0.59 | 0.524 | 3.16 | 2.73 | 2.78 | 0.589 | 0.547 | 0.621 | -3.03 | 3.57 | 2.74 | Critical_Oil | 333.6 | 350.6 | 1.051 | 0.702 | 4.73 | 0.621 | 3.57 | 0.7956 | 0.6044 | 0.8826 | 0.88 | 0.85 | 0.5303 | 0.7321 | 0.7457 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
837 | 1469.9 | 951.3 | 135.2 | 169 | 31 | 1156.5 | 7893 | 34.1 | 44.2 | 103.8 | 104 | 91.8 | 109.5 | 43.9 | 28.1 | 1577.9 | 2301 | 2422.1 | 1839.7 | 2724.5 | 2936.9 | 1.166 | 1.184 | 1.213 | 0.864 | 0.895 | 0.913 | 7.96 | 8.85 | -7.94 | 0.871 | 0.91 | 0.833 | 6.26 | 7.08 | -6.39 | 0.849 | 0.802 | 0.719 | 6.16 | 6.3 | 8.01 | 0.853 | 0.733 | 0.812 | 7.01 | 7.99 | -6.43 | Very Poor_Mixed | 1577.9 | 1839.7 | 1.166 | 0.913 | 8.85 | 0.91 | 8.01 | 0.139 | 0.6376 | 0.211 | 0.4683 | 1 | 0.1619 | 0.2539 | 0.3842 | 0.3842 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
838 | 828.9 | 491.5 | 97.2 | 120.9 | 16.4 | 818 | 5196.1 | 45.8 | 37.5 | 93.8 | 93.3 | 84.5 | 99.1 | 39.5 | 25 | 5764.7 | 4638.1 | 5796.9 | 9486.6 | 7005.9 | 8485.6 | 1.646 | 1.511 | 1.464 | 0.748 | 0.718 | 0.718 | -5.01 | 5.58 | 5.52 | 0.7 | 0.675 | 0.68 | 5.52 | 4.11 | 5.23 | 0.717 | 0.74 | 0.67 | -6.44 | 5.02 | 5.66 | 0.714 | 0.695 | 0.67 | 5.89 | 5.37 | 4.86 | Poor_Mixed | 4638.1 | 7005.9 | 1.464 | 0.748 | 5.58 | 0.74 | 6.44 | 0.4594 | 0.7065 | 0.4585 | 0.5796 | 1 | 0.4431 | 0.434 | 0.5746 | 0.5746 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
839 | 554.4 | 387.6 | 96.2 | 90.2 | 57.3 | 617.9 | 3813.2 | 30.6 | 49 | 81.7 | 83.1 | 77.7 | 87.6 | 37.6 | 15.9 | 4879.2 | 4339.3 | 4907.4 | 7436.1 | 6128.3 | 7626.8 | 1.524 | 1.412 | 1.554 | 0.674 | 0.679 | 0.644 | 4.82 | 5.16 | 5.8 | 0.533 | 0.521 | 0.554 | -3.89 | 2.99 | -2.97 | 0.539 | 0.564 | 0.551 | 2 | -3.04 | -2.34 | 0.5 | 0.538 | 0.528 | 2.9 | -3.55 | 2.85 | Critical_Oil | 4339.3 | 6128.3 | 1.412 | 0.679 | 5.8 | 0.564 | 3.89 | 0.469 | 0.5924 | 0.7266 | 0.869 | 1 | 0.5079 | 0.7925 | 0.6782 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
840 | 1627.3 | 873.1 | 138.2 | 183.9 | 28.5 | 1324.7 | 8279.5 | 34.4 | 44.3 | 106.8 | 105 | 95.4 | 114.9 | 43.6 | 34.9 | 2122.3 | 903.1 | 2390.1 | 2448 | 1200 | 2803.5 | 1.153 | 1.329 | 1.173 | 0.907 | 0.897 | 0.917 | -8.58 | 8.18 | 8.21 | 0.92 | 0.749 | 0.99 | -5.55 | 6.67 | 6.98 | 0.738 | 0.777 | 0.928 | 8.58 | 8.44 | -7.13 | 0.736 | 0.911 | 0.817 | 5.82 | 5.74 | 7.54 | Very Poor_Mixed | 903.1 | 1200 | 1.153 | 0.917 | 8.58 | 0.99 | 8.58 | 0.1094 | 0.6367 | 0.1438 | 0.2078 | 1 | 0.1464 | 0.235 | 0.3513 | 0.3513 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
841 | 1665.2 | 982.4 | 144.8 | 190 | 30.3 | 1379 | 8445.5 | 31.2 | 46.4 | 105.9 | 108.5 | 93 | 117.5 | 43.8 | 32.2 | 812.3 | 1064.3 | 888.5 | 1200 | 1200 | 1200 | 1.477 | 1.128 | 1.351 | 0.932 | 0.969 | 0.911 | -9.27 | -9.24 | 9.02 | 0.77 | 0.731 | 0.942 | 7.97 | -6.82 | -8.4 | 0.931 | 0.838 | 0.857 | 7.8 | 8.65 | 5.95 | 0.789 | 0.893 | 0.942 | -8.37 | -8.16 | -6.98 | Very Poor_Mixed | 812.3 | 1200 | 1.128 | 0.969 | 9.27 | 0.942 | 8.65 | 0.0682 | 0.6166 | 0.1284 | 0.3137 | 1 | 0.0825 | 0.1961 | 0.3264 | 0.3264 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
842 | 284.5 | 273.5 | 82 | 80.2 | 61.5 | 547.2 | 3322.1 | 33.2 | 44.4 | 83.5 | 82.7 | 76.4 | 90.6 | 37 | 19.1 | 4867.2 | 4974.4 | 5180.7 | 7454.7 | 7768.3 | 7959.7 | 1.532 | 1.562 | 1.536 | 0.653 | 0.665 | 0.646 | 5.13 | 4.69 | -4.36 | 0.566 | 0.539 | 0.544 | 3.1 | -2.01 | 2.59 | 0.5 | 0.522 | 0.558 | -2.32 | 2 | -2.21 | 0.551 | 0.514 | 0.512 | 2.59 | 2.45 | -3.74 | Critical_Oil | 4867.2 | 7454.7 | 1.532 | 0.665 | 5.13 | 0.566 | 3.74 | 0.5415 | 0.6357 | 0.7132 | 0.7749 | 1 | 0.5493 | 0.8213 | 0.7065 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
843 | 1296.5 | 724.7 | 131.4 | 164.7 | 28.2 | 1115.9 | 7181.5 | 34.6 | 43.9 | 105.3 | 103.2 | 94.4 | 114.4 | 45.8 | 30.6 | 3323.4 | 1938.2 | 4200 | 4291 | 2403.9 | 5338.9 | 1.291 | 1.24 | 1.271 | 0.989 | 0.929 | 0.893 | 9.14 | 8.56 | -8.86 | 0.865 | 0.802 | 0.775 | 7.14 | 8.42 | 7.42 | 0.812 | 0.89 | 0.879 | -8.15 | 6.7 | 7.15 | 0.843 | 0.861 | 0.839 | -6.01 | 7.07 | -7.62 | Very Poor_Mixed | 1938.2 | 2403.9 | 1.24 | 0.989 | 9.14 | 0.89 | 8.42 | 0.2096 | 0.6406 | 0.1541 | 0.3749 | 1 | 0.0993 | 0.2185 | 0.3767 | 0.3767 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
844 | 491.7 | 354 | 87.2 | 84.1 | 9.1 | 603.4 | 4514.2 | 51.9 | 27.7 | 87.3 | 85.1 | 79.2 | 93.6 | 37.5 | 18.1 | 7222.2 | 7721.5 | 6332.4 | 12556.7 | 13878.6 | 10523.3 | 1.739 | 1.797 | 1.662 | 0.684 | 0.608 | 0.632 | 4.5 | 4.36 | 4.43 | 0.548 | 0.62 | 0.558 | -2.53 | -3.31 | 3.2 | 0.531 | 0.569 | 0.556 | 4.05 | 4.14 | -2.9 | 0.625 | 0.572 | 0.658 | 2.74 | -4.44 | 3.44 | Fair_Mixed | 6332.4 | 10523.3 | 1.662 | 0.684 | 4.5 | 0.658 | 4.44 | 0.6396 | 0.8279 | 0.6301 | 0.8054 | 1 | 0.5818 | 0.6747 | 0.7254 | 0.7254 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
845 | 759.5 | 457.5 | 96.3 | 120.5 | 13.2 | 748.1 | 5354.3 | 42.7 | 37.1 | 92.7 | 91.7 | 83.4 | 97.2 | 40.2 | 24.4 | 5825.8 | 6353 | 6018.7 | 9090.8 | 10245 | 9409.8 | 1.56 | 1.613 | 1.563 | 0.713 | 0.745 | 0.763 | 5.6 | 5.51 | -6.19 | 0.698 | 0.65 | 0.68 | 4.9 | -4.87 | 3.05 | 0.697 | 0.638 | 0.708 | -4.72 | 4.35 | 4.37 | 0.576 | 0.641 | 0.633 | 5.41 | 5.08 | -4.71 | Poor_Mixed | 5825.8 | 9090.8 | 1.56 | 0.763 | 6.19 | 0.708 | 5.41 | 0.4994 | 0.7109 | 0.4875 | 0.6005 | 1 | 0.4105 | 0.5104 | 0.5983 | 0.5983 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
846 | 100 | 127.4 | 65 | 51.5 | 2 | 381.1 | 2500 | 58.2 | 23.5 | 77.8 | 78.8 | 71.3 | 81.1 | 35.6 | 10.8 | 9869.1 | 8932.5 | 8762.5 | 18609 | 16144.4 | 16286.1 | 1.886 | 1.807 | 1.859 | 0.551 | 0.501 | 0.532 | 2.46 | 2.04 | -2 | 0.512 | 0.547 | 0.519 | -2.63 | 2.65 | 2 | 0.509 | 0.5 | 0.534 | -2.59 | 2.27 | 2.38 | 0.501 | 0.505 | 0.52 | 2 | 2.05 | 2 | Good_Mixed | 8762.5 | 16144.4 | 1.807 | 0.551 | 2.46 | 0.547 | 2.65 | 0.92 | 0.8969 | 0.8913 | 0.9892 | 1 | 0.9006 | 0.889 | 0.9223 | 0.9223 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
847 | 1281.1 | 688.5 | 124.4 | 166.4 | 25.9 | 1142.4 | 7196.1 | 37.6 | 43.4 | 103.5 | 101.5 | 90.3 | 111.9 | 42.9 | 33.6 | 1898.5 | 3582.3 | 2125.3 | 2222.7 | 4835.8 | 2490.4 | 1.171 | 1.35 | 1.172 | 0.815 | 0.799 | 0.821 | 7 | 6.94 | 7.56 | 0.766 | 0.783 | 0.743 | 4.94 | 5.7 | -6.33 | 0.688 | 1.726 | 0.778 | -5.69 | -8.1 | 6.54 | 0.822 | 0.853 | 0.748 | 5.61 | 6.19 | -4.32 | Critical_Mixed | 1898.5 | 2222.7 | 1.171 | 0.821 | 7.56 | 1.726 | 8.1 | 0.2268 | 0.6455 | 0.2306 | 0.2591 | 1 | 0.2765 | 0.309 | 0.4245 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
848 | 382 | 247.5 | 79.6 | 67.6 | 1 | 518.3 | 3616.3 | 58.8 | 20.4 | 79.1 | 77 | 70 | 82.6 | 35.8 | 13.9 | 4563.2 | 4651.6 | 5125.3 | 5971.6 | 6909.2 | 7648.6 | 1.309 | 1.485 | 1.492 | 0.629 | 0.626 | 0.616 | 3.81 | 3.36 | 3.71 | 0.523 | 0.531 | 0.572 | 2.5 | 3.32 | -2.36 | 0.591 | 0.541 | 0.527 | 2.39 | -2 | 3.19 | 0.559 | 0.53 | 0.503 | 2.79 | -2.23 | -2.51 | Poor_IR_PI | 4563.2 | 5971.6 | 1.309 | 0.629 | 3.81 | 0.591 | 3.32 | 0.8752 | 0.9748 | 0.9048 | 0.9219 | 1 | 0.6486 | 0.7957 | 0.8664 | 0.8664 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
849 | 1707.5 | 982.4 | 143.1 | 190.2 | 34.3 | 1379 | 8603.6 | 56.1 | 26.5 | 80.8 | 82 | 77.7 | 87.1 | 37 | 14.5 | 7775.2 | 8410.7 | 7676.7 | 13884.6 | 15316.8 | 14026.4 | 1.786 | 1.821 | 1.827 | 0.571 | 0.563 | 0.509 | 3.24 | 3.17 | 16.07 | 0.526 | 0.512 | 0.526 | 2 | -2.52 | 2.66 | 0.5 | 0.5 | 0.513 | 3.15 | -2 | 2.49 | 0.5 | 0.539 | 0.567 | 2.52 | -2.6 | 3.01 | Critical_DGA | 7676.7 | 13884.6 | 1.786 | 0.571 | 16.07 | 0.567 | 3.15 | 0.0465 | 0.8458 | 0.7485 | 0.9067 | 1 | 0.6604 | 0.8709 | 0.6425 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
850 | 474.8 | 340.7 | 94.1 | 94.6 | 13.7 | 678 | 5250.4 | 54.1 | 26.9 | 82.2 | 84.1 | 77.7 | 87.7 | 38.5 | 19 | 7973.6 | 7778.2 | 8204.2 | 14175.4 | 13577.7 | 14601.8 | 1.778 | 1.746 | 1.78 | 0.687 | 0.621 | 0.673 | -5.34 | 3.84 | 4.37 | 0.637 | 0.59 | 0.563 | 4.11 | 3.41 | -4.3 | 0.551 | 0.581 | 0.582 | 3.36 | 3.91 | -4.39 | 0.597 | 0.551 | 0.591 | 2.94 | 2.24 | -3.6 | Fair_Mixed | 7778.2 | 13577.7 | 1.746 | 0.687 | 5.34 | 0.637 | 4.39 | 0.5712 | 0.8397 | 0.7093 | 0.778 | 1 | 0.5573 | 0.6623 | 0.7106 | 0.7106 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
851 | 1646.8 | 982.4 | 146.7 | 197 | 33.5 | 1379 | 8472.7 | 16.9 | 25.1 | 77.4 | 76.8 | 72.3 | 84.3 | 36.9 | 15.2 | 8903.1 | 9991 | 8914.9 | 16631.2 | 18827 | 17159.7 | 1.868 | 1.884 | 1.925 | 0.574 | 0.592 | 0.611 | 2.97 | 3.54 | 3.54 | 0.54 | 0.55 | 0.536 | 2.41 | -3.09 | 2.38 | 0.521 | 0.532 | 0.525 | 2.87 | 2.04 | 3.32 | 0.551 | 0.563 | 0.57 | 2.83 | 2.62 | 2.78 | Critical_DGA | 8903.1 | 16631.2 | 1.868 | 0.611 | 3.54 | 0.57 | 3.32 | 0.0476 | 0.285 | 0.884 | 0.8882 | 1 | 0.7042 | 0.7795 | 0.5778 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
852 | 408.3 | 242.5 | 75.5 | 73.4 | 3.5 | 529.5 | 3452.3 | 59.3 | 20 | 110.2 | 81.4 | 74 | 86.7 | 37.2 | 12.4 | 8881.4 | 8683.1 | 9354.2 | 16979.9 | 16018.2 | 18094.8 | 1.912 | 1.845 | 1.934 | 0.509 | 0.562 | 0.5 | 2.22 | 3.29 | -2.2 | 0.505 | 0.575 | 0.603 | 3.94 | 3.4 | 3.19 | 0.633 | 0.948 | 0.633 | 2.81 | 9.73 | 2.44 | 0.59 | 0.591 | 0.521 | 2.6 | -3.65 | 2.18 | Critical_Bushing_TD_Cap | 8683.1 | 16018.2 | 1.845 | 0.562 | 3.29 | 0.948 | 9.73 | 0.7688 | 1 | 0.5967 | 0.9575 | 1 | 0.8861 | 0.6286 | 0.817 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature | WTI_HV
853 | 220.2 | 142.9 | 67.3 | 59 | 1.7 | 478.2 | 3001 | 58.5 | 20 | 75 | 75 | 70.1 | 80 | 35 | 10 | 9908.6 | 9862.8 | 9469.1 | 19817.2 | 19725.6 | 18705.2 | 2 | 2 | 1.975 | 0.653 | 0.63 | 0.703 | -4.89 | -4.4 | 4.96 | 0.502 | 0.5 | 0.523 | 2 | 2.48 | 2.65 | 0.536 | 0.534 | 0.519 | 2.17 | 2.22 | -2.21 | 0.567 | 0.537 | 0.55 | -2.49 | 3.24 | -2.43 | Fair_Winding_TD_Cap | 9469.1 | 18705.2 | 1.975 | 0.703 | 4.96 | 0.567 | 3.24 | 0.8779 | 1 | 0.9979 | 1 | 1 | 0.5415 | 0.8393 | 0.8762 | 0.8762 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
854 | 1348.1 | 777.1 | 130.9 | 164 | 31.1 | 1174.3 | 7930 | 34.6 | 47.2 | 102.4 | 106.7 | 93.2 | 114.9 | 44.2 | 32.4 | 1741.5 | 2579.6 | 1473.2 | 1995 | 3179.1 | 1606.9 | 1.146 | 1.232 | 1.091 | 0.82 | 0.892 | 0.882 | 7.79 | 8.19 | 7.21 | 0.803 | 0.848 | 0.726 | -8.31 | -7.8 | 7.88 | 0.724 | 0.823 | 0.78 | 4.93 | 8.65 | 6.34 | 0.863 | 0.864 | 0.773 | 7.4 | 7.04 | 7.12 | Very Poor_Mixed | 1473.2 | 1606.9 | 1.091 | 0.892 | 8.19 | 0.864 | 8.65 | 0.1715 | 0.609 | 0.1669 | 0.3059 | 1 | 0.2076 | 0.2588 | 0.3836 | 0.3836 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
855 | 1654.8 | 953.7 | 143.7 | 187.7 | 34.3 | 1295.5 | 8331.4 | 35.6 | 45.9 | 106.5 | 107.9 | 92.6 | 114.4 | 45.5 | 31.5 | 1221.2 | 1774.5 | 690 | 1322.4 | 1887.8 | 1200 | 1.083 | 1.064 | 1.739 | 0.952 | 0.907 | 0.906 | -8.75 | 8.57 | 8.49 | 0.894 | 0.84 | 0.821 | -7.47 | 6.35 | 9.39 | 0.918 | 0.753 | 0.776 | 7.08 | 6.8 | -6.09 | 0.786 | 0.82 | 0.928 | 8.45 | 6.19 | 5.92 | Very Poor_Mixed | 690 | 1200 | 1.064 | 0.952 | 8.75 | 0.928 | 9.39 | 0.0676 | 0.6213 | 0.1337 | 0.3406 | 1 | 0.1221 | 0.2305 | 0.3404 | 0.3404 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
856 | 1087 | 587 | 115 | 129.6 | 20.7 | 819.6 | 6426.8 | 47.4 | 33.8 | 93.7 | 93.2 | 83.7 | 99.3 | 39.2 | 24.9 | 5124 | 6244.6 | 5478.9 | 7748.2 | 10208.8 | 8684.6 | 1.512 | 1.635 | 1.585 | 0.737 | 0.732 | 0.785 | 5.12 | 5.8 | 6.93 | 0.621 | 0.733 | 0.658 | 4.87 | 5.44 | -4.51 | 0.671 | 0.651 | 0.656 | 4.39 | 5.52 | -6.01 | 0.688 | 0.659 | 0.669 | -4.99 | 4.94 | 6.79 | Poor_Mixed | 5124 | 7748.2 | 1.512 | 0.785 | 6.93 | 0.733 | 6.79 | 0.3677 | 0.7485 | 0.4656 | 0.5831 | 1 | 0.3915 | 0.4717 | 0.5572 | 0.5572 | Poor | 0 | 1 | DGA | 0 |  | C2H2
857 | 452.9 | 322.5 | 81.8 | 71.5 | 1.3 | 545.1 | 3950.6 | 30.6 | 47 | 79.8 | 79.6 | 120.8 | 83.2 | 36.8 | 16.9 | 4784.3 | 4502.7 | 5226.4 | 7140.7 | 6278.5 | 7847.7 | 1.493 | 1.394 | 1.502 | 0.602 | 0.7 | 0.703 | 4.55 | 5.44 | 5.56 | 0.615 | 0.596 | 0.573 | 3.59 | 4.33 | 3.33 | 0.572 | 0.54 | 0.649 | 3.48 | 3.92 | 3.87 | 0.565 | 0.56 | 0.576 | -2.36 | 2.22 | -2.88 | Critical_Oil | 4502.7 | 6278.5 | 1.394 | 0.703 | 5.56 | 0.649 | 4.33 | 0.8087 | 0.6109 | 0.6652 | 0.8407 | 1 | 0.5123 | 0.6741 | 0.7371 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Moisture_PPM
858 | 1399 | 896.7 | 137.4 | 177 | 32.2 | 1290.3 | 7851 | 32.6 | 46.8 | 105.4 | 106.4 | 93.7 | 113.1 | 44.2 | 33.5 | 942.4 | 1982.8 | 1479.5 | 1200 | 2179.9 | 1623.6 | 1.273 | 1.099 | 1.097 | 0.936 | 0.915 | 0.933 | -9.28 | 8.56 | -8.64 | 0.821 | 0.951 | 0.822 | 8.23 | -6.73 | 6.15 | 0.869 | 0.902 | 0.842 | 4.95 | 8.03 | 6.01 | 0.767 | 0.757 | 0.682 | 6.77 | 6.9 | 5.65 | Very Poor_Mixed | 942.4 | 1200 | 1.097 | 0.936 | 9.28 | 0.951 | 8.23 | 0.1219 | 0.6128 | 0.1579 | 0.2631 | 1 | 0.1064 | 0.2609 | 0.3548 | 0.3548 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
859 | 150.2 | 257 | 68.2 | 69.9 | 1 | 486.1 | 2989.9 | 55.1 | 24.2 | 82.5 | 81.4 | 75.1 | 87.3 | 36.3 | 10.6 | 4862.4 | 5055.7 | 4294.1 | 7378.8 | 7002.5 | 6047.9 | 1.518 | 1.385 | 1.408 | 0.577 | 0.617 | 0.644 | 4.17 | -4.15 | 3.85 | 0.542 | 0.55 | 0.549 | 2.52 | -3.43 | -2 | 0.565 | 0.598 | 0.591 | -3.7 | 3.33 | 2.95 | 0.597 | 0.589 | 0.537 | 2.7 | -2 | 2.97 | Poor_IR_PI | 4294.1 | 6047.9 | 1.385 | 0.644 | 4.17 | 0.598 | 3.7 | 0.91 | 0.8839 | 0.7611 | 0.9925 | 1 | 0.6363 | 0.722 | 0.8383 | 0.8383 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
860 | 144.3 | 220.9 | 72 | 55.1 | 4.1 | 464.3 | 2881.1 | 59.2 | 24.3 | 76.3 | 75 | 70 | 80 | 35 | 14.4 | 10000 | 10000 | 9201.5 | 20000 | 20000 | 18355.3 | 2 | 2 | 1.995 | 0.534 | 0.587 | 0.531 | 2 | 3.46 | 2.33 | 0.527 | 0.5 | 0.5 | 2.3 | 2 | 2 | 0.5 | 0.512 | 0.5 | 2 | 2.59 | 2.26 | 0.503 | 0.52 | 0.5 | 2.04 | -2 | 2.28 | Good_Mixed | 9201.5 | 18355.3 | 1.995 | 0.587 | 3.46 | 0.527 | 2.59 | 0.8308 | 0.8821 | 0.9788 | 0.9092 | 1 | 0.8215 | 0.945 | 0.902 | 0.902 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
861 | 1589.5 | 940.3 | 141.4 | 187.9 | 31.9 | 1355.5 | 7955.3 | 34.8 | 44.6 | 102.4 | 102 | 92.5 | 110.9 | 42.8 | 31.1 | 2150.5 | 2084.1 | 2930.6 | 2570.7 | 2410.1 | 3678 | 1.195 | 1.156 | 1.255 | 0.962 | 0.914 | 0.962 | 9.38 | -8.74 | 9.18 | 0.823 | 0.765 | 0.724 | -7.12 | 8.23 | -5.8 | 0.889 | 0.731 | 0.878 | -6.29 | 7.03 | 7.92 | 0.827 | 0.864 | 0.867 | -6.58 | 6.11 | 5.54 | Very Poor_Mixed | 2084.1 | 2410.1 | 1.156 | 0.962 | 9.38 | 0.889 | 8.23 | 0.0842 | 0.6338 | 0.2271 | 0.3559 | 1 | 0.0805 | 0.2595 | 0.3556 | 0.3556 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
862 | 1478.5 | 792.9 | 133.9 | 162.3 | 30.2 | 1205.8 | 7247.4 | 36.5 | 71 | 100.8 | 100.6 | 89.6 | 109.5 | 42.4 | 34.5 | 2565.4 | 3743.6 | 2258.6 | 3328.4 | 4660.4 | 2552.1 | 1.297 | 1.245 | 1.13 | 0.894 | 0.887 | 0.847 | -8.03 | 8.44 | -7.55 | 0.801 | 0.694 | 0.633 | 7.16 | 5.78 | 7.09 | 0.671 | 0.843 | 0.788 | 5.16 | -6.15 | 7.34 | 0.809 | 0.8 | 0.715 | 5.47 | 7.71 | 7.35 | Critical_Mixed | 2258.6 | 2552.1 | 1.13 | 0.894 | 8.44 | 0.843 | 7.71 | 0.1686 | 0.5833 | 0.2708 | 0.2237 | 1 | 0.1848 | 0.335 | 0.3966 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
863 | 373.9 | 167.6 | 72.7 | 71.4 | 1.7 | 496.5 | 3143 | 53.7 | 28.1 | 80.2 | 81 | 75.3 | 84.6 | 36.5 | 11.8 | 6920.2 | 8179.2 | 494 | 11495.9 | 14483.4 | 591.9 | 1.661 | 1.771 | 1.198 | 0.605 | 0.558 | 0.592 | 4.4 | 3.88 | 3.31 | 0.513 | 0.5 | 0.923 | -3.58 | -2.92 | 8.22 | 0.521 | 0.595 | 0.628 | 2.74 | -3.46 | 2.35 | 0.5 | 0.517 | 0.654 | 4.31 | 2.29 | 3.76 | Critical_Bushing_TD_Cap | 494 | 591.9 | 1.198 | 0.605 | 4.4 | 0.923 | 8.22 | 0.8355 | 0.8221 | 0.7943 | 0.9703 | 0.85 | 0.6822 | 0.7011 | 0.7932 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
864 | 1094.7 | 574.9 | 110.2 | 128 | 25.6 | 958.3 | 6201.1 | 57.5 | 22.7 | 80.6 | 82.3 | 75 | 87.5 | 36.7 | 14.2 | 7830 | 8177.2 | 9041 | 13894.5 | 14940.4 | 16120.5 | 1.775 | 1.827 | 1.783 | 0.508 | 0.53 | 0.502 | 2 | -2.35 | 2.4 | 0.56 | 0.59 | 0.552 | 2.52 | 2.61 | 3.39 | 0.532 | 0.552 | 0.562 | -2.41 | -3.62 | 2.52 | 0.55 | 0.588 | 0.572 | -2.53 | -3.62 | 2.35 | Poor_DGA | 7830 | 13894.5 | 1.775 | 0.53 | 2.4 | 0.59 | 3.62 | 0.3329 | 0.9129 | 0.7671 | 0.9144 | 1 | 0.9226 | 0.7321 | 0.7361 | 0.7361 | Fair | 1 | 1 | DGA | 0 |  | C2H2
865 | 1101.5 | 664.1 | 116.9 | 138.4 | 21.5 | 876.7 | 6232 | 46.7 | 33 | 91.3 | 93 | 80.9 | 98.5 | 39.6 | 25.9 | 5084.9 | 6217.3 | 5257.1 | 7559.8 | 10056.1 | 8257.6 | 1.487 | 1.617 | 1.571 | 0.75 | 0.707 | 0.705 | 5.24 | 5.87 | 5.02 | 0.651 | 0.689 | 0.772 | 4.12 | -4.71 | -4.76 | 0.7 | 0.762 | 0.681 | 4.82 | -3.57 | 3.73 | 0.61 | 0.739 | 0.66 | 4.93 | -5.96 | 4.86 | Poor_Mixed | 5084.9 | 7559.8 | 1.487 | 0.75 | 5.87 | 0.772 | 5.96 | 0.3391 | 0.7581 | 0.5015 | 0.5478 | 1 | 0.4495 | 0.4637 | 0.5597 | 0.5597 | Poor | 0 | 1 | DGA | 0 |  | C2H2
866 | 819.9 | 529 | 98.7 | 109.4 | 17.8 | 813.5 | 5920.5 | 47.9 | 32.1 | 91.2 | 89.8 | 79.8 | 98.3 | 39.8 | 24 | 7161.8 | 5086.5 | 4892 | 12142.3 | 7534 | 7183.6 | 1.695 | 1.481 | 1.468 | 0.746 | 0.71 | 0.78 | 5.39 | 5.71 | 6.3 | 0.711 | 0.605 | 0.675 | 5.45 | 3.93 | 5.01 | 0.642 | 0.682 | 0.665 | 5.11 | 4.46 | -3.84 | 0.674 | 0.633 | 0.663 | 3.61 | 3.48 | 4.52 | Poor_Mixed | 4892 | 7183.6 | 1.468 | 0.78 | 6.3 | 0.711 | 5.45 | 0.4502 | 0.7691 | 0.5299 | 0.6143 | 1 | 0.4047 | 0.5131 | 0.5976 | 0.5976 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
867 | 1766 | 944.4 | 144.8 | 195.9 | 34.3 | 1299 | 8734.1 | 34 | 48 | 109.3 | 108.3 | 94 | 119.2 | 44.4 | 32.4 | 720.1 | 1011.5 | 1561.8 | 1200 | 1200 | 1670.2 | 1.666 | 1.186 | 1.069 | 0.961 | 0.925 | 0.99 | 9.04 | 9.84 | -9.57 | 0.819 | 0.941 | 0.825 | 5.33 | 6.75 | -6.5 | 0.853 | 0.739 | 0.815 | 6.67 | 6.7 | 5.48 | 0.779 | 0.716 | 0.851 | -8.87 | 6.4 | 8.1 | Very Poor_Mixed | 720.1 | 1200 | 1.069 | 0.99 | 9.84 | 0.941 | 8.87 | 0.0474 | 0.6016 | 0.0925 | 0.3059 | 1 | 0.0529 | 0.2623 | 0.3232 | 0.3232 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
868 | 391.3 | 284 | 83 | 75.1 | 8.7 | 552.6 | 4040.3 | 50.9 | 29.3 | 84.8 | 80.7 | 74.9 | 88.7 | 37.8 | 19.2 | 6792.1 | 7270.7 | 5964.4 | 11213.1 | 12295.7 | 9157.9 | 1.651 | 1.691 | 1.535 | 0.669 | 0.642 | 0.672 | 4.49 | 3.97 | 4.58 | 0.692 | 0.578 | 0.571 | 4.7 | 4.26 | 3.27 | 0.507 | 0.56 | 0.627 | 3.56 | 3.29 | 3.86 | 0.575 | 0.634 | 0.635 | 3.81 | 3.86 | 4.61 | Fair_Mixed | 5964.4 | 9157.9 | 1.535 | 0.672 | 4.58 | 0.692 | 4.7 | 0.6855 | 0.8054 | 0.7359 | 0.7718 | 1 | 0.5653 | 0.6332 | 0.7333 | 0.7333 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
869 | 587.9 | 330.7 | 90.1 | 89.6 | 4.3 | 655.8 | 3671.3 | 51.2 | 30.3 | 77.4 | 118.9 | 72.1 | 83 | 36.5 | 11.4 | 8320.5 | 8067.6 | 9639.6 | 15545.3 | 14567 | 17615.7 | 1.868 | 1.806 | 1.827 | 0.99 | 0.99 | 0.936 | 9.52 | 9.17 | 9.59 | 0.536 | 0.59 | 0.55 | 2.33 | 2.64 | 3.86 | 0.562 | 0.634 | 0.586 | 3.39 | 2.6 | 2.17 | 0.577 | 0.62 | 0.62 | 2.64 | 3.53 | -3.25 | Critical_Winding_TD_Cap | 8067.6 | 14567 | 1.806 | 0.99 | 9.59 | 0.634 | 3.86 | 0.6814 | 0.792 | 0.6714 | 0.9783 | 1 | 0.0468 | 0.6866 | 0.6716 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | C2H2
870 | 846.4 | 465.9 | 102.5 | 121.1 | 16 | 747 | 6039.4 | 59.8 | 21.2 | 78.2 | 75.4 | 71 | 80 | 35.4 | 11.2 | 10000 | 10000 | 9848.5 | 19912.2 | 19922.2 | 19674.7 | 1.991 | 1.992 | 1.998 | 0.565 | 0.539 | 0.57 | 2.05 | 2.45 | -3.2 | 0.516 | 0.517 | 0.546 | -2.17 | 2.11 | 2.09 | 0.546 | 0.52 | 0.535 | 2.83 | 2.3 | 2.49 | 0.561 | 0.509 | 0.522 | -2 | 2.23 | 2.88 | Fair_DGA | 9848.5 | 19674.7 | 1.991 | 0.57 | 3.2 | 0.561 | 2.88 | 0.4597 | 0.9486 | 0.9352 | 0.9821 | 1 | 0.8076 | 0.8335 | 0.7945 | 0.7945 | Fair | 1 | 1 | DGA | 0 |  | C2H2
871 | 331 | 269.1 | 80.9 | 61.4 | 3.8 | 577.6 | 3658.1 | 56 | 24 | 77.6 | 79.8 | 71.1 | 80.4 | 35.3 | 11.7 | 8943.5 | 9721.8 | 9618.7 | 16514 | 19012.3 | 18231.4 | 1.846 | 1.956 | 1.895 | 0.695 | 0.771 | 0.75 | 4.9 | 6.28 | -5.86 | 0.517 | 0.593 | 0.52 | -2.67 | 3.5 | 3.41 | 0.579 | 0.549 | 0.594 | 2.99 | 2.61 | 2.61 | 0.601 | 0.543 | 0.5 | 3.16 | 3.05 | 3.59 | Poor_Winding_TD_Cap | 8943.5 | 16514 | 1.846 | 0.771 | 6.28 | 0.601 | 3.59 | 0.7723 | 0.8875 | 0.891 | 0.9724 | 1 | 0.4175 | 0.7512 | 0.791 | 0.791 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
872 | 549.3 | 297 | 86.3 | 85.6 | 11.6 | 659 | 3977.1 | 53.9 | 26.6 | 83.4 | 82 | 75 | 88 | 38.1 | 14.9 | 7832.2 | 8043.7 | 8882.1 | 14791.6 | 14774.9 | 16398.9 | 1.889 | 1.837 | 1.846 | 0.583 | 0.605 | 0.607 | 3.39 | 3.56 | 3.4 | 0.55 | 0.554 | 0.584 | 3.39 | 4.15 | -3.18 | 0.529 | 0.537 | 0.54 | -3.2 | 2.74 | -2.7 | 0.582 | 0.579 | 0.575 | 3.23 | 3.07 | -3.2 | Fair_Mixed | 7832.2 | 14774.9 | 1.837 | 0.607 | 3.56 | 0.584 | 4.15 | 0.6155 | 0.8443 | 0.7367 | 0.8962 | 1 | 0.6897 | 0.722 | 0.7602 | 0.7602 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
873 | 1052 | 614.7 | 109.7 | 137.7 | 23.1 | 877.1 | 5451.5 | 47.7 | 30.8 | 91.3 | 93.8 | 83.1 | 98.1 | 40.3 | 25.6 | 5810.6 | 4679.4 | 6544.6 | 9098.4 | 6822.9 | 10261.4 | 1.566 | 1.458 | 1.568 | 0.764 | 0.739 | 0.78 | 6.22 | 5.6 | 6.45 | 0.67 | 0.696 | 0.68 | 4.36 | -3.21 | 5.43 | 0.764 | 0.741 | 0.65 | 4.44 | 5.41 | -4.16 | 0.664 | 0.699 | 0.661 | 4.15 | 5.46 | 4.69 | Poor_Mixed | 4679.4 | 6822.9 | 1.458 | 0.78 | 6.45 | 0.764 | 5.46 | 0.354 | 0.7855 | 0.4799 | 0.5584 | 1 | 0.3751 | 0.4677 | 0.5554 | 0.5554 | Poor | 0 | 1 | DGA | 0 |  | C2H2
874 | 225 | 168.7 | 66.6 | 55.9 | 1 | 350 | 2981.1 | 57.8 | 21.8 | 76.8 | 75 | 70.8 | 80.9 | 36 | 12.7 | 9892.9 | 10000 | 9726.4 | 19785.7 | 19820 | 18765 | 2 | 1.982 | 1.929 | 0.53 | 0.511 | 0.524 | 2.02 | 2.22 | -2.21 | 0.508 | 0.515 | 0.515 | 2.5 | 2.07 | 2 | 0.5 | 0.528 | 0.531 | 2 | -2 | -2.37 | 0.553 | 0.5 | 0.5 | -2 | 2.47 | -2.09 | Good_Mixed | 9726.4 | 18765 | 1.929 | 0.53 | 2.22 | 0.553 | 2.5 | 0.9617 | 0.9331 | 0.9536 | 0.9507 | 1 | 0.9048 | 0.9024 | 0.9444 | 0.9444 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
875 | 864.1 | 529.6 | 102.9 | 118.5 | 21.1 | 918 | 5352.3 | 47.2 | 32.1 | 93.1 | 92.8 | 83.3 | 96.1 | 39.4 | 26.6 | 4836 | 5997.5 | 5994 | 7523.6 | 9223.2 | 9229 | 1.556 | 1.538 | 1.54 | 0.751 | 0.701 | 0.77 | 6.15 | 4.65 | 5.82 | 0.619 | 0.705 | 0.702 | -5.14 | 4.6 | 3.73 | 0.682 | 0.591 | 0.596 | 5.09 | 3.8 | 4.01 | 0.755 | 0.651 | 0.658 | 4.58 | 5.41 | 3.77 | Poor_Mixed | 4836 | 7523.6 | 1.538 | 0.77 | 6.15 | 0.755 | 5.41 | 0.4082 | 0.7691 | 0.4892 | 0.5228 | 1 | 0.4235 | 0.512 | 0.5808 | 0.5808 | Poor | 0 | 1 | DGA | 0 |  | C2H2
876 | 905.3 | 546.3 | 111.6 | 124.7 | 19.8 | 859 | 5860.6 | 44.6 | 33.6 | 93.1 | 91.1 | 82.2 | 100.4 | 40.2 | 25.6 | 6360.4 | 6096.7 | 5706.4 | 10560.5 | 9641 | 9091 | 1.66 | 1.581 | 1.593 | 0.82 | 0.699 | 0.773 | 6.75 | -6.04 | 5.52 | 0.696 | 0.573 | 0.723 | 5.23 | -4.69 | 4.18 | 0.607 | 0.576 | 0.742 | 5.28 | 4.27 | 4.52 | 0.696 | 0.606 | 0.721 | -3.11 | -4.43 | 4.87 | Poor_Mixed | 5706.4 | 9091 | 1.581 | 0.82 | 6.75 | 0.742 | 5.28 | 0.4001 | 0.7509 | 0.4805 | 0.5584 | 1 | 0.3735 | 0.5163 | 0.5713 | 0.5713 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
877 | 1161.9 | 683.9 | 114.2 | 145.8 | 21.5 | 1057.5 | 6407.5 | 57.8 | 21 | 80.4 | 81 | 75 | 86 | 36.6 | 17.4 | 9380.8 | 8720.3 | 8752.6 | 18198.4 | 16292.5 | 16710.2 | 1.94 | 1.868 | 1.909 | 0.623 | 0.607 | 0.592 | 4.37 | 3.55 | 3.58 | 0.536 | 0.613 | 0.54 | 3.48 | 2.81 | 2.12 | 0.548 | 0.525 | 0.544 | 3.43 | -2.29 | -2.88 | 0.525 | 0.572 | 0.517 | 3.04 | -2.68 | 3.12 | Poor_DGA | 8720.3 | 16292.5 | 1.868 | 0.623 | 4.37 | 0.613 | 3.48 | 0.3042 | 0.9543 | 0.7873 | 0.8262 | 1 | 0.6552 | 0.7676 | 0.7005 | 0.7005 | Fair | 1 | 1 | DGA | 0 |  | C2H2
878 | 271 | 146.6 | 73.4 | 137.9 | 1 | 421.9 | 2676.2 | 58 | 20.3 | 107.3 | 105.9 | 95.1 | 116.8 | 44.7 | 11.2 | 7468.9 | 6821 | 6474.9 | 12558.5 | 11189.2 | 10772.3 | 1.681 | 1.64 | 1.664 | 0.647 | 1.887 | 0.568 | -4.29 | 3.34 | 2.89 | 0.581 | 0.596 | 0.542 | 2.47 | 3.08 | 2.45 | 0.576 | 0.614 | 0.552 | 3.02 | 2.85 | 4.06 | 0.618 | 0.608 | 0.611 | -2.38 | 3.05 | 2.87 | Critical_Thermal | 6474.9 | 10772.3 | 1.64 | 1.887 | 4.29 | 0.618 | 4.06 | 0.8483 | 0.9791 | 0.1202 | 0.9821 | 1 | 0.5705 | 0.6812 | 0.7532 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H4
879 | 928.2 | 519.6 | 102.9 | 116.3 | 17 | 867.7 | 5737.1 | 44.7 | 33.4 | 91 | 89.8 | 79.5 | 95.8 | 40.2 | 27.2 | 5968.6 | 5109.7 | 5774.8 | 9263.3 | 7912.1 | 8885.1 | 1.552 | 1.548 | 1.539 | 0.68 | 0.732 | 0.752 | -4.74 | 5.66 | -5.28 | 0.63 | 0.629 | 0.67 | -4.96 | 4.38 | 4.22 | 0.623 | 0.649 | 0.622 | 5 | 5.43 | 4.72 | 0.674 | 0.743 | 0.627 | 4.56 | 4.41 | 4.75 | Poor_Mixed | 5109.7 | 7912.1 | 1.539 | 0.752 | 5.66 | 0.743 | 5.43 | 0.4332 | 0.7532 | 0.5432 | 0.5011 | 1 | 0.4578 | 0.5127 | 0.5944 | 0.5944 | Poor | 0 | 1 | DGA | 0 |  | C2H2
880 | 1468.3 | 829.4 | 138.9 | 173.4 | 30.9 | 1219.1 | 8184.5 | 35.1 | 45.9 | 107.4 | 105.8 | 94 | 117.1 | 45.3 | 33.8 | 1610 | 1359.8 | 1068.6 | 1782.2 | 1583.1 | 1200 | 1.107 | 1.164 | 1.123 | 0.936 | 0.956 | 0.945 | -8.88 | -8.93 | 8.04 | 0.801 | 0.862 | 0.846 | 5.25 | 7.79 | 5.65 | 0.908 | 0.8 | 0.967 | 6.41 | 6.72 | 5.85 | 0.759 | 0.76 | 0.99 | 9.51 | 9.16 | 6 | Very Poor_Mixed | 1068.6 | 1200 | 1.107 | 0.956 | 8.93 | 0.99 | 9.51 | 0.1354 | 0.6213 | 0.1204 | 0.2513 | 1 | 0.105 | 0.2218 | 0.3476 | 0.3476 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
881 | 343.7 | 232.5 | 78.3 | 72.6 | 67.4 | 578.3 | 3328.6 | 57 | 23.4 | 84.5 | 85.5 | 78.3 | 92.3 | 37.6 | 14.1 | 6766.7 | 8044.5 | 8220.3 | 11627.6 | 14455.9 | 15383.3 | 1.718 | 1.797 | 1.871 | 0.898 | 0.927 | 0.949 | -8.55 | 9.22 | 9.83 | 0.5 | 0.524 | 0.538 | -2.66 | -2.64 | 2.2 | 0.558 | 0.557 | 0.546 | 2.33 | -3.46 | 2.89 | 0.513 | 0.52 | 0.5 | 2.13 | 2.6 | 3.14 | Critical_Winding_TD_Cap | 6766.7 | 11627.6 | 1.718 | 0.949 | 9.83 | 0.558 | 3.46 | 0.5478 | 0.8988 | 0.6594 | 0.9169 | 1 | 0.0901 | 0.8345 | 0.6794 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
882 | 433.6 | 319.3 | 85 | 89.6 | 8.8 | 593.4 | 4327.1 | 54 | 27.6 | 82.2 | 80.8 | 75.6 | 84 | 36.8 | 15.5 | 7514.3 | 9177.9 | 8030.3 | 12781.8 | 17406.2 | 14373.8 | 1.701 | 1.897 | 1.79 | 0.562 | 0.609 | 0.6 | 3.71 | 3.04 | 3.41 | 0.545 | 0.536 | 0.573 | 2.88 | 2.42 | 2.25 | 0.523 | 0.582 | 0.557 | 3.27 | 2.27 | 3.34 | 0.5 | 0.568 | 0.576 | -3.22 | 3.62 | 2.32 | Fair_Mixed | 7514.3 | 12781.8 | 1.701 | 0.609 | 3.71 | 0.582 | 3.62 | 0.6499 | 0.8293 | 0.7786 | 0.88 | 1 | 0.705 | 0.7658 | 0.7804 | 0.7804 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
883 | 1562 | 799.4 | 139.3 | 187.5 | 31.7 | 1153.7 | 7626.8 | 34.1 | 47.2 | 103.5 | 107.6 | 94.3 | 115.1 | 44.8 | 31.4 | 2670.5 | 2171 | 2204.7 | 3184.4 | 2594.8 | 2638.4 | 1.192 | 1.195 | 1.197 | 0.92 | 0.898 | 0.858 | 9.28 | 8.33 | -8.02 | 0.92 | 0.829 | 0.725 | 6.33 | 8.64 | -7.56 | 0.909 | 0.819 | 0.857 | -7.97 | 9.2 | 8.6 | 0.853 | 0.711 | 0.896 | 6.5 | 6.33 | 6.83 | Very Poor_Mixed | 2171 | 2594.8 | 1.192 | 0.92 | 9.28 | 0.92 | 9.2 | 0.1308 | 0.609 | 0.1442 | 0.3444 | 1 | 0.1461 | 0.2181 | 0.3571 | 0.3571 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
884 | 100 | 120 | 69.4 | 57.1 | 1.4 | 359.2 | 2936.9 | 59.5 | 20 | 75 | 75.4 | 71.2 | 81 | 35 | 10.3 | 8918.3 | 8751.4 | 9709.1 | 16979 | 16042.5 | 19172.5 | 1.904 | 1.833 | 1.975 | 0.5 | 0.507 | 0.569 | -2.23 | 2.05 | 3.57 | 0.5 | 0.509 | 0.553 | -2.08 | 2.27 | 2.87 | 0.5 | 0.524 | 0.5 | -2.39 | 2 | 2 | 0.516 | 0.53 | 0.522 | -2.44 | -2 | 2.07 | Good_Mixed | 8751.4 | 16042.5 | 1.833 | 0.569 | 3.57 | 0.553 | 2.87 | 0.9335 | 1 | 0.971 | 0.9968 | 1 | 0.8834 | 0.8963 | 0.9453 | 0.9453 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
885 | 1500.4 | 807.5 | 127.5 | 172.7 | 27.3 | 1173.4 | 7648.5 | 36.1 | 47.6 | 104.9 | 103.7 | 95.2 | 114.8 | 44.2 | 31.5 | 2049.4 | 2075.4 | 1630.9 | 2539 | 2445 | 1873.3 | 1.239 | 1.178 | 1.149 | 0.859 | 0.838 | 0.916 | 7.55 | 7.71 | 8.19 | 0.913 | 0.783 | 0.862 | 8.39 | 6.07 | 8.28 | 0.868 | 0.8 | 0.916 | 6.02 | -6.51 | -8.67 | 0.844 | 0.757 | 0.726 | 8.19 | 7.32 | 5.84 | Very Poor_Mixed | 1630.9 | 1873.3 | 1.149 | 0.916 | 8.19 | 0.916 | 8.67 | 0.1739 | 0.6053 | 0.1588 | 0.3406 | 1 | 0.1985 | 0.2322 | 0.3786 | 0.3786 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
886 | 352.8 | 214.5 | 75.3 | 73.7 | 4.3 | 426.9 | 2959.8 | 41 | 40.5 | 76.7 | 77.5 | 73.5 | 81.5 | 35 | 13 | 5644.3 | 7648.8 | 8068 | 9187.6 | 13425.4 | 13526.1 | 1.628 | 1.755 | 1.677 | 0.586 | 0.633 | 0.605 | -3.62 | 5.01 | 3.9 | 0.552 | 0.546 | 0.514 | 2.03 | -3.94 | 2.7 | 0.579 | 0.547 | 0.548 | -3.08 | 3.2 | 2.65 | 0.583 | 0.526 | 0.558 | 2.62 | 2.95 | -3.47 | Poor_Oil | 5644.3 | 9187.6 | 1.628 | 0.633 | 5.01 | 0.583 | 3.94 | 0.7837 | 0.6747 | 0.8962 | 0.9438 | 1 | 0.6344 | 0.7536 | 0.7982 | 0.7982 | Fair | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
887 | 192.1 | 130.4 | 66.6 | 62.6 | 2.6 | 371.1 | 3078.4 | 58.7 | 20 | 75 | 76.2 | 70.9 | 80 | 35 | 10.9 | 8749.2 | 10000 | 9670 | 16596 | 19533.3 | 18588.4 | 1.897 | 1.953 | 1.922 | 0.5 | 0.549 | 0.57 | 2 | -2.77 | 3.45 | 0.5 | 0.5 | 0.5 | 2.08 | 2.44 | 2 | 0.507 | 0.51 | 0.523 | 2 | -2 | 2.16 | 0.515 | 0.531 | 0.51 | 2 | 2.22 | 2 | Good_Mixed | 8749.2 | 16596 | 1.897 | 0.57 | 3.45 | 0.531 | 2.44 | 0.8716 | 1 | 0.968 | 0.9875 | 1 | 0.8434 | 0.9246 | 0.9286 | 0.9286 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
888 | 1336.8 | 848 | 126.2 | 167.6 | 34.3 | 1214.8 | 8442.5 | 34.9 | 46.8 | 105.2 | 106.4 | 95.4 | 114.5 | 45.5 | 34.8 | 884 | 1787.7 | 933.5 | 1200 | 1907.1 | 1200 | 1.357 | 1.067 | 1.285 | 0.974 | 0.968 | 0.95 | 9.4 | 9.84 | 9.16 | 0.83 | 0.952 | 0.911 | 7.94 | 7.82 | 6.36 | 0.834 | 0.85 | 0.953 | 6.65 | 8.6 | 5.05 | 0.918 | 0.729 | 0.77 | 5.48 | -6.81 | 8.59 | Very Poor_Mixed | 884 | 1200 | 1.067 | 0.974 | 9.84 | 0.953 | 8.6 | 0.1399 | 0.6128 | 0.133 | 0.2118 | 1 | 0.05 | 0.2122 | 0.3376 | 0.3376 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
889 | 1745.4 | 931.3 | 144.3 | 183 | 34 | 1203.1 | 8274.6 | 34.9 | 44.5 | 108.3 | 109.3 | 95.5 | 119.1 | 45.3 | 34 | 1699.1 | 1676.1 | 1415.4 | 1797.9 | 1817.3 | 1486.1 | 1.058 | 1.084 | 1.05 | 0.976 | 0.987 | 0.972 | -9.55 | 9.35 | 9.64 | 0.956 | 0.909 | 0.808 | 8.38 | 9.18 | 9.84 | 0.95 | 0.773 | 0.899 | 6.44 | 6.84 | -8.63 | 0.835 | 0.761 | 0.808 | 9.4 | 7.89 | 8.52 | Very Poor_Mixed | 1415.4 | 1486.1 | 1.05 | 0.987 | 9.64 | 0.956 | 9.84 | 0.0792 | 0.6347 | 0.0781 | 0.2434 | 1 | 0.0382 | 0.1739 | 0.3126 | 0.3126 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
890 | 863.6 | 486.4 | 106.7 | 118.5 | 14.9 | 777.3 | 5950.9 | 58.5 | 24.6 | 77.5 | 77.2 | 70.7 | 83.2 | 35.2 | 12.6 | 9608 | 9610.7 | 9306.2 | 17792.4 | 19221.4 | 18496.8 | 1.852 | 2 | 1.988 | 0.513 | 0.549 | 0.586 | 2.59 | 2.11 | 2.63 | 0.5 | 0.58 | 0.557 | 2.11 | 2.47 | 2.79 | 0.506 | 0.545 | 0.5 | 2.44 | -2.42 | -2.13 | 0.528 | 0.524 | 0.528 | 2.8 | 2.55 | -3.18 | Fair_DGA | 9306.2 | 17792.4 | 1.852 | 0.586 | 2.63 | 0.58 | 3.18 | 0.46 | 0.8768 | 0.9076 | 0.953 | 1 | 0.8348 | 0.8402 | 0.7868 | 0.7868 | Fair | 1 | 1 | DGA | 0 |  | C2H2
891 | 816.4 | 554.4 | 105.9 | 114.4 | 19.7 | 838.9 | 5405.1 | 57.5 | 23.6 | 78.4 | 79.9 | 74.9 | 85.2 | 36.9 | 15.6 | 9051 | 9036.2 | 9731.6 | 17529.3 | 16849.2 | 18380 | 1.937 | 1.865 | 1.889 | 0.551 | 0.534 | 0.58 | 2.19 | 3.22 | 3.32 | 0.53 | 0.508 | 0.545 | 2.53 | 2 | 2 | 0.5 | 0.56 | 0.5 | 2.13 | 2.22 | 2.36 | 0.553 | 0.545 | 0.563 | -2.54 | 2.33 | 2.99 | Poor_DGA | 9036.2 | 16849.2 | 1.865 | 0.58 | 3.32 | 0.563 | 2.99 | 0.4283 | 0.895 | 0.818 | 0.8773 | 1 | 0.7884 | 0.8399 | 0.7617 | 0.7617 | Fair | 1 | 1 | DGA | 0 |  | C2H2
892 | 849.4 | 586.3 | 102.7 | 118.8 | 17.2 | 784.5 | 5093.4 | 41.8 | 34.2 | 88.6 | 93.5 | 83.6 | 97 | 40.4 | 27 | 4852.6 | 5710.2 | 5680.6 | 6980.8 | 8992.3 | 8549.1 | 1.439 | 1.575 | 1.505 | 0.758 | 0.683 | 0.74 | 5.47 | -5.16 | 5.91 | 0.717 | 0.751 | 0.653 | 4.41 | 4.81 | -4.96 | 0.751 | 0.685 | 0.68 | 4.43 | -5.41 | -6.04 | 0.705 | 0.712 | 0.682 | 4.22 | 4.01 | 5.2 | Poor_Mixed | 4852.6 | 6980.8 | 1.439 | 0.758 | 5.91 | 0.751 | 6.04 | 0.4454 | 0.7438 | 0.5014 | 0.5083 | 1 | 0.4367 | 0.4435 | 0.5771 | 0.5771 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
893 | 510.3 | 359.2 | 92.2 | 102.1 | 13.5 | 641.1 | 4605.9 | 49.2 | 29.8 | 86.7 | 92.9 | 83 | 96.6 | 38 | 18.7 | 6427 | 6745 | 7155.6 | 10448 | 11268.6 | 11461.4 | 1.626 | 1.671 | 1.602 | 0.682 | 0.671 | 0.657 | -4.74 | -4.91 | 4.29 | 0.577 | 0.581 | 0.621 | 3.6 | 3.03 | 3.7 | 0.586 | 0.631 | 0.596 | 3.3 | -4.43 | 3.58 | 0.64 | 0.678 | 0.63 | 4.77 | 4.17 | -4.21 | Fair_Mixed | 6427 | 10448 | 1.602 | 0.682 | 4.91 | 0.678 | 4.77 | 0.572 | 0.7986 | 0.539 | 0.7872 | 1 | 0.5385 | 0.5971 | 0.675 | 0.675 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
894 | 100 | 166.7 | 66.1 | 50 | 1.6 | 351 | 2762.8 | 48.1 | 31.2 | 79.8 | 82.6 | 73.3 | 86.6 | 36.8 | 11.8 | 8024.4 | 7067.1 | 8781.4 | 14600.5 | 12361.4 | 16512.2 | 1.82 | 1.749 | 1.88 | 0.525 | 0.577 | 0.529 | 2.62 | -3.31 | 2.66 | 0.503 | 0.502 | 0.5 | 2.17 | 2 | 2 | 0.515 | 0.518 | 0.5 | 2 | -2.16 | -2.25 | 0.525 | 0.502 | 0.521 | -2.24 | -2 | 2.27 | Fair_Oil | 7067.1 | 12361.4 | 1.749 | 0.577 | 3.31 | 0.525 | 2.27 | 0.94 | 0.7804 | 0.7891 | 0.9703 | 1 | 0.8105 | 0.9262 | 0.8963 | 0.8963 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
895 | 1411.1 | 880.8 | 136.1 | 178.4 | 29 | 1238 | 8111.8 | 33.2 | 49 | 109.2 | 109.3 | 95.4 | 115.2 | 44.7 | 30.8 | 1091.2 | 1528.7 | 1578.8 | 1222.4 | 1839.1 | 1754.4 | 1.12 | 1.203 | 1.111 | 0.956 | 0.95 | 0.94 | -9.55 | 8.78 | -8.28 | 0.857 | 0.774 | 0.836 | 7.7 | 6.7 | 7.17 | 0.888 | 0.766 | 0.891 | 8.19 | -6.39 | 9.52 | 0.741 | 0.724 | 0.889 | -8.86 | 6.24 | 9.84 | Very Poor_Mixed | 1091.2 | 1222.4 | 1.111 | 0.956 | 9.55 | 0.891 | 9.84 | 0.1397 | 0.5924 | 0.0977 | 0.3673 | 1 | 0.0902 | 0.2241 | 0.3471 | 0.3471 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
896 | 913.3 | 425.6 | 94.1 | 117.9 | 19 | 823.3 | 4910.4 | 44.6 | 36.1 | 88.8 | 94.4 | 80.8 | 99.6 | 39.3 | 24.4 | 6310.1 | 5429 | 5697.6 | 10034.2 | 8203.6 | 9110.8 | 1.59 | 1.511 | 1.599 | 0.767 | 0.72 | 0.674 | 5.93 | 6.12 | 5.47 | 0.667 | 0.674 | 0.671 | -4.07 | 4.08 | 6.11 | 0.752 | 0.727 | 0.685 | 5.64 | 5.84 | 6.66 | 0.704 | 0.688 | 0.688 | 4.75 | 3.57 | 4.74 | Poor_Mixed | 5429 | 8203.6 | 1.511 | 0.767 | 6.12 | 0.752 | 6.66 | 0.4511 | 0.722 | 0.5064 | 0.6005 | 1 | 0.4248 | 0.4462 | 0.5799 | 0.5799 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
897 | 1351.7 | 751 | 126.8 | 155.6 | 28.4 | 1066.6 | 6955.3 | 41.4 | 40.5 | 103.5 | 104 | 89.8 | 110.3 | 43.2 | 34 | 2773.7 | 2695 | 3544.9 | 3419.5 | 3385.2 | 4776.6 | 1.233 | 1.256 | 1.347 | 0.834 | 0.829 | 0.81 | 8.21 | 7.35 | -7.33 | 0.705 | 0.78 | 1.909 | 6.56 | 6.62 | 6.18 | 0.75 | 0.819 | 0.76 | 7.08 | -4.98 | 5.67 | 0.778 | 0.721 | 0.85 | 5.53 | -5.33 | 5.71 | Critical_Mixed | 2695 | 3385.2 | 1.233 | 0.834 | 8.21 | 1.909 | 7.08 | 0.2215 | 0.6747 | 0.2252 | 0.2434 | 1 | 0.2426 | 0.3094 | 0.4207 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
898 | 951.2 | 530.3 | 103.8 | 120.4 | 18.4 | 883.3 | 5268.7 | 45.8 | 33.9 | 91.9 | 90.1 | 82.8 | 98 | 40.1 | 24.8 | 5753 | 5836.2 | 5420.7 | 8551.1 | 9242.2 | 8356.8 | 1.486 | 1.584 | 1.542 | 0.7 | 0.676 | 0.657 | 5.21 | -4.73 | 4.82 | 0.707 | 0.666 | 0.641 | -5.13 | -4.05 | 4.99 | 0.71 | 0.732 | 0.688 | 5.2 | 3.49 | 4.78 | 0.736 | 0.648 | 0.743 | 4.98 | 3.88 | 4.65 | Poor_Mixed | 5420.7 | 8356.8 | 1.486 | 0.7 | 5.21 | 0.743 | 5.2 | 0.4197 | 0.7473 | 0.5035 | 0.5865 | 1 | 0.5153 | 0.4622 | 0.5896 | 0.5896 | Poor | 0 | 1 | DGA | 0 |  | C2H2
899 | 1610.2 | 899.5 | 142.1 | 188 | 33.7 | 1281.1 | 8196.1 | 35.7 | 45.7 | 106.7 | 107.6 | 97.2 | 115.3 | 44.5 | 34.1 | 2457.3 | 1912.6 | 1954.5 | 2805 | 2191.6 | 2203.8 | 1.141 | 1.146 | 1.128 | 0.886 | 0.938 | 0.932 | 8.3 | 8.44 | 9.02 | 0.797 | 0.958 | 0.799 | 6.82 | 8.01 | 7.93 | 0.984 | 0.899 | 0.767 | 8.1 | 7.35 | 7.04 | 0.803 | 0.87 | 0.853 | 8.03 | 8.08 | -8.79 | Very Poor_Mixed | 1912.6 | 2191.6 | 1.128 | 0.938 | 9.02 | 0.984 | 8.79 | 0.0836 | 0.6232 | 0.1116 | 0.2395 | 1 | 0.1251 | 0.1879 | 0.3301 | 0.3301 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
900 | 1530.3 | 831.1 | 137.9 | 184.4 | 33.2 | 1259.6 | 7619.1 | 35.6 | 43.3 | 106.8 | 108 | 93.7 | 115 | 44.6 | 31.1 | 1642.6 | 1869.9 | 1894.5 | 1788.3 | 1973.2 | 2033.2 | 1.089 | 1.055 | 1.073 | 0.912 | 0.935 | 0.968 | 9.07 | 9.44 | 9.35 | 0.775 | 0.922 | 0.945 | 7.37 | 9.16 | -7.92 | 0.879 | 0.854 | 0.807 | 8.92 | 6.41 | 5.97 | 0.753 | 0.788 | 0.73 | 7.9 | -8.03 | 6.99 | Very Poor_Mixed | 1642.6 | 1788.3 | 1.055 | 0.968 | 9.44 | 0.945 | 9.16 | 0.115 | 0.6465 | 0.129 | 0.3559 | 1 | 0.0763 | 0.2221 | 0.3477 | 0.3477 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
901 | 1536.3 | 850.9 | 136.5 | 177.5 | 33.7 | 1241.2 | 7196.9 | 33.9 | 45.8 | 102.7 | 98.6 | 92.4 | 111.9 | 43.5 | 32.2 | 2559.5 | 1535.3 | 1384 | 3057.4 | 1811.4 | 1493.2 | 1.195 | 1.18 | 1.079 | 0.902 | 0.892 | 0.937 | -9.11 | -8.21 | 8.25 | 0.818 | 0.856 | 0.881 | 8.02 | 6.45 | -8.43 | 0.754 | 0.886 | 0.81 | 6.92 | 4.82 | 5.54 | 0.801 | 0.836 | 0.91 | 7.19 | -6.25 | 8.23 | Very Poor_Mixed | 1384 | 1493.2 | 1.079 | 0.937 | 9.11 | 0.91 | 8.43 | 0.1243 | 0.6222 | 0.2358 | 0.3137 | 1 | 0.1341 | 0.2352 | 0.3661 | 0.3661 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
902 | 775 | 489.8 | 101.1 | 114.3 | 13.4 | 738.8 | 5200.4 | 49.8 | 29.4 | 87.8 | 87.8 | 81.5 | 94.3 | 39.2 | 22.6 | 6634.8 | 6920.1 | 7353 | 10515.3 | 11579.7 | 12607.1 | 1.585 | 1.673 | 1.715 | 0.707 | 0.679 | 0.69 | -5.51 | 5.17 | 5.04 | 0.631 | 0.645 | 0.643 | 4.34 | -3.66 | 5.8 | 0.653 | 0.599 | 0.656 | 4.06 | 3.91 | -4.43 | 0.609 | 0.63 | 0.641 | -4.69 | -5.01 | 4.97 | Poor_Mixed | 6634.8 | 10515.3 | 1.585 | 0.707 | 5.51 | 0.656 | 5.8 | 0.4985 | 0.804 | 0.5788 | 0.6619 | 1 | 0.4832 | 0.5421 | 0.6373 | 0.6373 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
903 | 100 | 120 | 66 | 64.5 | 1 | 409.6 | 2500 | 56.7 | 20 | 76.1 | 78 | 73.3 | 81.5 | 36.8 | 11.2 | 10000 | 8480.4 | 9909.8 | 18498.6 | 16600.1 | 19084.7 | 1.85 | 1.957 | 1.926 | 0.561 | 0.507 | 0.5 | 3.69 | 2 | -2 | 0.524 | 0.547 | 0.58 | -2.49 | -2.96 | 3.12 | 0.531 | 0.5 | 0.561 | -2.85 | 2.64 | 2 | 0.5 | 0.749 | 0.566 | 2.4 | 4.01 | -3.19 | Fair_Bushing_TD_Cap | 8480.4 | 16600.1 | 1.85 | 0.561 | 3.69 | 0.749 | 4.01 | 0.9578 | 1 | 0.8922 | 0.9821 | 1 | 0.8944 | 0.768 | 0.9212 | 0.9212 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_TV_Y_TanDelta_pct
904 | 1573.9 | 926.9 | 147.4 | 175.7 | 32 | 1321.4 | 8468.5 | 35.5 | 45.1 | 105.3 | 105.4 | 92.6 | 114 | 45.2 | 32.4 | 2760 | 1236.2 | 1475.3 | 3418.9 | 1354.9 | 1789.2 | 1.239 | 1.096 | 1.213 | 0.942 | 0.977 | 0.962 | 8.86 | 9.38 | -8.98 | 0.971 | 0.743 | 0.816 | 8.04 | 8.88 | 7.95 | 0.947 | 0.808 | 0.77 | 5.64 | -8.77 | 5.94 | 0.756 | 0.918 | 0.984 | 6.65 | -8.76 | 6.21 | Very Poor_Mixed | 1236.2 | 1354.9 | 1.096 | 0.977 | 9.38 | 0.984 | 8.88 | 0.0886 | 0.6289 | 0.1583 | 0.3059 | 1 | 0.0721 | 0.2042 | 0.3356 | 0.3356 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
905 | 851.9 | 516.5 | 103.1 | 119.1 | 15.8 | 772.6 | 5111.5 | 46.2 | 33.8 | 91.5 | 86.5 | 83.2 | 99.9 | 39.2 | 25.7 | 4883.7 | 5383 | 6565.3 | 7305.2 | 8104.6 | 10187 | 1.496 | 1.506 | 1.552 | 0.762 | 0.766 | 0.741 | -6.37 | 5.85 | 6.81 | 0.752 | 0.655 | 0.656 | -4.95 | 6.76 | 3.85 | 0.684 | 0.712 | 0.709 | 4.64 | 4.95 | 4.28 | 0.762 | 0.788 | 0.744 | 4.79 | 5.7 | -4.96 | Poor_Mixed | 4883.7 | 7305.2 | 1.496 | 0.766 | 6.81 | 0.788 | 6.76 | 0.4629 | 0.7485 | 0.5244 | 0.5549 | 1 | 0.3652 | 0.4232 | 0.573 | 0.573 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
906 | 1052.5 | 518 | 105.1 | 120.8 | 16.9 | 849.7 | 5568.4 | 48.7 | 31.2 | 93.4 | 92.7 | 83.1 | 99.7 | 39.9 | 26.7 | 5763.4 | 6539.7 | 5641.8 | 8793.9 | 10281.8 | 8810.8 | 1.526 | 1.572 | 1.562 | 0.715 | 0.758 | 0.688 | 6.11 | 6.09 | 5.99 | 0.655 | 0.722 | 0.633 | -5.18 | 3.76 | 5.24 | 0.639 | 0.662 | 0.603 | 6.14 | 4.67 | 5.21 | 0.694 | 0.64 | 0.71 | 4.24 | 4.94 | 4.88 | Poor_Mixed | 5641.8 | 8793.9 | 1.526 | 0.758 | 6.11 | 0.722 | 6.14 | 0.4224 | 0.7804 | 0.468 | 0.5192 | 1 | 0.412 | 0.4925 | 0.5783 | 0.5783 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
907 | 492 | 270.9 | 84.8 | 66.9 | 2.8 | 548.4 | 3412.6 | 34.6 | 87 | 87.2 | 84.3 | 78.6 | 90.5 | 37.2 | 13.6 | 5323.3 | 5914.9 | 5949.5 | 8162.6 | 9868.2 | 9557.4 | 1.533 | 1.668 | 1.606 | 0.671 | 0.572 | 0.61 | 5.06 | 3.31 | -3.69 | 0.559 | 0.536 | 0.533 | 3.39 | 3.44 | 3.22 | 0.622 | 0.594 | 0.625 | -2.18 | -2.35 | 3.3 | 0.615 | 0.526 | 0.563 | -2.65 | 2.07 | -3.51 | Critical_Oil | 5323.3 | 8162.6 | 1.533 | 0.671 | 5.06 | 0.625 | 3.51 | 0.7718 | 0.5833 | 0.658 | 0.9294 | 1 | 0.6355 | 0.7121 | 0.7524 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
908 | 521.5 | 409.9 | 84.9 | 90.8 | 14.5 | 620.8 | 4437.5 | 52 | 29.1 | 86.8 | 87 | 77.9 | 91.7 | 38.5 | 20.4 | 7282.6 | 6864.5 | 6986.7 | 12300.7 | 11389.8 | 11672.3 | 1.689 | 1.659 | 1.671 | 0.617 | 0.679 | 0.639 | 4.22 | -4.36 | 4.62 | 0.596 | 0.588 | 0.576 | 3.56 | 2.91 | 4.06 | 0.63 | 0.665 | 0.626 | 4.1 | 4.49 | 3.89 | 0.633 | 0.575 | 0.576 | 3.68 | 4.37 | -4.33 | Fair_Mixed | 6864.5 | 11389.8 | 1.659 | 0.679 | 4.62 | 0.665 | 4.49 | 0.5794 | 0.8081 | 0.6327 | 0.734 | 1 | 0.5792 | 0.607 | 0.6922 | 0.6922 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
909 | 1682.9 | 885.7 | 137.8 | 172.9 | 46.6 | 1349 | 8106.1 | 51.2 | 27.3 | 77.5 | 79.9 | 73.5 | 81.2 | 36.1 | 14.4 | 8206.9 | 7082.6 | 9743 | 15095.7 | 12841.8 | 19234.9 | 1.839 | 1.813 | 1.974 | 0.571 | 0.561 | 0.556 | 2.92 | 3.24 | -4.05 | 0.646 | 0.579 | 0.613 | 3.48 | -3.82 | -3.2 | 0.569 | 0.653 | 0.58 | 2.46 | -3.88 | 2.82 | 0.693 | 0.633 | 0.586 | 3.76 | -4.39 | 4.79 | Critical_DGA | 7082.6 | 12841.8 | 1.813 | 0.571 | 4.05 | 0.693 | 4.79 | 0.0841 | 0.8337 | 0.862 | 0.9092 | 1 | 0.7411 | 0.6073 | 0.6258 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
910 | 1170.1 | 768.1 | 123 | 153.5 | 25.6 | 1094.6 | 7161.7 | 57.2 | 23.4 | 78.2 | 77.2 | 72.4 | 83.4 | 35 | 11.7 | 9662.5 | 9405 | 9232.6 | 19325 | 18029.4 | 17900 | 2 | 1.917 | 1.939 | 0.522 | 0.539 | 0.561 | 2.15 | 2.33 | 2.58 | 0.521 | 0.534 | 0.501 | -2.68 | -2.56 | 2.39 | 0.531 | 0.527 | 0.569 | -2.93 | 2.68 | 2.98 | 0.528 | 0.525 | 0.542 | 2.51 | 2.71 | 3.18 | Poor_DGA | 9232.6 | 17900 | 1.917 | 0.561 | 2.58 | 0.569 | 3.18 | 0.2459 | 0.8988 | 0.8835 | 0.9724 | 1 | 0.8512 | 0.8126 | 0.7317 | 0.7317 | Fair | 1 | 1 | DGA | 0 |  | C2H2
911 | 1695.4 | 982.4 | 144.5 | 183.2 | 34.3 | 1379 | 8749.1 | 33.9 | 46.3 | 104.2 | 103.5 | 95.7 | 115.4 | 44.9 | 32.8 | 1414.6 | 1746.8 | 749.4 | 1545.1 | 1897.3 | 1200 | 1.092 | 1.086 | 1.601 | 0.95 | 0.971 | 0.982 | 8.94 | 9.5 | 9.84 | 0.966 | 0.786 | 0.876 | 6.41 | -8.5 | 7.33 | 0.879 | 0.773 | 0.911 | 5.97 | 9.17 | -8.83 | 0.767 | 0.843 | 0.795 | -7.81 | 7.21 | 7.08 | Very Poor_Mixed | 749.4 | 1200 | 1.086 | 0.982 | 9.84 | 0.966 | 9.17 | 0.05 | 0.6175 | 0.153 | 0.2904 | 1 | 0.0496 | 0.208 | 0.3208 | 0.3208 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
912 | 1652.2 | 936.5 | 135.6 | 193.8 | 39.6 | 1330 | 8712.8 | 54.2 | 26.2 | 78.1 | 79.7 | 70 | 84.7 | 35.8 | 13.3 | 7393.6 | 7129.9 | 7786.5 | 13354.3 | 11617.4 | 13440.4 | 1.806 | 1.629 | 1.726 | 0.586 | 0.587 | 0.57 | 3.93 | -2.83 | 4.08 | 0.591 | 0.581 | 0.522 | 3.18 | 2.69 | 2.27 | 0.535 | 0.583 | 0.585 | 3.43 | 2.56 | 2.49 | 0.601 | 0.664 | 0.544 | 3.04 | 3.1 | 2.9 | Critical_DGA | 7129.9 | 11617.4 | 1.629 | 0.587 | 4.08 | 0.664 | 3.43 | 0.0593 | 0.8505 | 0.8775 | 0.9367 | 1 | 0.7025 | 0.7066 | 0.637 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
913 | 163.7 | 120 | 65.1 | 79.6 | 1 | 387.1 | 3148.7 | 57.7 | 20.6 | 86.5 | 89.6 | 79.6 | 94.5 | 39 | 12.8 | 9862.2 | 8922.9 | 10000 | 19724.4 | 17283.7 | 19935.5 | 2 | 1.937 | 1.994 | 0.516 | 0.58 | 0.537 | -2.1 | -2.81 | -2.39 | 0.553 | 0.534 | 0.546 | 2.58 | 2 | 2.37 | 0.553 | 0.557 | 0.542 | -2.21 | 2.8 | 2 | 0.543 | 0.5 | 0.5 | 2.65 | 2.03 | 2.2 | Poor_Thermal | 8922.9 | 17283.7 | 1.937 | 0.58 | 2.81 | 0.557 | 2.8 | 0.9314 | 0.9672 | 0.5884 | 0.9484 | 1 | 0.8428 | 0.8318 | 0.8829 | 0.8829 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_LV
914 | 100 | 120 | 78.7 | 63.2 | 2.9 | 466 | 3342.7 | 58.8 | 22.4 | 76 | 76.8 | 73.2 | 80.6 | 37.1 | 11.1 | 5642 | 5049.3 | 6438.6 | 8854.1 | 7694.7 | 10246.2 | 1.569 | 1.524 | 1.591 | 0.611 | 0.624 | 0.637 | -3.48 | -4.24 | 4.69 | 0.517 | 0.515 | 0.5 | 2.81 | 2.69 | -2 | 0.518 | 0.577 | 0.528 | -2.49 | 2 | 2.6 | 0.524 | 0.561 | 0.503 | 2.38 | -2.02 | 3.22 | Fair_IR_PI | 5049.3 | 7694.7 | 1.524 | 0.637 | 4.69 | 0.577 | 3.22 | 0.8512 | 0.9193 | 0.9098 | 0.984 | 1 | 0.6175 | 0.8482 | 0.8624 | 0.8624 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
915 | 979.3 | 527.8 | 106.1 | 120.4 | 21.5 | 892.6 | 5938.2 | 46.7 | 32.3 | 89.8 | 90.1 | 81.7 | 96.6 | 39.3 | 24.8 | 6453.9 | 5997.3 | 5169 | 9955.5 | 9537.1 | 7607.1 | 1.543 | 1.59 | 1.472 | 0.727 | 0.758 | 0.671 | 5.69 | 5.96 | 6.01 | 0.6 | 0.676 | 0.809 | 4.36 | -4.24 | -5.43 | 0.598 | 0.761 | 0.78 | 5.91 | 4.88 | -4.51 | 0.656 | 0.714 | 0.673 | -3.78 | -5.89 | 4.08 | Poor_Mixed | 5169 | 7607.1 | 1.472 | 0.758 | 6.01 | 0.809 | 5.91 | 0.3898 | 0.7666 | 0.5363 | 0.5865 | 1 | 0.4236 | 0.4603 | 0.5746 | 0.5746 | Poor | 0 | 1 | DGA | 0 |  | C2H2
916 | 835.7 | 476.6 | 108.5 | 117.7 | 18.6 | 833 | 5523.8 | 55.5 | 23.4 | 77.4 | 78.4 | 72.8 | 84.9 | 36.9 | 10.8 | 9198.1 | 9030.3 | 9542.4 | 18064.5 | 17284.4 | 18989.9 | 1.964 | 1.914 | 1.99 | 0.521 | 0.569 | 0.5 | 2.14 | 2.87 | 2.29 | 0.53 | 0.5 | 0.543 | 2.14 | 2.27 | -2.75 | 0.548 | 0.5 | 0.573 | -2.29 | 2.4 | 3.16 | 0.513 | 0.555 | 0.51 | 2.61 | -2.31 | -2 | Fair_DGA | 9030.3 | 17284.4 | 1.914 | 0.569 | 2.87 | 0.573 | 3.16 | 0.4364 | 0.8988 | 0.8601 | 0.9892 | 1 | 0.8813 | 0.8445 | 0.7878 | 0.7878 | Fair | 1 | 1 | DGA | 0 |  | C2H2
917 | 712.9 | 441.2 | 100.6 | 112.4 | 11.3 | 734.6 | 5363.3 | 47.3 | 30.7 | 86.3 | 89.3 | 78.4 | 94.5 | 38.9 | 22.3 | 7291.2 | 7434 | 6510.9 | 11932.9 | 12969.3 | 10649.5 | 1.637 | 1.745 | 1.636 | 0.705 | 0.694 | 0.726 | -5.43 | 5.47 | 5.72 | 0.626 | 0.654 | 0.622 | 4.27 | -4.59 | 3.78 | 0.601 | 0.622 | 0.601 | 4.17 | -4.47 | -2.68 | 0.719 | 0.583 | 0.706 | 4.96 | 4.05 | 3.28 | Poor_Mixed | 6510.9 | 10649.5 | 1.636 | 0.726 | 5.72 | 0.719 | 4.96 | 0.5264 | 0.7868 | 0.6006 | 0.6719 | 1 | 0.4512 | 0.5615 | 0.6439 | 0.6439 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
918 | 831.2 | 425.7 | 104.3 | 125.7 | 16.4 | 942.7 | 5354.5 | 45.3 | 32.6 | 90.7 | 89.9 | 85.1 | 99.7 | 39.3 | 25.8 | 6627.4 | 6287.4 | 5998.6 | 10626.2 | 9893.9 | 9201.6 | 1.603 | 1.574 | 1.534 | 0.711 | 0.71 | 0.728 | 4.69 | 6.39 | -5.6 | 0.644 | 0.653 | 0.682 | -4.79 | 4.51 | 5.08 | 0.713 | 0.647 | 0.633 | 4.9 | -4.53 | 4.56 | 0.632 | 0.677 | 0.655 | 4.22 | 4.07 | -4.97 | Poor_Mixed | 5998.6 | 9201.6 | 1.534 | 0.728 | 6.39 | 0.713 | 5.08 | 0.4401 | 0.7629 | 0.4949 | 0.5513 | 1 | 0.4433 | 0.5047 | 0.5916 | 0.5916 | Poor | 0 | 1 | DGA | 0 |  | C2H2
919 | 1018.6 | 585.5 | 111.8 | 132.8 | 21.5 | 935.6 | 6126.3 | 57.6 | 20.9 | 81.5 | 80 | 72.8 | 84 | 37 | 14.2 | 10000 | 8981.1 | 9294.1 | 19315.6 | 17449.2 | 17703.2 | 1.932 | 1.943 | 1.905 | 0.555 | 0.586 | 0.542 | -2.31 | 3.21 | 2.7 | 0.5 | 0.524 | 0.511 | -2.57 | -2.67 | 3 | 0.554 | 0.568 | 0.531 | 2.72 | 2.22 | 3.33 | 0.549 | 0.555 | 0.518 | 2.22 | 2.32 | 2.02 | Poor_DGA | 8981.1 | 17449.2 | 1.905 | 0.586 | 3.21 | 0.568 | 3.33 | 0.3572 | 0.9574 | 0.8123 | 0.9144 | 1 | 0.7896 | 0.8186 | 0.749 | 0.749 | Fair | 1 | 1 | DGA | 0 |  | C2H2
920 | 915.1 | 546 | 104.2 | 116.9 | 19.3 | 800.8 | 4760.4 | 50.3 | 31.8 | 89.8 | 93.9 | 84.5 | 99.7 | 40.4 | 22.3 | 6017.8 | 4352.9 | 5689.1 | 9440.3 | 6490.7 | 8489.4 | 1.569 | 1.491 | 1.492 | 0.714 | 0.728 | 0.765 | 5.34 | 5.48 | 5.98 | 0.693 | 0.64 | 0.7 | 5.22 | 4.78 | -4.08 | 0.654 | 0.681 | 0.688 | -4.81 | 3.46 | 3.3 | 0.612 | 0.757 | 0.662 | -3.54 | 4.86 | 4.27 | Poor_Mixed | 4352.9 | 6490.7 | 1.491 | 0.765 | 5.98 | 0.757 | 5.22 | 0.4337 | 0.7728 | 0.4718 | 0.6719 | 1 | 0.4238 | 0.4995 | 0.5912 | 0.5912 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
921 | 1107.7 | 553.2 | 107.5 | 125.2 | 22.1 | 986.1 | 6067.5 | 57.9 | 25 | 81.6 | 80.7 | 75.2 | 87.5 | 36.8 | 14.6 | 8547.5 | 8118.5 | 7246.3 | 15989.7 | 14993.4 | 12406.7 | 1.871 | 1.847 | 1.712 | 0.519 | 0.534 | 0.525 | 2.26 | 2.7 | -2.57 | 0.574 | 0.538 | 0.543 | 2.77 | 2.76 | 3.05 | 0.514 | 0.558 | 0.547 | 2.96 | 2.89 | 2.15 | 0.565 | 0.543 | 0.593 | -2.52 | 2.53 | 2.25 | Poor_DGA | 7246.3 | 12406.7 | 1.712 | 0.534 | 2.7 | 0.593 | 3.05 | 0.3556 | 0.87 | 0.7698 | 0.904 | 1 | 0.8654 | 0.7619 | 0.7338 | 0.7338 | Fair | 1 | 1 | DGA | 0 |  | C2H2
922 | 954.2 | 581.7 | 102.5 | 120.4 | 18.5 | 812.3 | 5197.4 | 46.3 | 31.9 | 92.9 | 89.6 | 81.2 | 98 | 39 | 24.3 | 5499.3 | 5658.9 | 5098.4 | 8087.4 | 8662.7 | 7914.7 | 1.471 | 1.531 | 1.552 | 0.75 | 0.709 | 0.801 | -5.44 | -5.54 | 5.75 | 0.716 | 0.726 | 0.671 | 4.33 | 4.13 | 4.41 | 0.767 | 0.616 | 0.659 | 5.34 | -5.16 | 3.51 | 0.664 | 0.695 | 0.744 | 5.41 | 4.67 | 5.11 | Poor_Mixed | 5098.4 | 7914.7 | 1.471 | 0.801 | 5.75 | 0.767 | 5.41 | 0.4236 | 0.7716 | 0.5176 | 0.6039 | 1 | 0.4105 | 0.4611 | 0.5809 | 0.5809 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
923 | 718.5 | 461.1 | 100.6 | 112.8 | 12.5 | 779.5 | 4814.4 | 50.8 | 30.1 | 88.8 | 86.6 | 76.4 | 94.5 | 38.8 | 19.2 | 6990.2 | 7134.8 | 7332.6 | 11889.6 | 11689.4 | 12523.5 | 1.701 | 1.638 | 1.708 | 0.674 | 0.723 | 0.658 | -4.63 | 5.45 | 4.71 | 0.66 | 0.631 | 0.615 | 3.39 | 4.18 | 3.97 | 0.53 | 0.649 | 0.626 | -5.07 | -3.53 | -3.87 | 0.695 | 0.662 | 0.611 | 3.37 | 3.24 | 4.4 | Poor_Mixed | 6990.2 | 11689.4 | 1.638 | 0.723 | 5.45 | 0.695 | 5.07 | 0.5134 | 0.7947 | 0.6165 | 0.7718 | 1 | 0.5082 | 0.5774 | 0.6591 | 0.6591 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
924 | 255.5 | 122.7 | 70.6 | 50 | 1.4 | 458.1 | 2907.4 | 50.4 | 29.8 | 76.8 | 75 | 71.2 | 80 | 35 | 10 | 8921.7 | 7963.6 | 8228.2 | 16354.2 | 14363.9 | 15026.5 | 1.833 | 1.804 | 1.826 | 0.581 | 0.581 | 0.533 | 2.69 | -3.39 | 2.42 | 0.5 | 0.5 | 0.537 | 2.73 | 2.12 | 2.87 | 0.54 | 0.526 | 0.521 | 2.66 | 2.96 | -3.03 | 0.584 | 0.523 | 0.5 | -2 | 2.13 | 2 | Fair_Oil | 7963.6 | 14363.9 | 1.804 | 0.581 | 3.39 | 0.584 | 3.03 | 0.911 | 0.7986 | 0.9578 | 1 | 1 | 0.7783 | 0.8596 | 0.8931 | 0.8931 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
925 | 703 | 411.3 | 95.5 | 99.1 | 15.1 | 765.1 | 4464.4 | 58.2 | 20.5 | 75 | 78.2 | 70 | 80 | 35 | 11.5 | 10000 | 9206.9 | 9337 | 19129.9 | 17685.9 | 18482.8 | 1.913 | 1.921 | 1.98 | 0.516 | 0.541 | 0.5 | 2.43 | 2.78 | -2 | 0.545 | 0.521 | 0.569 | 2.44 | 2 | 2.61 | 0.517 | 0.573 | 0.547 | 3.38 | 3.25 | 2.43 | 0.55 | 0.563 | 0.588 | 2.37 | 2.97 | 3.61 | Fair_DGA | 9206.9 | 17685.9 | 1.913 | 0.541 | 2.78 | 0.588 | 3.61 | 0.5242 | 0.9709 | 0.9584 | 0.9764 | 1 | 0.9032 | 0.7578 | 0.8151 | 0.8151 | Good | 1 | 1 | DGA | 0 |  | C2H2
926 | 466.3 | 260.3 | 78.9 | 71.3 | 3.2 | 563.6 | 4000.2 | 31.5 | 49.4 | 81.4 | 84.3 | 117.4 | 89 | 37.2 | 14.9 | 5663.3 | 4907.8 | 4493.4 | 9087.9 | 6986.3 | 6746.8 | 1.605 | 1.424 | 1.501 | 0.699 | 0.679 | 0.658 | 5.28 | 4.89 | -4.53 | 0.553 | 0.55 | 0.591 | 3.18 | -4.59 | 2.56 | 0.606 | 0.651 | 0.626 | -4.13 | 3.34 | -2.97 | 0.504 | 0.587 | 0.55 | 3.11 | 3.17 | 3.45 | Critical_Oil | 4493.4 | 6746.8 | 1.424 | 0.699 | 5.28 | 0.651 | 4.59 | 0.7584 | 0.5888 | 0.5826 | 0.8962 | 1 | 0.5156 | 0.6851 | 0.7188 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Moisture_PPM
927 | 805.6 | 509.7 | 99.4 | 113 | 12.6 | 733.8 | 5078.2 | 48.9 | 34.5 | 86.8 | 86.3 | 80.5 | 97.1 | 38.3 | 24.5 | 6737.3 | 6393.8 | 7695.4 | 10771.6 | 10341.5 | 13580.7 | 1.599 | 1.617 | 1.765 | 0.77 | 0.773 | 0.678 | 5.8 | 6.5 | 4.83 | 0.64 | 0.655 | 0.71 | 5.9 | 4.82 | 5.74 | 0.642 | 0.705 | 0.624 | 4.93 | 3.83 | 5.32 | 0.581 | 0.683 | 0.621 | -5.04 | 4.67 | -4.1 | Poor_Mixed | 6393.8 | 10341.5 | 1.599 | 0.773 | 6.5 | 0.71 | 5.9 | 0.5042 | 0.7403 | 0.5942 | 0.597 | 1 | 0.4152 | 0.5069 | 0.6135 | 0.6135 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
928 | 259.7 | 151.2 | 72.8 | 62.1 | 2.9 | 502.8 | 2868.2 | 57.9 | 22.8 | 75.2 | 75.7 | 70 | 80.4 | 35 | 11.1 | 3910.3 | 4412.8 | 3603.5 | 5392.2 | 6171.4 | 4710.7 | 1.379 | 1.399 | 1.307 | 0.612 | 0.653 | 0.563 | -3.55 | 3.65 | -3.52 | 0.535 | 0.521 | 0.582 | 2.82 | 2 | 2.53 | 0.524 | 0.57 | 0.5 | 2.55 | 2.63 | 2.17 | 0.523 | 0.505 | 0.564 | -2.11 | 2.77 | 2 | Poor_IR_PI | 3603.5 | 4710.7 | 1.307 | 0.653 | 3.65 | 0.582 | 2.82 | 0.8303 | 0.9108 | 0.9795 | 0.984 | 1 | 0.6714 | 0.8278 | 0.867 | 0.867 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
929 | 1019.3 | 574.3 | 107 | 118 | 16.6 | 858 | 6014.3 | 49.8 | 32.7 | 91.8 | 90.1 | 80.2 | 96.4 | 39.7 | 25.1 | 6699.7 | 6136.1 | 6450.4 | 10362.3 | 9568 | 10247 | 1.547 | 1.559 | 1.589 | 0.723 | 0.737 | 0.72 | 5.22 | -6.42 | 5.27 | 0.742 | 0.703 | 0.738 | -5.04 | -4.7 | 5.3 | 0.627 | 0.62 | 0.687 | 5.05 | 4.78 | 5.02 | 0.669 | 0.654 | 0.681 | -4.46 | -3.9 | 4.11 | Poor_Mixed | 6136.1 | 9568 | 1.547 | 0.737 | 6.42 | 0.742 | 5.3 | 0.4161 | 0.7617 | 0.5315 | 0.576 | 1 | 0.4296 | 0.4776 | 0.5835 | 0.5835 | Poor | 0 | 1 | DGA | 0 |  | C2H2
930 | 1619.9 | 898.9 | 141.8 | 161.8 | 27.9 | 1313.5 | 8430 | 55.8 | 23.4 | 80 | 77.1 | 103.8 | 83.9 | 35.5 | 13.3 | 10000 | 9276.4 | 9551.1 | 19427.2 | 18248.6 | 18243.3 | 1.943 | 1.967 | 1.91 | 0.656 | 0.676 | 0.647 | 3.63 | 5.47 | 4.49 | 0.561 | 0.615 | 0.558 | 3.05 | 3.43 | -3.17 | 0.6 | 0.574 | 0.574 | 2.63 | 4.22 | 3.6 | 0.581 | 0.589 | 0.557 | 3.11 | 3.07 | 3.88 | Critical_DGA | 9276.4 | 18243.3 | 1.91 | 0.676 | 5.47 | 0.615 | 4.22 | 0.125 | 0.8988 | 0.6904 | 0.9367 | 1 | 0.5566 | 0.6767 | 0.6147 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | C2H2
931 | 538.1 | 381.9 | 91.8 | 88.7 | 12.2 | 621.7 | 4342.2 | 51.2 | 30.1 | 85.1 | 80.6 | 77.3 | 88.4 | 36.5 | 19 | 7538.1 | 7734.9 | 6079.1 | 13210.2 | 14301.1 | 9738.4 | 1.752 | 1.849 | 1.602 | 0.618 | 0.601 | 0.66 | 4.17 | -4.02 | 4.68 | 0.598 | 0.615 | 0.652 | -3.71 | 3.04 | 4.56 | 0.577 | 0.566 | 0.661 | 3.84 | 3.26 | 4.17 | 0.579 | 0.574 | 0.655 | 2.7 | 3.94 | 2.94 | Fair_Mixed | 6079.1 | 9738.4 | 1.602 | 0.66 | 4.68 | 0.661 | 4.56 | 0.5967 | 0.7947 | 0.7255 | 0.778 | 1 | 0.6062 | 0.6212 | 0.7127 | 0.7127 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
932 | 984.5 | 625.7 | 109.8 | 121.5 | 21.7 | 880.8 | 5427.7 | 46.7 | 32.5 | 89.4 | 91.3 | 83.7 | 97.8 | 39.2 | 26 | 4957.3 | 6971.4 | 6061.5 | 7400.1 | 11237.8 | 9144 | 1.493 | 1.612 | 1.509 | 0.71 | 0.677 | 0.703 | 5.68 | 4.99 | 5.2 | 0.641 | 0.685 | 0.613 | 5.13 | 4.65 | 5.21 | 0.645 | 0.686 | 0.615 | -4.37 | -4.99 | 3.94 | 0.708 | 0.657 | 0.624 | 5.53 | 4.21 | 3.77 | Poor_Mixed | 4957.3 | 7400.1 | 1.493 | 0.71 | 5.68 | 0.708 | 5.53 | 0.3805 | 0.7641 | 0.5131 | 0.5442 | 1 | 0.4761 | 0.5142 | 0.5846 | 0.5846 | Poor | 0 | 1 | DGA | 0 |  | C2H2
933 | 644.3 | 504.6 | 100.2 | 104.4 | 14.7 | 695.2 | 4876 | 58.4 | 22.3 | 76.6 | 76.2 | 73.3 | 84.2 | 36.2 | 10.6 | 8070.4 | 8942.6 | 9389.3 | 14985.2 | 17366.2 | 17360.1 | 1.857 | 1.942 | 1.849 | 0.54 | 0.594 | 0.543 | 2.78 | 3.16 | 2.94 | 0.54 | 0.606 | 0.576 | -2.28 | 2 | -2.9 | 0.512 | 0.528 | 0.542 | -2.1 | 2.91 | 2.99 | 0.562 | 0.511 | 0.543 | 2.42 | 2.77 | 2.87 | Fair_DGA | 8070.4 | 14985.2 | 1.849 | 0.594 | 3.16 | 0.606 | 2.99 | 0.5177 | 0.9215 | 0.8953 | 0.9925 | 1 | 0.7778 | 0.7845 | 0.7893 | 0.7893 | Fair | 1 | 1 | DGA | 0 |  | C2H2
934 | 893.2 | 547.5 | 97 | 95.9 | 16.8 | 708.2 | 5253.8 | 58.4 | 21.6 | 78.1 | 76.4 | 75.1 | 85.9 | 36.1 | 12.3 | 9854.7 | 9846.1 | 8942.7 | 19709.4 | 18902.6 | 17885.4 | 2 | 1.92 | 2 | 0.576 | 0.561 | 0.576 | 3.73 | 3.77 | 2.86 | 0.522 | 0.532 | 0.537 | 2.91 | 2.16 | 2.65 | 0.529 | 0.533 | 0.521 | 2 | -2.79 | 2.32 | 0.523 | 0.516 | 0.55 | 2.76 | 2 | 2.86 | Fair_DGA | 8942.7 | 17885.4 | 1.92 | 0.576 | 3.77 | 0.55 | 2.91 | 0.4845 | 0.938 | 0.8547 | 0.9597 | 1 | 0.7258 | 0.8249 | 0.7772 | 0.7772 | Fair | 1 | 1 | DGA | 0 |  | C2H2
935 | 1746.7 | 935.5 | 136.8 | 190.4 | 31.9 | 1330.9 | 7994.2 | 52.4 | 26.4 | 78.9 | 76.3 | 73.3 | 83.5 | 36.6 | 12.8 | 8342.4 | 9207.4 | 8155.9 | 14288.4 | 17262.1 | 5808.7 | 1.713 | 1.875 | 0.712 | 0.608 | 0.656 | 0.618 | 3.55 | 4.8 | 4.61 | 0.551 | 0.533 | 0.514 | 2.2 | 2 | 3.39 | 0.5 | 0.566 | 0.519 | 3.28 | 3.29 | 3.07 | 0.546 | 0.533 | 0.54 | 2.71 | 2.31 | 3.47 | Critical_DGA | 8155.9 | 5808.7 | 0.712 | 0.656 | 4.8 | 0.566 | 3.47 | 0.0774 | 0.8474 | 0.8721 | 0.9484 | 0.8125 | 0.6034 | 0.8054 | 0.6151 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
936 | 880 | 497.2 | 103.2 | 116 | 19 | 835.4 | 5632.5 | 47.3 | 32.9 | 91.1 | 89.6 | 81.9 | 98.9 | 40.8 | 25.6 | 5657.9 | 5351.2 | 5718.5 | 8498.7 | 8197.7 | 8851 | 1.502 | 1.532 | 1.548 | 0.696 | 0.727 | 0.672 | 5.5 | -5.55 | -4.24 | 0.652 | 0.627 | 0.601 | 4.03 | -4.7 | -4.13 | 0.591 | 0.737 | 0.679 | -5.38 | 4.91 | -4.91 | 0.658 | 0.62 | 0.677 | -4.55 | 5.03 | 5.93 | Poor_Mixed | 5351.2 | 8197.7 | 1.502 | 0.727 | 5.55 | 0.737 | 5.93 | 0.4322 | 0.7593 | 0.5087 | 0.5584 | 1 | 0.4862 | 0.5131 | 0.5984 | 0.5984 | Poor | 0 | 1 | DGA | 0 |  | C2H2
937 | 273 | 297.2 | 76.4 | 88.3 | 8.6 | 570.8 | 3537.5 | 55.1 | 28.3 | 78.7 | 80.7 | 73.2 | 86.7 | 36.8 | 14.3 | 8754 | 7490.2 | 8950.2 | 16148.9 | 13234.3 | 16966.6 | 1.845 | 1.767 | 1.896 | 0.567 | 0.598 | 0.571 | -2.63 | 3.35 | 3.09 | 0.585 | 0.547 | 0.582 | 2.52 | -3.46 | 3.2 | 0.543 | 0.51 | 0.598 | 2.64 | 2.76 | -3.58 | 0.559 | 0.6 | 0.608 | 3.22 | -3.53 | -2.68 | Fair_Mixed | 7490.2 | 13234.3 | 1.767 | 0.598 | 3.35 | 0.608 | 3.58 | 0.6859 | 0.8193 | 0.8148 | 0.9118 | 1 | 0.7436 | 0.711 | 0.7889 | 0.7889 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
938 | 1666.7 | 927.8 | 138.9 | 181.2 | 34.2 | 1370.5 | 8183.7 | 33.7 | 47.6 | 109.3 | 105.9 | 94.4 | 116.6 | 44.9 | 32.6 | 1544.5 | 2022.2 | 1601.2 | 1691.5 | 2509.5 | 1753.7 | 1.095 | 1.241 | 1.095 | 0.908 | 0.962 | 0.938 | 8.32 | 9.51 | -9.84 | 0.989 | 0.805 | 0.94 | 7.31 | -5.83 | -8.25 | 0.819 | 0.81 | 0.744 | 5.46 | 8.69 | 6.62 | 0.749 | 0.748 | 0.939 | 7.65 | 8.53 | 7.18 | Very Poor_Mixed | 1544.5 | 1691.5 | 1.095 | 0.962 | 9.84 | 0.989 | 8.69 | 0.073 | 0.6053 | 0.1128 | 0.2982 | 1 | 0.0812 | 0.2257 | 0.3291 | 0.3291 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
939 | 1524.7 | 904.5 | 130.9 | 177.7 | 30.2 | 1221.7 | 7858.1 | 33.5 | 45.7 | 103.6 | 103 | 91.1 | 111.2 | 44.2 | 31.3 | 1801.1 | 1657.8 | 2103.5 | 2023.9 | 1825 | 2310.3 | 1.124 | 1.101 | 1.098 | 0.953 | 0.972 | 0.933 | -9.5 | 9.01 | 9.15 | 0.87 | 0.779 | 0.842 | -6.2 | -9.38 | 8.08 | 0.877 | 0.74 | 0.732 | -7.51 | 6.03 | 5.2 | 0.856 | 0.709 | 0.922 | 6.23 | -7.19 | 7.13 | Very Poor_Mixed | 1657.8 | 1825 | 1.098 | 0.972 | 9.5 | 0.922 | 9.38 | 0.133 | 0.6232 | 0.2111 | 0.3483 | 1 | 0.0699 | 0.2566 | 0.3625 | 0.3625 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
940 | 846.6 | 572.5 | 112 | 109.5 | 18.2 | 764.5 | 4829.8 | 49.8 | 31.8 | 92.4 | 92.3 | 82.3 | 100.8 | 40.1 | 24.2 | 4982.1 | 5310.6 | 6837.9 | 7413.8 | 7631.1 | 11105.9 | 1.488 | 1.437 | 1.624 | 0.755 | 0.714 | 0.752 | 6.37 | 5.04 | 5.79 | 0.573 | 0.654 | 0.696 | 5.05 | -4.19 | 3.84 | 0.68 | 0.782 | 0.704 | 3.81 | 3.8 | 4.45 | 0.728 | 0.639 | 0.642 | 4.73 | -6.16 | 4.93 | Poor_Mixed | 4982.1 | 7413.8 | 1.437 | 0.755 | 6.37 | 0.782 | 6.16 | 0.4484 | 0.7728 | 0.4752 | 0.6074 | 1 | 0.4125 | 0.4898 | 0.5887 | 0.5887 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
941 | 189 | 171.6 | 70.6 | 57.5 | 2.9 | 387.6 | 2785.1 | 56.4 | 23.4 | 78.1 | 78.2 | 73 | 83.4 | 35 | 12.8 | 9101.7 | 10000 | 8851 | 17344.4 | 19310.2 | 16693.6 | 1.906 | 1.931 | 1.886 | 0.5 | 0.5 | 0.511 | 2 | 2.44 | 2.31 | 0.5 | 0.5 | 0.5 | 2.4 | -2 | 2.12 | 0.5 | 0.5 | 0.596 | 2.55 | -2.57 | 2.58 | 0.511 | 0.571 | 0.51 | 2 | -2.05 | 2.16 | Good_Mixed | 8851 | 16693.6 | 1.886 | 0.511 | 2.44 | 0.596 | 2.58 | 0.8642 | 0.8988 | 0.8691 | 0.9484 | 1 | 0.959 | 0.9052 | 0.9154 | 0.9154 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
942 | 1428.4 | 866.7 | 136.1 | 177.2 | 29.5 | 1225.1 | 8178.6 | 34.3 | 45.9 | 102.3 | 106 | 91.9 | 112 | 43.1 | 30.1 | 3525.7 | 2988.2 | 2619.3 | 4677 | 3644.4 | 3272.3 | 1.327 | 1.22 | 1.249 | 0.906 | 0.869 | 0.868 | 8.2 | -8.2 | 8.08 | 0.7 | 0.761 | 0.735 | 5.1 | 6.19 | 5.42 | 0.852 | 0.784 | 0.753 | -7.12 | 7.75 | -6.98 | 0.75 | 0.668 | 0.752 | 6.18 | -5.79 | 6.85 | Very Poor_Mixed | 2619.3 | 3272.3 | 1.22 | 0.906 | 8.2 | 0.852 | 7.75 | 0.1391 | 0.6213 | 0.201 | 0.3938 | 1 | 0.1732 | 0.3389 | 0.3944 | 0.3944 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
943 | 305.4 | 281.3 | 76.4 | 74.1 | 3.1 | 504.2 | 3820.2 | 26.1 | 20.9 | 82.2 | 78 | 72.3 | 86 | 36.2 | 13.5 | 8050.2 | 7168.2 | 8206.7 | 14234.4 | 12424.9 | 14777.5 | 1.768 | 1.733 | 1.801 | 0.954 | 0.99 | 0.99 | 9.25 | -9.68 | 9.34 | 0.501 | 0.525 | 0.516 | 3.36 | 2 | 2.38 | 0.51 | 0.544 | 0.5 | 2.56 | 2.59 | 2 | 0.549 | 0.512 | 0.506 | 2.46 | 2.14 | -2.49 | Critical_Winding_TD_Cap | 7168.2 | 12424.9 | 1.733 | 0.99 | 9.68 | 0.549 | 3.36 | 0.781 | 0.374 | 0.8236 | 0.9318 | 1 | 0.043 | 0.8754 | 0.6927 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
944 | 799.2 | 418 | 102.3 | 105.2 | 13.3 | 856.9 | 5449.4 | 46.5 | 32.9 | 88.4 | 91.7 | 83.3 | 98.9 | 39.9 | 25.6 | 5985 | 4531.1 | 5121.6 | 9336.4 | 6859 | 7455 | 1.56 | 1.514 | 1.456 | 0.75 | 0.742 | 0.73 | -5.76 | 5.56 | 5.96 | 0.658 | 0.739 | 0.713 | -4.09 | -5.76 | 4.64 | 0.718 | 0.68 | 0.692 | 5.6 | -4.62 | -4.69 | 0.678 | 0.662 | 0.676 | 4.98 | 3.73 | 3.8 | Poor_Mixed | 4531.1 | 6859 | 1.456 | 0.75 | 5.96 | 0.739 | 5.76 | 0.4962 | 0.7593 | 0.5098 | 0.5584 | 1 | 0.4102 | 0.4654 | 0.5953 | 0.5953 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
945 | 958.9 | 527.1 | 109.3 | 131.2 | 19.8 | 917.3 | 6066.8 | 48.1 | 32.4 | 90.5 | 92.4 | 82 | 97.6 | 39.7 | 26.9 | 5250 | 5962.4 | 4937.9 | 7414 | 9548.4 | 6666.4 | 1.412 | 1.601 | 1.35 | 0.679 | 0.749 | 0.72 | 4.79 | 6.32 | -5.59 | 0.645 | 0.639 | 0.561 | 5.7 | 4.58 | 4.06 | 0.597 | 0.618 | 0.648 | -4.47 | 4.29 | 4.84 | 0.673 | 0.708 | 0.618 | 3.55 | 5.12 | -4.56 | Poor_Mixed | 4937.9 | 6666.4 | 1.35 | 0.749 | 6.32 | 0.708 | 5.7 | 0.3842 | 0.7654 | 0.5073 | 0.512 | 1 | 0.4437 | 0.544 | 0.5843 | 0.5843 | Poor | 0 | 1 | DGA | 0 |  | C2H2
946 | 386.4 | 306.8 | 84.4 | 74.9 | 1.2 | 574.2 | 3136.6 | 25.1 | 24.9 | 81.5 | 82.6 | 77.8 | 90.3 | 37.7 | 16.8 | 2251.9 | 1242.9 | 1180.7 | 2725.5 | 1417.7 | 1242.1 | 1.21 | 1.141 | 1.052 | 0.76 | 0.732 | 0.711 | -5.36 | -5.95 | 5.47 | 0.549 | 0.595 | 0.554 | 3.16 | 2.55 | 3.46 | 0.562 | 0.583 | 0.615 | 2.36 | 3.57 | 3.5 | 0.562 | 0.553 | 0.56 | -2.41 | 4.1 | 2.85 | Critical_IR_PI | 1180.7 | 1242.1 | 1.052 | 0.76 | 5.95 | 0.615 | 4.1 | 0.8184 | 0.2883 | 0.7174 | 0.8436 | 1 | 0.4253 | 0.7042 | 0.6994 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
947 | 1766 | 942.1 | 144.1 | 197 | 34.3 | 1355.5 | 8379.5 | 55.8 | 58.8 | 79.8 | 80 | 76 | 86.1 | 37.2 | 15.8 | 7129.2 | 7337.3 | 7841.7 | 12344 | 13182.9 | 13943.9 | 1.731 | 1.797 | 1.778 | 0.572 | 0.634 | 0.638 | -4.03 | 4.2 | 4.79 | 0.502 | 0.587 | 0.517 | -3.02 | 2.23 | -3.04 | 0.5 | 0.5 | 0.538 | -2.54 | -3.02 | -2.28 | 0.514 | 0.556 | 0.5 | 2.96 | 2.64 | 2.08 | Critical_DGA | 7129.2 | 12344 | 1.731 | 0.638 | 4.79 | 0.587 | 3.04 | 0.046 | 0.5833 | 0.7899 | 0.8718 | 1 | 0.6175 | 0.8626 | 0.6058 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
948 | 100 | 120 | 66.3 | 50 | 2.2 | 415.9 | 2500 | 54.4 | 23.7 | 75 | 75.4 | 72 | 80 | 35 | 18.4 | 7710.6 | 8074.6 | 8489.2 | 13146.9 | 14301.7 | 15422.3 | 1.705 | 1.771 | 1.817 | 0.648 | 0.632 | 0.668 | -17.33 | 3.68 | 3.85 | 0.627 | 0.536 | 0.656 | -2.8 | -3.16 | 3.3 | 0.64 | 0.664 | 0.566 | 3.84 | -2.68 | -3.07 | 0.53 | 0.945 | 0.603 | 2.99 | -9.22 | 2.06 | Critical_Bushing_TD_Cap | 7710.6 | 13146.9 | 1.705 | 0.668 | 17.33 | 0.945 | 9.22 | 0.9132 | 0.8931 | 0.9683 | 0.7963 | 1 | 0.5004 | 0.5963 | 0.8095 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_HV_CapChange_pct
949 | 1004.2 | 588.7 | 113.2 | 125 | 21 | 922.7 | 6009.8 | 59.1 | 22.2 | 82.3 | 81.4 | 75.9 | 88.9 | 37.8 | 14.3 | 8735 | 9890.2 | 9008.1 | 16799.6 | 18466.8 | 17105.3 | 1.923 | 1.867 | 1.899 | 0.582 | 0.556 | 0.586 | 3.6 | 2.84 | -3.38 | 0.5 | 0.544 | 0.5 | 2.5 | 2.31 | 2 | 0.507 | 0.518 | 0.501 | 2.3 | 2.56 | -2.06 | 0.536 | 0.526 | 0.5 | -2 | 2.07 | 2.77 | Poor_DGA | 8735 | 16799.6 | 1.867 | 0.586 | 3.6 | 0.544 | 2.77 | 0.3699 | 0.9238 | 0.7406 | 0.9118 | 1 | 0.7326 | 0.9045 | 0.7483 | 0.7483 | Fair | 1 | 1 | DGA | 0 |  | C2H2
950 | 1619.3 | 834 | 131.4 | 179.7 | 33.2 | 1212.1 | 7300.4 | 37 | 43.4 | 103.3 | 103.9 | 92 | 113.1 | 44.6 | 29.5 | 2368.9 | 3008 | 3127.9 | 2792.6 | 3593.3 | 3865.8 | 1.179 | 1.195 | 1.236 | 0.911 | 0.884 | 0.928 | -8.74 | 8.07 | 8.65 | 0.941 | 0.908 | 0.801 | 8.62 | -7.09 | 8.07 | 0.774 | 0.796 | 0.734 | 5.19 | 7.17 | -5.83 | 0.724 | 0.811 | 0.764 | 8.47 | -7.74 | -6.92 | Very Poor_Mixed | 2368.9 | 2792.6 | 1.179 | 0.928 | 8.74 | 0.941 | 8.62 | 0.1265 | 0.6455 | 0.1902 | 0.4164 | 1 | 0.1377 | 0.2561 | 0.3743 | 0.3743 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
951 | 452 | 260.1 | 81.6 | 75.6 | 2 | 596.1 | 3542.8 | 55 | 23.1 | 77.8 | 76.8 | 72.5 | 83.2 | 36.8 | 14.3 | 8050.6 | 10000 | 8645.7 | 5125 | 19525 | 15578.5 | 0.637 | 1.952 | 1.802 | 0.5 | 0.593 | 0.59 | 2.16 | -2.97 | 3.46 | 0.574 | 0.577 | 0.562 | 4.11 | 4.3 | 3.22 | 0.52 | 0.927 | 0.582 | 2.24 | 9.26 | 3.79 | 0.58 | 0.557 | 0.547 | -3.72 | 3.87 | 2.09 | Critical_Bushing_TD_Cap | 8050.6 | 5125 | 0.637 | 0.593 | 3.46 | 0.927 | 9.26 | 0.7793 | 0.9047 | 0.8841 | 0.9118 | 0.8187 | 0.8033 | 0.6387 | 0.7958 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_HV
952 | 328.1 | 199.8 | 72.4 | 61.8 | 4.2 | 478.3 | 2805.7 | 56 | 21.9 | 77 | 80.6 | 70.1 | 83.7 | 36.3 | 12.5 | 10000 | 8743.6 | 9998.7 | 20000 | 16325.7 | 19038.6 | 2 | 1.867 | 1.904 | 0.5 | 0.54 | 0.573 | -2 | 2.47 | -3.68 | 0.622 | 0.522 | 0.53 | 2 | -3.11 | 3.12 | 0.525 | 0.527 | 0.563 | 2.93 | 2.94 | 2.34 | 0.583 | 0.513 | 0.553 | 2 | -2.54 | 3.22 | Good_Mixed | 8743.6 | 16325.7 | 1.867 | 0.573 | 3.68 | 0.622 | 3.22 | 0.7994 | 0.9307 | 0.8816 | 0.9552 | 1 | 0.8495 | 0.7765 | 0.8662 | 0.8662 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
953 | 563.8 | 440.1 | 91.8 | 149.7 | 3.3 | 633.6 | 3770.1 | 57.7 | 20.8 | 107.3 | 107.3 | 97.6 | 117.5 | 45.8 | 14.7 | 9247.4 | 9706.6 | 9114.9 | 17754.7 | 18145.7 | 17886.4 | 1.92 | 1.869 | 1.962 | 0.517 | 0.527 | 0.533 | 2 | -2.36 | 2.56 | 0.5 | 0.537 | 0.543 | 3.25 | -3.2 | 2.54 | 2.295 | 0.546 | 0.519 | 2.41 | 2.71 | -2.62 | 0.552 | 0.55 | 0.549 | 2.39 | 2.66 | -2.1 | Critical_Thermal | 9114.9 | 17754.7 | 1.869 | 0.533 | 2.56 | 2.295 | 3.25 | 0.63 | 0.9605 | 0.0872 | 0.9014 | 1 | 0.8833 | 0.7442 | 0.7442 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_TanDelta_pct>=1.0%: critical bushing tan delta | C2H4
954 | 262.2 | 169.8 | 67.4 | 50.9 | 1.2 | 449.3 | 2909.5 | 52.5 | 26.1 | 75 | 80.3 | 72 | 82.9 | 35.6 | 14.9 | 7788.4 | 8598.2 | 7252.7 | 13601.9 | 15827.4 | 13250.7 | 1.746 | 1.841 | 1.827 | 0.588 | 0.693 | 0.625 | -2.87 | 3.93 | 3.8 | 0.544 | 0.538 | 0.577 | -3.03 | -2.27 | 3.6 | 0.5 | 0.594 | 0.931 | 4.85 | -2.28 | 9.14 | 0.561 | 0.601 | 0.542 | 4.54 | -14.28 | 3.9 | Critical_Bushing_TD_Cap | 7252.7 | 13250.7 | 1.746 | 0.693 | 3.93 | 0.931 | 14.28 | 0.9155 | 0.852 | 0.8998 | 0.8962 | 1 | 0.6452 | 0.6312 | 0.8298 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
955 | 390 | 177.8 | 72.7 | 61.1 | 62.3 | 445 | 3313.8 | 37 | 43.3 | 80 | 78.3 | 73.7 | 83.9 | 36.3 | 14.5 | 6132.8 | 5274.4 | 5358.6 | 9886 | 7852.4 | 8469.6 | 1.612 | 1.489 | 1.581 | 0.626 | 0.567 | 0.636 | -4.2 | 3.76 | 3.85 | 0.513 | 0.5 | 0.549 | -2.31 | 2.48 | 2.61 | 0.536 | 0.529 | 0.534 | 2 | 2.88 | 2.74 | 0.538 | 0.528 | 0.518 | 2.31 | -2.64 | 2.96 | Critical_Oil | 5274.4 | 7852.4 | 1.489 | 0.636 | 4.2 | 0.549 | 2.96 | 0.5904 | 0.6465 | 0.8371 | 0.9067 | 1 | 0.6477 | 0.8344 | 0.7551 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
956 | 726.2 | 567.2 | 104.7 | 116.1 | 17.2 | 731.3 | 5030.2 | 48.5 | 34.2 | 90.5 | 93.4 | 83.6 | 98.3 | 40.2 | 24.5 | 5766.8 | 6012.3 | 6309.7 | 8943.7 | 9820.8 | 10203.5 | 1.551 | 1.633 | 1.617 | 0.69 | 0.699 | 0.736 | 4.82 | -5.31 | -6.02 | 0.641 | 0.698 | 0.716 | 3.86 | -4.08 | 4.64 | 0.672 | 0.621 | 0.639 | 5.63 | 4.86 | 4.03 | 0.688 | 0.709 | 0.735 | -4.02 | 4.86 | 4.29 | Poor_Mixed | 5766.8 | 8943.7 | 1.551 | 0.736 | 6.02 | 0.735 | 5.63 | 0.4661 | 0.7438 | 0.4842 | 0.597 | 1 | 0.4604 | 0.4863 | 0.596 | 0.596 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
957 | 1092.7 | 658 | 112.6 | 141.1 | 19.9 | 889.8 | 6204 | 59 | 20.8 | 80 | 79.6 | 71.4 | 85.5 | 37.2 | 12.3 | 8432.9 | 9382.1 | 9064.4 | 16021.7 | 17528.7 | 17514 | 1.9 | 1.868 | 1.932 | 0.522 | 0.541 | 0.536 | -2.86 | 2.75 | 2.15 | 0.51 | 0.59 | 0.506 | -3.01 | 2.92 | 2.84 | 0.5 | 0.5 | 0.591 | -2.16 | -3.32 | -2.8 | 0.58 | 0.52 | 0.522 | -2.96 | 2.37 | -2.19 | Poor_DGA | 8432.9 | 16021.7 | 1.868 | 0.541 | 2.86 | 0.591 | 3.32 | 0.3491 | 0.9605 | 0.8326 | 0.9597 | 1 | 0.8467 | 0.8248 | 0.7608 | 0.7608 | Fair | 1 | 1 | DGA | 0 |  | C2H2
958 | 981.5 | 504.2 | 102.5 | 115.9 | 17.2 | 800.4 | 6010.3 | 59.1 | 21.4 | 78.7 | 76.6 | 71.3 | 81.7 | 36.2 | 12.6 | 10000 | 10000 | 9353.1 | 20000 | 19509.2 | 17793.8 | 2 | 1.951 | 1.902 | 0.587 | 0.535 | 0.57 | 2.75 | 2 | 3.09 | 0.519 | 0.525 | 0.53 | -2.37 | -2 | -2 | 0.5 | 0.5 | 0.5 | 2.3 | -2.08 | 2.19 | 0.534 | 0.538 | 0.5 | 2.1 | -2 | 2 | Poor_DGA | 9353.1 | 17793.8 | 1.902 | 0.587 | 3.09 | 0.538 | 2.37 | 0.4356 | 0.9432 | 0.8994 | 0.953 | 1 | 0.7972 | 0.9102 | 0.7951 | 0.7951 | Fair | 1 | 1 | DGA | 0 |  | C2H2
959 | 889.7 | 560.2 | 101.4 | 112.9 | 14.3 | 885.5 | 5354.9 | 48.3 | 34.5 | 95 | 96.5 | 83 | 99.4 | 40 | 25.4 | 5974.1 | 5953.8 | 6907.9 | 9564.9 | 9478.5 | 11457 | 1.601 | 1.592 | 1.659 | 0.73 | 0.667 | 0.711 | 5.29 | -4.67 | 5.67 | 0.634 | 0.683 | 0.685 | 5.49 | -5.04 | -3.94 | 0.741 | 0.615 | 0.682 | 4.82 | 3.19 | 5.36 | 0.616 | 0.662 | 0.721 | -3.89 | 5.27 | -4.83 | Poor_Mixed | 5953.8 | 9478.5 | 1.592 | 0.73 | 5.67 | 0.741 | 5.49 | 0.4561 | 0.7403 | 0.436 | 0.5655 | 1 | 0.4756 | 0.4919 | 0.5899 | 0.5899 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
960 | 401.4 | 288.7 | 77.7 | 76.3 | 4 | 545.2 | 3978.9 | 25.3 | 24.7 | 84.1 | 82.6 | 76.6 | 87.1 | 37.4 | 15.1 | 8240.5 | 8762.7 | 7799.3 | 15212.9 | 16359.2 | 12639 | 1.846 | 1.867 | 1.621 | 0.563 | 0.57 | 0.508 | 3.11 | -3.41 | 2.2 | 0.521 | 0.582 | 0.61 | 4.47 | 3.56 | 3.76 | 0.558 | 0.987 | 0.514 | 3.1 | 9.22 | 3.72 | 0.616 | 0.618 | 0.636 | 2.97 | -2.7 | 3.78 | Critical_Bushing_TD_Cap | 7799.3 | 12639 | 1.621 | 0.57 | 3.41 | 0.987 | 9.22 | 0.7442 | 0.2918 | 0.7233 | 0.8908 | 1 | 0.8077 | 0.6043 | 0.7198 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
961 | 228.7 | 156.2 | 68.7 | 59.6 | 72.5 | 401.3 | 2500 | 55.1 | 22.4 | 76.9 | 76.6 | 73.4 | 84.2 | 37.1 | 17.6 | 1189.7 | 2948.2 | 1685.8 | 1253.2 | 3727.7 | 1782.8 | 1.053 | 1.264 | 1.058 | 0.648 | 0.731 | 0.69 | 4.74 | 5.79 | 4.79 | 0.53 | 0.521 | 0.549 | 2.94 | 2.4 | 3.35 | 0.547 | 0.567 | 0.62 | 3.44 | -3.2 | -3.45 | 0.613 | 0.541 | 0.595 | 3.5 | 3.32 | -3.54 | Critical_IR_PI | 1189.7 | 1253.2 | 1.053 | 0.731 | 5.79 | 0.62 | 3.54 | 0.6251 | 0.9193 | 0.8817 | 0.8203 | 1 | 0.4942 | 0.7137 | 0.7534 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
962 | 368.3 | 302 | 80.3 | 96.1 | 39.1 | 606.6 | 4172.7 | 32.6 | 48.3 | 76.1 | 75.9 | 70.5 | 82.4 | 35 | 19.8 | 5194.9 | 5162.7 | 4837.7 | 7454.9 | 7954.7 | 7068.6 | 1.435 | 1.541 | 1.461 | 0.653 | 0.758 | 0.705 | 5.04 | 6.25 | 4.18 | 0.564 | 0.582 | 0.573 | -4.37 | 2.73 | -3.19 | 0.561 | 0.591 | 0.609 | -2.38 | 2.51 | 2.92 | 0.585 | 0.544 | 0.592 | 2.54 | 3 | 2.26 | Critical_Oil | 4837.7 | 7068.6 | 1.435 | 0.758 | 6.25 | 0.609 | 4.37 | 0.4982 | 0.5988 | 0.9457 | 0.753 | 1 | 0.478 | 0.7005 | 0.6816 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
963 | 1619.9 | 916.2 | 143.5 | 197 | 32.6 | 1255.2 | 8632.2 | 32.4 | 44.5 | 106.6 | 109.3 | 90.7 | 114.5 | 44.5 | 33.5 | 1189.1 | 1798.9 | 895.6 | 1304.1 | 2235.7 | 1200 | 1.097 | 1.243 | 1.34 | 0.99 | 0.978 | 0.916 | 9.55 | -9.72 | -8.54 | 0.753 | 0.885 | 0.829 | -6.15 | 6.75 | 7.78 | 0.88 | 0.841 | 0.938 | -7.01 | -6.03 | 8.24 | 0.863 | 0.779 | 0.772 | -6.7 | 7.21 | -7.53 | Very Poor_Mixed | 895.6 | 1200 | 1.097 | 0.99 | 9.72 | 0.938 | 8.24 | 0.0745 | 0.6347 | 0.1433 | 0.2631 | 1 | 0.062 | 0.2307 | 0.3325 | 0.3325 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
964 | 100 | 120 | 65 | 51.5 | 1 | 350 | 2500 | 57.7 | 22.5 | 77 | 77.7 | 71 | 82.2 | 35.7 | 12.6 | 9313 | 9449.5 | 10000 | 17541.7 | 18510.8 | 20000 | 1.884 | 1.959 | 2 | 0.5 | 0.5 | 0.519 | -2.05 | 2.1 | 2.56 | 0.567 | 0.541 | 0.557 | 2.54 | 3.08 | 2.67 | 0.5 | 0.519 | 0.57 | 2.72 | 2.39 | 2.54 | 0.5 | 0.527 | 0.504 | -2.82 | 2.83 | 2.34 | Good_Mixed | 9313 | 17541.7 | 1.884 | 0.519 | 2.56 | 0.57 | 3.08 | 0.9949 | 0.9171 | 0.9075 | 0.953 | 1 | 0.953 | 0.8304 | 0.9401 | 0.9401 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
965 | 1410.7 | 782.6 | 133.1 | 162.6 | 26.3 | 1115.6 | 6851.7 | 36.6 | 39.7 | 102.5 | 97.8 | 91 | 110.5 | 42.7 | 32.7 | 3172 | 3095.2 | 2297.4 | 3903.1 | 3662.9 | 2697.1 | 1.23 | 1.183 | 1.174 | 1.349 | 0.783 | 0.853 | 8.69 | 7.09 | 6.88 | 0.892 | 0.898 | 0.811 | 5.47 | 7.75 | 6.75 | 0.686 | 0.844 | 0.781 | 7.53 | 6.8 | 5.46 | 0.843 | 0.734 | 0.807 | -5.2 | 7.08 | 5.71 | Critical_Mixed | 2297.4 | 2697.1 | 1.174 | 1.349 | 8.69 | 0.898 | 7.75 | 0.2086 | 0.683 | 0.2623 | 0.2943 | 1 | 0.2096 | 0.2785 | 0.4145 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
966 | 908.9 | 531.9 | 102.3 | 122.5 | 18.6 | 784.2 | 5807.7 | 47.2 | 35 | 91.6 | 95.1 | 84 | 100.1 | 39.4 | 21.3 | 5996.2 | 4843.8 | 6913.1 | 9518 | 6832.9 | 11633.7 | 1.587 | 1.411 | 1.683 | 0.744 | 0.66 | 0.782 | 5.93 | 4.79 | -6.13 | 0.667 | 0.7 | 0.713 | -4.91 | -4.41 | -4.16 | 0.642 | 0.563 | 0.694 | 5.27 | -4.71 | 3.96 | 0.624 | 0.594 | 0.584 | -5.28 | -4.59 | 3.86 | Poor_Mixed | 4843.8 | 6832.9 | 1.411 | 0.782 | 6.13 | 0.713 | 5.28 | 0.4274 | 0.7345 | 0.46 | 0.7049 | 1 | 0.4311 | 0.5348 | 0.5929 | 0.5929 | Poor | 0 | 1 | DGA | 0 |  | C2H2
967 | 960 | 523 | 104 | 114.3 | 15.2 | 948.6 | 5791.5 | 46.6 | 34.7 | 91.5 | 92.6 | 81.1 | 98.4 | 40.1 | 24.3 | 6830.2 | 5453.9 | 6469.3 | 11557.2 | 8522.2 | 10270.3 | 1.692 | 1.563 | 1.588 | 0.715 | 0.69 | 0.636 | 5.67 | 5.43 | -5.15 | 0.604 | 0.732 | 0.76 | 5.14 | 4.92 | 3.51 | 0.673 | 0.678 | 0.657 | 3.54 | 4.9 | -3.93 | 0.591 | 0.679 | 0.61 | 5.43 | 4.03 | 3.9 | Poor_Mixed | 5453.9 | 8522.2 | 1.563 | 0.715 | 5.67 | 0.76 | 5.43 | 0.433 | 0.7379 | 0.4988 | 0.6039 | 1 | 0.4855 | 0.5124 | 0.5971 | 0.5971 | Poor | 0 | 1 | DGA | 0 |  | C2H2
968 | 1242.7 | 720.1 | 126.2 | 154.6 | 26.9 | 1121.7 | 6746.5 | 56.2 | 21.8 | 78.8 | 77.1 | 72.9 | 81.6 | 35.2 | 12.7 | 10000 | 10000 | 9774.7 | 19846.7 | 19363.3 | 19549.4 | 1.985 | 1.936 | 2 | 0.546 | 0.558 | 0.586 | 3.22 | -2.76 | 2.29 | 0.511 | 0.528 | 0.5 | 2.26 | 2 | 2.61 | 0.532 | 0.561 | 0.5 | -2 | 2.96 | 2 | 0.564 | 0.518 | 0.545 | 2 | -2.22 | 2.51 | Poor_DGA | 9774.7 | 19363.3 | 1.936 | 0.586 | 3.22 | 0.564 | 2.96 | 0.2377 | 0.9331 | 0.883 | 0.9507 | 1 | 0.7847 | 0.8566 | 0.7313 | 0.7313 | Fair | 1 | 1 | DGA | 0 |  | C2H2
969 | 1434.4 | 883.6 | 137.3 | 180.1 | 34.3 | 1181.1 | 7378 | 34.1 | 46.5 | 104.8 | 105.1 | 92.5 | 115 | 44.7 | 31.6 | 1202.1 | 1141.5 | 1369.3 | 1410.3 | 1281.8 | 1437.8 | 1.173 | 1.123 | 1.05 | 0.905 | 0.949 | 0.99 | -8.45 | 9.22 | 9.77 | 0.751 | 0.684 | 0.83 | 6.75 | -5.74 | 6.33 | 0.879 | 0.747 | 0.779 | -7.66 | 7.78 | 6.33 | 0.901 | 0.798 | 0.827 | -6.05 | 5.22 | 6.25 | Very Poor_Mixed | 1141.5 | 1281.8 | 1.05 | 0.99 | 9.77 | 0.901 | 7.78 | 0.1271 | 0.6156 | 0.162 | 0.3368 | 1 | 0.0771 | 0.2876 | 0.3613 | 0.3613 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
970 | 738.7 | 392.5 | 95.4 | 105.7 | 12.5 | 720.6 | 4375.9 | 53.1 | 26.3 | 85.5 | 87.3 | 78 | 92.2 | 37.7 | 20.2 | 6881.2 | 5701.5 | 7155.8 | 10982.5 | 9502.7 | 12273.7 | 1.596 | 1.667 | 1.715 | 0.695 | 0.71 | 0.654 | 4.38 | 4.74 | -4.97 | 0.557 | 0.61 | 0.614 | 3.78 | 4.23 | -2.87 | 0.535 | 0.61 | 0.616 | -4.25 | 3.97 | -3.4 | 0.537 | 0.614 | 0.602 | -4.24 | 3.53 | 5.34 | Fair_Mixed | 5701.5 | 9502.7 | 1.596 | 0.71 | 4.97 | 0.616 | 5.34 | 0.5421 | 0.8489 | 0.6413 | 0.7404 | 1 | 0.5202 | 0.6396 | 0.6865 | 0.6865 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
971 | 1684.3 | 892.3 | 142 | 184.3 | 29.4 | 1265.8 | 7653.8 | 33.7 | 45.6 | 106.6 | 104.7 | 93.8 | 112.8 | 44.2 | 31.4 | 1176 | 1351.3 | 1307 | 1264.1 | 1559.6 | 1372.3 | 1.075 | 1.154 | 1.05 | 0.945 | 0.906 | 0.919 | 8.79 | -8.26 | 8.77 | 0.802 | 0.889 | 0.768 | -7.1 | -7.5 | 5.86 | 0.861 | 0.728 | 0.758 | 6.75 | 7.85 | 7.51 | 0.697 | 0.826 | 0.857 | 7.01 | 7.76 | 6.47 | Very Poor_Mixed | 1176 | 1264.1 | 1.05 | 0.945 | 8.79 | 0.889 | 7.85 | 0.1102 | 0.6241 | 0.1616 | 0.3444 | 1 | 0.1207 | 0.2672 | 0.3608 | 0.3608 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
972 | 192.5 | 170 | 75.1 | 152.7 | 3.2 | 472.8 | 3648.2 | 52.9 | 26.9 | 103.2 | 106.5 | 92.3 | 112.4 | 43.2 | 12.2 | 7901.7 | 6972.5 | 7465.1 | 14002.5 | 11974 | 12437.7 | 1.772 | 1.717 | 1.666 | 0.638 | 0.53 | 1.764 | -3.39 | 2.97 | -2.36 | 0.61 | 0.564 | 0.551 | 3.1 | 2.93 | 3.73 | 0.588 | 0.638 | 0.587 | -3.47 | 4 | 4.22 | 0.654 | 0.612 | 0.619 | 4.33 | 4.29 | -3.87 | Critical_Thermal | 6972.5 | 11974 | 1.666 | 1.764 | 3.39 | 0.654 | 4.33 | 0.7312 | 0.8397 | 0.1882 | 0.9618 | 1 | 0.6341 | 0.6216 | 0.7111 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H4
973 | 270 | 120 | 69.5 | 55.8 | 1 | 405.8 | 3135.2 | 60 | 20 | 77.9 | 78.4 | 70 | 81.3 | 35.3 | 11.8 | 9628 | 8508.5 | 9614.8 | 19152.5 | 15686.5 | 18887.7 | 1.989 | 1.844 | 1.964 | 0.502 | 0.582 | 0.5 | 2 | -2.62 | 2.22 | 0.529 | 0.556 | 0.5 | 2.5 | 2.45 | 2.42 | 0.5 | 0.545 | 0.531 | -2.32 | 2 | 2.27 | 0.523 | 0.5 | 0.5 | 2.23 | 2 | -2.06 | Good_Mixed | 8508.5 | 15686.5 | 1.844 | 0.582 | 2.62 | 0.556 | 2.5 | 0.948 | 1 | 0.9105 | 0.9703 | 1 | 0.9082 | 0.8911 | 0.9441 | 0.9441 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
974 | 830.6 | 519.6 | 102.7 | 125.8 | 19.6 | 837.6 | 5382.9 | 47.2 | 31.3 | 90.1 | 91.4 | 82.9 | 99.7 | 39 | 24.5 | 6828.1 | 5218.4 | 5499.6 | 10473.8 | 8284.1 | 8459.8 | 1.534 | 1.587 | 1.538 | 0.756 | 0.746 | 0.746 | 6.45 | -5.99 | 5.84 | 0.626 | 0.656 | 0.672 | 3.87 | 4.81 | 4.12 | 0.647 | 0.689 | 0.692 | 5.16 | 5.51 | 3.69 | 0.73 | 0.675 | 0.629 | 4.25 | 4.8 | 4.12 | Poor_Mixed | 5218.4 | 8284.1 | 1.534 | 0.756 | 6.45 | 0.73 | 5.51 | 0.4233 | 0.7791 | 0.5045 | 0.597 | 1 | 0.3845 | 0.4998 | 0.5834 | 0.5834 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
975 | 611.7 | 433.5 | 91.5 | 104.6 | 52.6 | 783 | 4468.7 | 51.5 | 29.5 | 83.2 | 83.3 | 77.7 | 89.5 | 38.1 | 16.4 | 8378 | 8544.7 | 7885.7 | 15874.1 | 15285.3 | 14191.6 | 1.895 | 1.789 | 1.8 | 0.581 | 0.502 | 0.546 | 2.76 | 2 | 2.5 | 0.944 | 0.602 | 0.628 | 9.43 | 3.77 | 3.39 | 0.618 | 0.629 | 0.614 | -2.05 | -4.02 | 3.3 | 0.569 | 0.557 | 0.588 | 4.71 | 3.6 | 2.71 | Critical_Bushing_TD_Cap | 7885.7 | 14191.6 | 1.789 | 0.581 | 2.76 | 0.944 | 9.43 | 0.4193 | 0.8027 | 0.7009 | 0.855 | 1 | 0.8553 | 0.5746 | 0.6972 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
976 | 1001.9 | 529.7 | 101 | 114.4 | 19.3 | 824.9 | 5665.5 | 48.4 | 31.4 | 94.3 | 92.5 | 82.9 | 100.1 | 39.7 | 24 | 6121.6 | 6152.8 | 5348.8 | 10119.4 | 9660.2 | 8012.7 | 1.653 | 1.57 | 1.498 | 0.684 | 0.741 | 0.735 | 5.75 | 6.49 | 6.21 | 0.707 | 0.608 | 0.661 | -3.61 | 4.85 | 5.06 | 0.715 | 0.69 | 0.632 | 3.37 | 4.61 | 5.6 | 0.646 | 0.63 | 0.696 | 4.61 | -3.66 | -4.5 | Poor_Mixed | 5348.8 | 8012.7 | 1.498 | 0.741 | 6.49 | 0.715 | 5.6 | 0.4214 | 0.7778 | 0.4642 | 0.6143 | 1 | 0.4075 | 0.5071 | 0.5842 | 0.5842 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
977 | 1550.8 | 824.3 | 134.7 | 174.3 | 31 | 1176.6 | 7291.6 | 35.9 | 44.5 | 102.7 | 102.7 | 92 | 113 | 43.9 | 33.1 | 2706.9 | 2994.3 | 2262.3 | 3282.4 | 3610.9 | 2816.1 | 1.213 | 1.206 | 1.245 | 0.925 | 0.918 | 0.951 | 7.81 | 8.38 | -8.57 | 0.884 | 0.813 | 0.736 | 6.82 | 6.77 | -7.54 | 0.744 | 0.88 | 0.688 | 7.63 | 8.13 | 5.67 | 0.822 | 0.867 | 0.788 | -6.48 | 7.28 | 7.17 | Very Poor_Mixed | 2262.3 | 2816.1 | 1.206 | 0.951 | 8.57 | 0.884 | 8.13 | 0.1482 | 0.6347 | 0.206 | 0.2787 | 1 | 0.1333 | 0.2649 | 0.3741 | 0.3741 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
978 | 744.5 | 463.4 | 93.7 | 100.3 | 15.3 | 736.8 | 4917.6 | 50.5 | 30.3 | 88.8 | 86.8 | 80.1 | 93.3 | 37.6 | 24 | 6251.9 | 5658.6 | 7070.1 | 10126.1 | 9343 | 11483.3 | 1.62 | 1.651 | 1.624 | 0.669 | 0.688 | 0.658 | 4.96 | 5.05 | -4.17 | 0.647 | 0.664 | 0.609 | -3.7 | 5.64 | 3.58 | 0.591 | 0.636 | 0.616 | 3.08 | 3.6 | -3.78 | 0.614 | 0.644 | 0.701 | 4.6 | 3.23 | -5.1 | Poor_Mixed | 5658.6 | 9343 | 1.62 | 0.688 | 5.05 | 0.701 | 5.64 | 0.5129 | 0.792 | 0.6026 | 0.6143 | 1 | 0.5324 | 0.5613 | 0.6498 | 0.6498 | Fair | 1 | 1 | DGA | 0 |  | C2H2
979 | 444.4 | 360.7 | 86.8 | 79.6 | 2.5 | 690.4 | 4012 | 32.4 | 46.3 | 79.7 | 80.9 | 73.7 | 86.8 | 37 | 11.4 | 5065.9 | 5061.8 | 4704.4 | 7685.2 | 7360.7 | 6701.6 | 1.517 | 1.454 | 1.425 | 0.657 | 0.669 | 0.664 | -22.76 | 4.45 | -4.71 | 0.562 | 0.5 | 0.545 | 2.81 | 2.98 | 2.99 | 0.55 | 0.577 | 0.533 | 3.09 | 3.46 | -3.5 | 0.533 | 0.511 | 0.57 | 3.09 | -2.91 | -2.78 | Critical_Oil | 4704.4 | 6701.6 | 1.425 | 0.669 | 22.76 | 0.577 | 3.5 | 0.7302 | 0.6175 | 0.7984 | 0.9783 | 1 | 0.4532 | 0.7745 | 0.7483 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
980 | 215.9 | 164.9 | 69.4 | 52 | 1.5 | 411.6 | 3007.9 | 58.4 | 22.7 | 82 | 81.5 | 73.9 | 84.2 | 37.4 | 26.7 | 8626.1 | 9043.8 | 8689.6 | 15602.4 | 17920 | 15829 | 1.809 | 1.981 | 1.822 | 0.56 | 0.518 | 0.588 | 3.06 | 3.08 | 3.24 | 0.5 | 0.561 | 0.507 | 2.29 | 2.32 | 2 | 0.555 | 0.524 | 0.5 | 2.18 | 2.66 | -2 | 0.551 | 0.563 | 0.528 | 2.73 | 2.61 | 2.41 | Poor_Age | 8626.1 | 15602.4 | 1.809 | 0.588 | 3.24 | 0.563 | 2.73 | 0.907 | 0.9129 | 0.7833 | 0.5192 | 1 | 0.775 | 0.8441 | 0.861 | 0.861 | Good | 1 | 0 | No_Anomaly | 0 |  | Age_Years
981 | 183.5 | 206.1 | 79.2 | 105.8 | 1.3 | 437.6 | 3146 | 55.4 | 25.2 | 97.3 | 96.8 | 88.9 | 102.9 | 40.8 | 14 | 8843.7 | 9965.5 | 9781.1 | 16623 | 19534.2 | 18716.6 | 1.88 | 1.96 | 1.914 | 0.541 | 0.543 | 0.582 | 3.04 | 2.81 | 2.77 | 0.5 | 0.562 | 0.5 | 2.49 | 2.42 | 2.13 | 0.501 | 0.507 | 0.52 | 2.1 | 2.16 | 2.18 | 0.505 | 0.545 | 0.514 | 2.19 | 2.03 | 2.59 | Poor_Thermal | 8843.7 | 16623 | 1.88 | 0.582 | 3.04 | 0.562 | 2.59 | 0.8341 | 0.8666 | 0.3618 | 0.9194 | 1 | 0.7883 | 0.8961 | 0.8263 | 0.8263 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
982 | 1685.8 | 941.9 | 143.6 | 187.8 | 27 | 1323.1 | 8740.8 | 33.6 | 48.4 | 105.5 | 105.9 | 93.9 | 113.6 | 44.6 | 34.3 | 1356.1 | 2633.1 | 1272.6 | 1423.9 | 3003.7 | 1570.8 | 1.05 | 1.141 | 1.234 | 0.944 | 0.924 | 0.962 | 8.84 | 9.01 | -9.84 | 0.887 | 0.766 | 0.848 | 9.09 | 6.57 | -5.93 | 0.817 | 0.946 | 0.74 | 7.65 | -6.94 | -7.66 | 0.766 | 0.775 | 0.926 | 7.31 | -8.21 | 7.93 | Very Poor_Mixed | 1272.6 | 1423.9 | 1.05 | 0.962 | 9.84 | 0.946 | 9.09 | 0.0916 | 0.5979 | 0.1535 | 0.2316 | 1 | 0.0757 | 0.225 | 0.3327 | 0.3327 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
983 | 1594 | 867.2 | 140.4 | 176.6 | 33.2 | 1347.5 | 7763.3 | 32 | 47.5 | 104.7 | 104.6 | 94.2 | 112.9 | 45.3 | 34.9 | 2045.1 | 1593.5 | 2943.7 | 2295.6 | 1897.1 | 3521.6 | 1.122 | 1.191 | 1.196 | 0.946 | 0.969 | 0.972 | 9.48 | 9.58 | -9.13 | 0.712 | 0.871 | 0.7 | 8.27 | 4.91 | -8.25 | 0.762 | 0.729 | 0.757 | 5.21 | 5.2 | 6.33 | 0.706 | 0.718 | 0.782 | 8.21 | -6.89 | 6.8 | Very Poor_Mixed | 1593.5 | 1897.1 | 1.122 | 0.972 | 9.58 | 0.871 | 8.27 | 0.0996 | 0.6062 | 0.1619 | 0.2078 | 1 | 0.0546 | 0.3317 | 0.3516 | 0.3516 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
984 | 334.5 | 251.5 | 76.3 | 158.4 | 1 | 523.3 | 3017.3 | 14.3 | 22.3 | 108.4 | 108.8 | 97.3 | 119.2 | 45 | 15 | 8731.5 | 9389 | 8928.5 | 16276 | 17463.5 | 17018.8 | 1.864 | 1.86 | 1.906 | 0.631 | 0.641 | 0.688 | -4.49 | -5.26 | 5.31 | 0.576 | 0.5 | 0.593 | 2.43 | 2.56 | 3.69 | 0.552 | 0.554 | 0.545 | 3.31 | 3.04 | -3.11 | 0.538 | 0.555 | 0.538 | 2.99 | 2.96 | 3.06 | Critical_Thermal | 8731.5 | 16276 | 1.86 | 0.688 | 5.31 | 0.593 | 3.69 | 0.791 | 0.3382 | 0.0721 | 0.8935 | 1 | 0.5346 | 0.7578 | 0.6615 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
985 | 1107 | 800.3 | 123.7 | 158.5 | 30.3 | 1141 | 6676.5 | 56.4 | 22.1 | 79.5 | 83 | 76.6 | 88.1 | 37.1 | 12.4 | 8284.6 | 9610.7 | 8412.2 | 15526.6 | 19221.4 | 16605.7 | 1.874 | 2 | 1.974 | 0.5 | 0.574 | 0.503 | 2 | 2.66 | -2 | 0.581 | 0.614 | 0.574 | 2.85 | 3.59 | 3.02 | 0.57 | 0.533 | 0.53 | 2.49 | 2.51 | 2.12 | 0.5 | 0.548 | 0.529 | 2.85 | 3.2 | 3.18 | Poor_DGA | 8284.6 | 15526.6 | 1.874 | 0.574 | 2.66 | 0.614 | 3.59 | 0.2201 | 0.926 | 0.7542 | 0.9575 | 1 | 0.9164 | 0.7621 | 0.7149 | 0.7149 | Fair | 1 | 1 | DGA | 0 |  | C2H2
986 | 344.9 | 302.1 | 82.3 | 77.4 | 8.4 | 529.3 | 3604.6 | 53 | 25.7 | 81.3 | 81.2 | 76.3 | 87.9 | 37.7 | 17 | 7195.5 | 8929.1 | 8437.2 | 12702.2 | 16877.5 | 14403.8 | 1.765 | 1.89 | 1.707 | 0.57 | 0.621 | 0.62 | 3.27 | -3.77 | 3.64 | 0.572 | 0.541 | 0.607 | 2.68 | 3.68 | 3.39 | 0.6 | 0.551 | 0.561 | 3.18 | 2.7 | 3.46 | 0.581 | 0.572 | 0.586 | -4.13 | 3.65 | 2.39 | Fair_Mixed | 7195.5 | 12702.2 | 1.707 | 0.621 | 3.77 | 0.607 | 4.13 | 0.6951 | 0.8584 | 0.753 | 0.8378 | 1 | 0.6775 | 0.6897 | 0.773 | 0.773 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
987 | 1766 | 982.4 | 145.2 | 197 | 33.6 | 1379 | 8689.7 | 60 | 62.1 | 82.5 | 86 | 74.3 | 87.5 | 36.3 | 13.8 | 9365.2 | 9407.1 | 8283.8 | 18291.6 | 18457.3 | 15235.2 | 1.953 | 1.962 | 1.839 | 0.564 | 0.551 | 0.505 | 3.04 | 2.27 | 2.21 | 0.617 | 0.566 | 0.582 | 3.09 | 3.09 | 3.27 | 0.564 | 0.584 | 0.576 | 3.66 | 3.41 | -2.99 | 0.535 | 0.535 | 0.602 | 2.59 | -4.19 | -3.97 | Critical_DGA | 8283.8 | 15235.2 | 1.839 | 0.564 | 3.04 | 0.617 | 4.19 | 0.0371 | 0.5833 | 0.7312 | 0.9244 | 1 | 0.8483 | 0.6883 | 0.6013 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
988 | 449.8 | 265.7 | 78.9 | 64.4 | 52.4 | 570.1 | 3448.9 | 31.3 | 49.4 | 81.5 | 77 | 74.6 | 87.5 | 36.1 | 19.1 | 4511.4 | 5613.9 | 5299.5 | 6193.7 | 8249.8 | 7530 | 1.373 | 1.47 | 1.421 | 0.602 | 0.702 | 0.655 | 4.13 | 4.43 | 4.12 | 0.592 | 0.6 | 0.586 | 3.16 | 2.77 | 3.52 | 0.581 | 0.614 | 0.631 | 3.96 | -4.38 | 3.71 | 0.62 | 0.597 | 0.587 | 3.77 | 3.53 | 3.26 | Critical_Oil | 4511.4 | 6193.7 | 1.373 | 0.702 | 4.43 | 0.631 | 4.38 | 0.5453 | 0.5888 | 0.8136 | 0.7749 | 1 | 0.5826 | 0.63 | 0.682 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
989 | 713 | 339 | 91 | 109.8 | 12.8 | 651.3 | 3756.6 | 49.4 | 30.9 | 90.1 | 87.9 | 78.5 | 92.3 | 38.3 | 20.5 | 6478.1 | 6906.2 | 6913.4 | 11507.3 | 12066.9 | 11845.1 | 1.776 | 1.747 | 1.713 | 0.7 | 0.691 | 0.698 | -5.43 | 4.74 | 5.52 | 0.63 | 0.652 | 0.563 | 3.62 | 3.78 | 3.42 | 0.626 | 0.575 | 0.594 | 2.85 | 3.88 | -2.83 | 0.607 | 0.612 | 0.715 | 4.11 | 4.28 | -4.49 | Fair_Mixed | 6478.1 | 11507.3 | 1.713 | 0.7 | 5.52 | 0.715 | 4.49 | 0.5614 | 0.7842 | 0.598 | 0.7308 | 1 | 0.4797 | 0.6005 | 0.666 | 0.666 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
990 | 100 | 155.9 | 73.7 | 50 | 1.3 | 404.4 | 3149.4 | 56.2 | 22.3 | 83.1 | 85.7 | 78.3 | 90.1 | 37.9 | 15.4 | 76.8 | 1942.2 | 1097.4 | 92.6 | 2230.5 | 1140.9 | 1.206 | 1.148 | 1.04 | 0.747 | 0.674 | 0.709 | 5.29 | -5.02 | 5.34 | 0.502 | 0.5 | 0.523 | -2.06 | 2.82 | -2.34 | 0.528 | 0.534 | 0.5 | -2.76 | 2 | 2.35 | 0.515 | 0.513 | 0.55 | 2.19 | 2.36 | 2.14 | Critical_IR_PI | 76.8 | 92.6 | 1.04 | 0.747 | 5.34 | 0.55 | 2.82 | 0.9367 | 0.9215 | 0.6778 | 0.8828 | 0.85 | 0.4684 | 0.8823 | 0.8171 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_HV_TanDelta_pct
991 | 1314.7 | 830 | 131.7 | 168 | 31.3 | 1162.5 | 7798.5 | 35.1 | 44.3 | 105.6 | 103.3 | 92.5 | 112.8 | 43.7 | 31.6 | 2599.1 | 2898.3 | 2942.7 | 3278.5 | 3712.6 | 3781.3 | 1.261 | 1.281 | 1.285 | 0.99 | 0.953 | 0.948 | 9.18 | 8.76 | -8.72 | 0.851 | 0.713 | 0.831 | -5.05 | 7.03 | 6.71 | 0.776 | 0.838 | 0.772 | 4.92 | 6.78 | 6.21 | 0.825 | 0.853 | 0.781 | 5.88 | -6.46 | -7.03 | Very Poor_Mixed | 2599.1 | 3278.5 | 1.261 | 0.99 | 9.18 | 0.853 | 7.03 | 0.1663 | 0.6367 | 0.1859 | 0.3368 | 1 | 0.0794 | 0.2889 | 0.3765 | 0.3765 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
992 | 1518.3 | 864.6 | 135.7 | 179.5 | 34.3 | 1195.5 | 8064 | 37.3 | 45.3 | 104.1 | 99.5 | 90.4 | 109.6 | 44.1 | 31.6 | 1950.3 | 1833.4 | 2311 | 2152.4 | 2179.5 | 2530.1 | 1.104 | 1.189 | 1.095 | 0.961 | 0.879 | 0.904 | 8.47 | 8.39 | 8.51 | 0.819 | 0.824 | 0.774 | -6.8 | 8.12 | 5.75 | 0.847 | 0.865 | 0.773 | -5.63 | 4.72 | -6 | 0.864 | 0.854 | 0.79 | 7.36 | 5.2 | -5.77 | Very Poor_Mixed | 1833.4 | 2152.4 | 1.095 | 0.961 | 8.51 | 0.865 | 8.12 | 0.1146 | 0.627 | 0.2412 | 0.3368 | 1 | 0.1346 | 0.2734 | 0.3729 | 0.3729 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
993 | 1495.7 | 906.8 | 132.4 | 170 | 33.2 | 1226.5 | 8327 | 36.5 | 43.5 | 105.6 | 103.8 | 93.3 | 113.3 | 43.7 | 33.6 | 1699.8 | 1954.6 | 3642.8 | 1939.6 | 2367.3 | 4707.5 | 1.141 | 1.211 | 1.292 | 0.94 | 0.88 | 0.94 | 9.84 | 8.11 | 8.94 | 0.83 | 0.865 | 0.754 | 6.33 | 6.37 | 5.26 | 0.959 | 0.867 | 0.859 | -7.65 | 7.81 | 7.38 | 0.837 | 0.844 | 0.892 | 6.24 | -6.34 | -9.1 | Very Poor_Mixed | 1699.8 | 1939.6 | 1.141 | 0.94 | 9.84 | 0.959 | 9.1 | 0.1201 | 0.6445 | 0.1761 | 0.2591 | 1 | 0.1054 | 0.2172 | 0.3518 | 0.3518 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
994 | 1047.3 | 495.1 | 115.9 | 123.1 | 18.9 | 815.6 | 5863.2 | 55.8 | 22.6 | 79.5 | 82.5 | 70.6 | 83.1 | 36.2 | 12.6 | 8556.3 | 8739.8 | 8097.9 | 15988.2 | 16106.3 | 14645.8 | 1.869 | 1.843 | 1.809 | 0.589 | 0.518 | 0.576 | 3.31 | 2 | -3.47 | 0.521 | 0.57 | 0.5 | 2.3 | -2.46 | -2 | 0.511 | 0.572 | 0.543 | -2.45 | -2.79 | -2.21 | 0.522 | 0.5 | 0.518 | -2.92 | 2.45 | 2.64 | Poor_DGA | 8097.9 | 14645.8 | 1.809 | 0.589 | 3.47 | 0.572 | 2.92 | 0.4039 | 0.915 | 0.8385 | 0.953 | 1 | 0.7847 | 0.8472 | 0.7646 | 0.7646 | Fair | 1 | 1 | DGA | 0 |  | C2H2
995 | 547.3 | 434.6 | 91.3 | 83.5 | 10.1 | 665.4 | 4080.7 | 52.3 | 28.8 | 83.9 | 86.1 | 77.9 | 89.8 | 37.7 | 15.5 | 8568.3 | 7475.5 | 8213.6 | 15676.4 | 12955.8 | 14917.4 | 1.83 | 1.733 | 1.816 | 0.597 | 0.615 | 0.627 | 3.57 | -3.64 | -3.72 | 0.552 | 0.597 | 0.644 | 3.97 | 3.22 | 2.95 | 0.564 | 0.576 | 0.571 | 3.53 | 3.39 | 4.58 | 0.579 | 0.572 | 0.579 | 3.56 | 3.4 | 3.16 | Fair_Mixed | 7475.5 | 12955.8 | 1.733 | 0.627 | 3.72 | 0.644 | 4.58 | 0.6097 | 0.8123 | 0.6743 | 0.88 | 1 | 0.6599 | 0.6651 | 0.7334 | 0.7334 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
996 | 1622.8 | 899.9 | 143.8 | 189.5 | 34.3 | 1284 | 8491.3 | 31.1 | 48 | 107.6 | 104.3 | 92.8 | 112.8 | 43.5 | 31.8 | 690 | 690 | 943.8 | 1200 | 1200 | 1200 | 1.739 | 1.739 | 1.271 | 0.947 | 0.917 | 0.912 | 8.98 | 9.12 | 8.45 | 0.901 | 0.792 | 0.803 | 8.98 | 8.74 | 7.35 | 0.903 | 0.785 | 0.823 | 7.47 | -5.66 | 6.53 | 0.859 | 0.708 | 0.731 | 8.27 | 8.63 | -8.35 | Very Poor_Mixed | 690 | 1200 | 1.271 | 0.947 | 9.12 | 0.903 | 8.98 | 0.0732 | 0.6016 | 0.169 | 0.3291 | 1 | 0.107 | 0.2327 | 0.3407 | 0.3407 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
997 | 120.1 | 120 | 66.5 | 51.5 | 3.6 | 368.2 | 2500 | 58.9 | 21.3 | 78.6 | 78.2 | 72.6 | 84 | 36.7 | 12.4 | 10000 | 8589.6 | 9246.3 | 19420.3 | 16260 | 16511.8 | 1.942 | 1.893 | 1.786 | 0.509 | 0.523 | 0.573 | -2.22 | 2.17 | 2.75 | 0.5 | 0.649 | 0.522 | 2.47 | 4.79 | 2.32 | 0.571 | 0.513 | 0.533 | -2.7 | -2 | 3.28 | 0.541 | 0.524 | 0.525 | 2.72 | 2.99 | 2 | Fair_Bushing_TD_Cap | 8589.6 | 16260 | 1.786 | 0.573 | 2.75 | 0.649 | 4.79 | 0.8851 | 0.9458 | 0.8574 | 0.9575 | 1 | 0.8657 | 0.7984 | 0.8933 | 0.8933 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
998 | 131.1 | 120 | 68.9 | 54.5 | 2.7 | 350 | 2514.8 | 59.3 | 21.3 | 75.7 | 83.5 | 73.3 | 82.3 | 35.8 | 12 | 9549 | 9652.1 | 8987.4 | 19098.1 | 17844.3 | 16514.2 | 2 | 1.849 | 1.837 | 0.557 | 0.512 | 0.553 | -2.37 | -2.61 | 2.85 | 0.515 | 0.5 | 0.5 | 2.74 | 2.17 | 2 | 0.528 | 0.5 | 0.5 | 2 | -2 | 2.17 | 0.5 | 0.5 | 0.53 | 2 | -2.23 | 2.29 | Good_Mixed | 8987.4 | 16514.2 | 1.837 | 0.557 | 2.85 | 0.53 | 2.74 | 0.8989 | 0.9458 | 0.8515 | 0.9661 | 1 | 0.8342 | 0.9439 | 0.9184 | 0.9184 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
999 | 132.3 | 212.8 | 65 | 52.6 | 1 | 410.9 | 2603 | 53.8 | 24.1 | 80.9 | 80.2 | 75.6 | 84.9 | 36.7 | 22.5 | 10000 | 9187.7 | 8466.8 | 20000 | 18118.3 | 15782.4 | 2 | 1.972 | 1.864 | 0.524 | 0.585 | 0.571 | 2.06 | 3.02 | -2.28 | 0.545 | 0.576 | 0.5 | 2 | 2.34 | -2.1 | 0.533 | 0.501 | 0.532 | -2 | 2.14 | 2.75 | 0.507 | 0.5 | 0.514 | 2.82 | 2 | 2.87 | Poor_Age | 8466.8 | 15782.4 | 1.864 | 0.585 | 3.02 | 0.576 | 2.87 | 0.9611 | 0.8857 | 0.7903 | 0.6652 | 1 | 0.8158 | 0.8752 | 0.8906 | 0.8906 | Good | 1 | 0 | No_Anomaly | 0 |  | Age_Years
1000 | 873.1 | 472.8 | 97.3 | 110.6 | 17.2 | 810.1 | 5271.5 | 56.8 | 22.8 | 77.9 | 75 | 70.3 | 82 | 35.3 | 13.2 | 9581.9 | 9108.9 | 9695.4 | 18588.6 | 17083.3 | 18869.6 | 1.94 | 1.875 | 1.946 | 0.519 | 0.589 | 0.53 | 2.44 | -2.79 | 3.21 | 0.534 | 0.5 | 0.508 | 2.52 | 2.17 | 2.18 | 0.5 | 0.55 | 0.511 | 2.29 | -2 | 2 | 0.528 | 0.507 | 0.519 | 2 | 2 | 2 | Poor_DGA | 9108.9 | 17083.3 | 1.875 | 0.589 | 3.21 | 0.55 | 2.52 | 0.4631 | 0.9108 | 0.9455 | 0.939 | 1 | 0.8126 | 0.8974 | 0.8019 | 0.8019 | Good | 1 | 1 | DGA | 0 |  | C2H2
1001 | 1549.2 | 916.5 | 136.5 | 184.9 | 30 | 1263.2 | 8047.7 | 36.4 | 45.6 | 102.6 | 105.3 | 95.8 | 114.2 | 45 | 30.3 | 3971.2 | 1642 | 3330.4 | 5132 | 1951.8 | 4177.4 | 1.292 | 1.189 | 1.254 | 0.941 | 0.916 | 0.896 | -8.85 | -8.22 | 7.73 | 0.854 | 0.768 | 0.907 | -8.32 | 7.4 | 6.16 | 0.848 | 0.826 | 0.899 | -6.27 | 7.16 | 8.11 | 0.842 | 0.824 | 0.818 | 6.15 | 5.91 | 5.7 | Very Poor_Mixed | 1642 | 1951.8 | 1.189 | 0.941 | 8.85 | 0.907 | 8.32 | 0.1135 | 0.6241 | 0.1567 | 0.3863 | 1 | 0.1421 | 0.2334 | 0.3602 | 0.3602 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1002 | 277 | 243.2 | 79.9 | 150.1 | 2.4 | 504.9 | 3853.6 | 54.4 | 66.2 | 109.3 | 107.4 | 97 | 118.6 | 45.1 | 13 | 7231.2 | 5885.7 | 6185 | 12280.5 | 9265.3 | 10099.5 | 1.698 | 1.574 | 1.633 | 0.566 | 0.554 | 0.523 | 2.94 | 2.65 | 2.84 | 0.512 | 0.529 | 0.531 | 2 | 2.25 | 2.86 | 0.532 | 0.535 | 0.511 | -2 | 2.25 | -3.19 | 0.529 | 0.5 | 0.527 | 2.79 | -2.07 | 2.37 | Critical_Thermal | 5885.7 | 9265.3 | 1.574 | 0.566 | 2.94 | 0.535 | 3.19 | 0.7235 | 0.5833 | 0.0788 | 0.9438 | 1 | 0.8057 | 0.8545 | 0.7325 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1003 | 215.1 | 248.1 | 74.3 | 81.4 | 4.3 | 435.7 | 3501.1 | 57.9 | 22.7 | 83.7 | 81.2 | 76.3 | 89.4 | 36.8 | 12 | 1532.9 | 1037.2 | 367.8 | 1661.8 | 1121.7 | 562.7 | 1.084 | 1.081 | 1.53 | 0.75 | 0.685 | 0.805 | 6.17 | 5.79 | 6.11 | 0.586 | 0.589 | 0.546 | -2.35 | -2.12 | 2.41 | 0.585 | 0.522 | 0.511 | -3.13 | 3.38 | -3.13 | 0.566 | 0.604 | 0.526 | 3.05 | 3.85 | -3.11 | Critical_IR_PI | 367.8 | 562.7 | 1.081 | 0.805 | 6.17 | 0.604 | 3.85 | 0.7794 | 0.9129 | 0.7315 | 0.9661 | 0.85 | 0.3923 | 0.7401 | 0.75 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1004 | 259.2 | 222.7 | 72.4 | 58.5 | 1.2 | 427.5 | 2975.7 | 59.2 | 20.2 | 78.7 | 79.7 | 74.6 | 86 | 36.4 | 11.8 | 8229.2 | 159.5 | 9844.4 | 14764.2 | 242.5 | 19599.1 | 1.794 | 1.52 | 1.991 | 0.605 | 0.627 | 0.626 | 3.14 | 4.08 | 3.53 | 0.972 | 0.543 | 0.588 | -9.57 | 3.63 | -2.34 | 0.533 | 0.528 | 0.692 | 4.67 | 2.95 | -2.9 | 0.63 | 0.528 | 0.599 | 3.76 | 3.11 | 2.81 | Critical_Bushing_TD_Cap | 159.5 | 242.5 | 1.52 | 0.627 | 4.08 | 0.972 | 9.57 | 0.895 | 0.984 | 0.8178 | 0.9703 | 0.85 | 0.6567 | 0.6186 | 0.8114 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Bushing_HV_R_TanDelta_pct
1005 | 109.8 | 136.9 | 70.7 | 55.2 | 46.7 | 350 | 2928.8 | 51.6 | 27.6 | 81 | 85.3 | 75.9 | 88.1 | 37 | 15.9 | 9270.4 | 9795.7 | 8223.8 | 16612.9 | 18526.5 | 14537.1 | 1.792 | 1.891 | 1.768 | 0.552 | 0.619 | 0.569 | 3.26 | 3.66 | 4.1 | 0.598 | 0.635 | 0.541 | 2.73 | 4.01 | 4.18 | 0.987 | 0.615 | 0.636 | 9.35 | -3.65 | 3.38 | 0.576 | 0.588 | 0.628 | 4.21 | 2.49 | 3.36 | Critical_Bushing_TD_Cap | 8223.8 | 14537.1 | 1.768 | 0.619 | 4.1 | 0.987 | 9.35 | 0.6587 | 0.8293 | 0.7296 | 0.869 | 1 | 0.7017 | 0.5671 | 0.7409 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1006 | 1009.1 | 517.7 | 104.3 | 138.2 | 21.3 | 830.6 | 5848.5 | 44.4 | 33.7 | 91.4 | 88.1 | 82.2 | 97.5 | 39.3 | 26.8 | 5563.1 | 5155.2 | 5764.6 | 8457.3 | 7602 | 8673.6 | 1.52 | 1.475 | 1.505 | 0.765 | 0.723 | 0.774 | 5.88 | 5.43 | 5.61 | 0.679 | 0.699 | 0.704 | -4.22 | 6.14 | 4.85 | 0.684 | 0.638 | 0.649 | -5.25 | 4 | -4.99 | 0.718 | 0.612 | 0.708 | -4.91 | 4.97 | 5.31 | Poor_Mixed | 5155.2 | 7602 | 1.475 | 0.774 | 5.88 | 0.718 | 6.14 | 0.383 | 0.7497 | 0.5316 | 0.5156 | 1 | 0.4058 | 0.4718 | 0.5664 | 0.5664 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1007 | 1554.2 | 796 | 131.1 | 182 | 31.3 | 1177.7 | 7852.9 | 55.6 | 82.9 | 81.3 | 80.5 | 73.9 | 85.3 | 36.2 | 17.6 | 6837.5 | 7096.7 | 6862.1 | 11644.7 | 12376.3 | 11924.6 | 1.703 | 1.744 | 1.738 | 0.628 | 0.515 | 0.615 | -3.99 | 2.63 | 3.56 | 0.609 | 0.596 | 0.53 | 3.44 | 2.91 | -2.46 | 0.561 | 0.563 | 0.588 | 2.85 | 3.29 | 2.08 | 0.543 | 0.569 | 0.58 | -3.34 | -2.54 | 3.75 | Critical_DGA | 6837.5 | 11644.7 | 1.703 | 0.628 | 3.99 | 0.609 | 3.75 | 0.139 | 0.5833 | 0.7981 | 0.8203 | 1 | 0.7216 | 0.7109 | 0.6145 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
1008 | 1465.5 | 761.8 | 126.4 | 162.5 | 34.3 | 1117.1 | 6911.3 | 35.7 | 44.8 | 105.4 | 105.2 | 93.5 | 117.9 | 44.1 | 32.2 | 1157 | 1342 | 2418.2 | 1271 | 1609.8 | 2927.4 | 1.099 | 1.2 | 1.211 | 0.911 | 0.924 | 0.87 | -7.85 | 8.51 | 8.14 | 0.924 | 0.914 | 0.716 | 6.65 | 6.56 | 6.28 | 0.707 | 0.878 | 0.849 | 7.97 | 7.34 | 8.86 | 0.759 | 0.752 | 0.808 | 7.33 | 8.84 | 6.03 | Very Poor_Mixed | 1157 | 1271 | 1.099 | 0.924 | 8.51 | 0.924 | 8.86 | 0.1745 | 0.6318 | 0.1424 | 0.3137 | 1 | 0.1583 | 0.2485 | 0.3763 | 0.3763 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1009 | 535.1 | 352.7 | 89.3 | 85 | 1 | 594.2 | 4740.7 | 56.5 | 22.8 | 80.5 | 76.6 | 72.1 | 82.7 | 35 | 22.1 | 7628.8 | 7961.1 | 8797 | 13473.9 | 7776 | 16533.3 | 1.766 | 0.977 | 1.879 | 0.58 | 0.569 | 0.549 | 3.93 | 3.47 | -2.5 | 0.518 | 0.975 | 0.714 | 2.15 | 9.67 | 3.75 | 0.644 | 0.63 | 0.633 | -4.3 | -3.94 | -2.68 | 0.502 | 0.571 | 0.653 | 4.01 | 3.7 | 4.73 | Critical_Bushing_TD_Cap | 7628.8 | 7776 | 0.977 | 0.58 | 3.93 | 0.975 | 9.67 | 0.8006 | 0.9108 | 0.8756 | 0.6786 | 0.8187 | 0.7443 | 0.5724 | 0.7692 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_LV
1010 | 489.1 | 303.3 | 79.2 | 83.6 | 9.8 | 622.1 | 4150.5 | 52.9 | 23.8 | 78.8 | 82.7 | 74.1 | 88.4 | 36.6 | 15.2 | 7523.3 | 7304.1 | 9031.1 | 13281.4 | 12598.7 | 16524.2 | 1.765 | 1.725 | 1.83 | 0.633 | 0.648 | 0.648 | -3.26 | 4.26 | 5.05 | 0.596 | 0.658 | 0.581 | -3.42 | -3.35 | 3.71 | 0.629 | 0.553 | 0.604 | 2.42 | 3.63 | -2.8 | 0.609 | 0.577 | 0.61 | -4.09 | -3.05 | 3.48 | Fair_Mixed | 7304.1 | 12598.7 | 1.725 | 0.648 | 5.05 | 0.658 | 4.09 | 0.6457 | 0.8912 | 0.7829 | 0.8882 | 1 | 0.5941 | 0.6407 | 0.7496 | 0.7496 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1011 | 367.3 | 308.2 | 78.1 | 88.8 | 13.3 | 607.7 | 3496 | 57.1 | 21 | 77.7 | 77.1 | 70.1 | 84.6 | 35.3 | 10.5 | 9952.6 | 9241.5 | 8983.8 | 19471 | 17231.3 | 17447.9 | 1.956 | 1.865 | 1.942 | 0.502 | 0.504 | 0.5 | 2.65 | 2 | 2 | 0.59 | 0.527 | 0.572 | -2.69 | 2.49 | 2.63 | 0.5 | 0.527 | 0.5 | 2.79 | 2.05 | -2.51 | 0.502 | 0.562 | 0.5 | 2.08 | 2.65 | 3.25 | Fair_DGA | 8983.8 | 17231.3 | 1.865 | 0.504 | 2.65 | 0.59 | 3.25 | 0.6296 | 0.9543 | 0.9071 | 0.994 | 1 | 0.9653 | 0.8483 | 0.8602 | 0.8602 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1012 | 366.3 | 205.1 | 71.6 | 69.1 | 1 | 535.4 | 3226.5 | 58.8 | 22.7 | 77.3 | 82.1 | 72 | 84.2 | 37.8 | 13.8 | 1133.5 | 1978.7 | 690 | 1156.1 | 2201.8 | 703.8 | 1.02 | 1.113 | 1.02 | 0.721 | 0.748 | 0.669 | 5.55 | -5.18 | 5.53 | 0.672 | 0.605 | 0.62 | -5.19 | -3.24 | 2.83 | 0.574 | 0.632 | 0.579 | 3.19 | 2.98 | -3.82 | 1.775 | 0.58 | 0.58 | 3.87 | -3.19 | 3.88 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.748 | 5.55 | 1.775 | 5.19 | 0.8845 | 0.9129 | 0.8347 | 0.9244 | 0.925 | 0.4548 | 0.5802 | 0.7765 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_TV_R_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_LV_TanDelta_pct
1013 | 153.7 | 134 | 67.8 | 55.5 | 1 | 395.3 | 2886 | 60 | 20 | 78.3 | 75 | 72.7 | 85 | 35 | 11.7 | 9566.1 | 9230.6 | 8362.1 | 18493 | 17613.1 | 15076.1 | 1.933 | 1.908 | 1.803 | 0.525 | 0.521 | 0.5 | 2 | 2.2 | 2.08 | 0.501 | 0.5 | 0.621 | -2.5 | 3.03 | 4.5 | 0.5 | 0.572 | 0.502 | -2.16 | -2.04 | 3.84 | 0.526 | 0.513 | 0.513 | -2.11 | 2.57 | -2.05 | Fair_Bushing_TD_Cap | 8362.1 | 15076.1 | 1.803 | 0.525 | 2.2 | 0.621 | 4.5 | 0.9632 | 1 | 0.9033 | 0.9724 | 1 | 0.9339 | 0.8539 | 0.9442 | 0.9442 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_HV_B_TanDelta_pct
1014 | 987.8 | 509.1 | 112.7 | 127.7 | 23.6 | 789.5 | 5866.9 | 42.6 | 36.8 | 91.5 | 89.5 | 81.1 | 96.8 | 39.9 | 25.3 | 3985.6 | 5118.3 | 4331.9 | 5797.6 | 7507.8 | 5973.2 | 1.455 | 1.467 | 1.379 | 0.732 | 0.736 | 0.728 | 6.11 | 4.96 | 5.61 | 0.6 | 0.716 | 0.623 | 4.64 | 3.9 | 5.84 | 0.718 | 0.694 | 0.726 | 5.58 | 4.76 | 5.55 | 0.744 | 0.694 | 0.637 | -4.85 | -4.04 | -4.49 | Poor_Mixed | 3985.6 | 5797.6 | 1.379 | 0.736 | 6.11 | 0.744 | 5.84 | 0.3816 | 0.7142 | 0.5283 | 0.569 | 1 | 0.429 | 0.4696 | 0.567 | 0.567 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1015 | 411.8 | 253.4 | 78.4 | 56.4 | 1 | 534.4 | 3409.4 | 57.9 | 22.2 | 78.2 | 76.6 | 70 | 84.3 | 35 | 12.8 | 10000 | 9674.3 | 9114.7 | 20000 | 18766.6 | 16444.8 | 2 | 1.94 | 1.804 | 0.614 | 0.629 | 0.607 | 3.71 | 4.29 | -4.49 | 0.5 | 0.503 | 0.5 | -2.45 | 2 | 2 | 0.509 | 0.5 | 0.517 | 2.25 | -2.98 | 2.09 | 0.5 | 0.505 | 0.517 | 2.96 | -2.02 | 2.08 | Fair_Winding_TD_Cap | 9114.7 | 16444.8 | 1.804 | 0.629 | 4.49 | 0.517 | 2.98 | 0.8886 | 0.9238 | 0.9122 | 0.9484 | 1 | 0.6239 | 0.9366 | 0.8876 | 0.8876 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1016 | 511.5 | 245.4 | 86.1 | 80.6 | 10.5 | 594.9 | 3934.2 | 52.5 | 26.6 | 79.6 | 81.9 | 74.4 | 87 | 35.7 | 18.3 | 8281.2 | 8051.7 | 7873.1 | 15299.3 | 14721.4 | 14459.3 | 1.847 | 1.828 | 1.837 | 0.612 | 0.638 | 0.631 | 3.89 | 4.3 | 4.42 | 0.566 | 0.575 | 0.591 | 2.78 | -3.55 | -3.47 | 0.584 | 0.569 | 0.608 | 4.22 | 3.37 | 3.73 | 0.549 | 0.551 | 0.584 | 3.01 | 4.29 | -2.76 | Fair_Mixed | 7873.1 | 14459.3 | 1.828 | 0.638 | 4.42 | 0.608 | 4.29 | 0.6492 | 0.8443 | 0.7909 | 0.7993 | 1 | 0.6098 | 0.6785 | 0.7502 | 0.7502 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1017 | 1575.8 | 960.7 | 147.9 | 187.4 | 34.3 | 1231 | 8290.1 | 34.3 | 47.8 | 108.8 | 108.8 | 92.6 | 119.2 | 44.2 | 34.3 | 690 | 1029.1 | 2100 | 1200 | 1200 | 2394.9 | 1.739 | 1.166 | 1.14 | 0.951 | 0.963 | 0.964 | 9.84 | -9.4 | 8.93 | 0.803 | 0.715 | 0.93 | 7.35 | -7.1 | 7.97 | 0.948 | 0.874 | 0.812 | 8.02 | 8 | 6.99 | 0.787 | 0.754 | 0.929 | -7.09 | -8.35 | 7.19 | Very Poor_Mixed | 690 | 1200 | 1.14 | 0.964 | 9.84 | 0.948 | 8.35 | 0.0769 | 0.6035 | 0.1018 | 0.2316 | 1 | 0.0569 | 0.2144 | 0.32 | 0.32 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1018 | 144.8 | 270.9 | 65 | 50 | 3.7 | 447.7 | 2678.6 | 55.8 | 21.3 | 78.7 | 78.9 | 70.4 | 83.9 | 36.7 | 16.5 | 8547.1 | 9147.1 | 9629.3 | 16341.6 | 17044.8 | 18999.3 | 1.912 | 1.863 | 1.973 | 0.502 | 0.526 | 0.566 | -2.24 | -2.54 | 3.26 | 0.501 | 0.553 | 0.528 | 2.16 | 3.5 | 2 | 0.574 | 0.522 | 0.56 | -2.92 | -2.53 | 2.5 | 0.528 | 0.518 | 0.51 | 2.97 | 2 | 2.27 | Good_Mixed | 8547.1 | 16341.6 | 1.863 | 0.566 | 3.26 | 0.574 | 3.5 | 0.8511 | 0.9458 | 0.8723 | 0.8522 | 1 | 0.8545 | 0.8241 | 0.8841 | 0.8841 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1019 | 746.2 | 565.2 | 100.2 | 119.7 | 18.2 | 783.5 | 5344.5 | 45.7 | 33.7 | 92.6 | 90.8 | 83.6 | 98.5 | 40.9 | 24.2 | 7319.6 | 7421 | 6411.3 | 12101.9 | 12355.4 | 9866 | 1.653 | 1.665 | 1.539 | 0.756 | 0.715 | 0.757 | 6.1 | -5.98 | 5.66 | 0.601 | 0.622 | 0.591 | 4.96 | 3.6 | 3.7 | 0.605 | 0.644 | 0.633 | 3.69 | 3.75 | 3.97 | 0.699 | 0.628 | 0.676 | 4.74 | 3.95 | 4.54 | Poor_Mixed | 6411.3 | 9866 | 1.539 | 0.757 | 6.1 | 0.699 | 4.96 | 0.4482 | 0.7497 | 0.4817 | 0.6074 | 1 | 0.4003 | 0.5618 | 0.5977 | 0.5977 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1020 | 705.9 | 406.4 | 100.3 | 97.3 | 15.3 | 656.6 | 4839.7 | 50.3 | 30.5 | 87.6 | 86.4 | 77.3 | 92 | 37.6 | 19.4 | 6137.3 | 7694.6 | 7182 | 10105.1 | 13525.9 | 12231.1 | 1.647 | 1.758 | 1.703 | 0.637 | 0.629 | 0.598 | 4.65 | 3.55 | 3.44 | 0.626 | 0.631 | 0.649 | 4 | 3.47 | 4.04 | 0.622 | 0.673 | 0.616 | -3.44 | 3.98 | -4.15 | 0.679 | 0.685 | 0.611 | 4.43 | -4.14 | 5.18 | Fair_Mixed | 6137.3 | 10105.1 | 1.647 | 0.637 | 4.65 | 0.685 | 5.18 | 0.5326 | 0.7894 | 0.6393 | 0.7656 | 1 | 0.6366 | 0.547 | 0.6777 | 0.6777 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1021 | 511.7 | 361.9 | 80.3 | 81.9 | 8.3 | 616.5 | 3945.8 | 54.5 | 27.9 | 86.3 | 86.6 | 76 | 93.1 | 39.1 | 18.9 | 6959 | 7199 | 7587.4 | 11443.6 | 12160.7 | 13395.6 | 1.644 | 1.689 | 1.766 | 0.577 | 0.592 | 0.62 | -3.86 | 4 | 3.9 | 0.542 | 0.585 | 0.592 | 3.81 | 3.65 | -4.38 | 0.609 | 0.538 | 0.604 | 3.38 | 4.1 | -3.29 | 0.601 | 0.59 | 0.592 | 3.64 | -4.47 | 3.66 | Fair_Mixed | 6959 | 11443.6 | 1.644 | 0.62 | 4 | 0.609 | 4.47 | 0.6547 | 0.825 | 0.6419 | 0.7811 | 1 | 0.6633 | 0.6501 | 0.7358 | 0.7358 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1022 | 916.2 | 550.5 | 106.7 | 120 | 15.2 | 746.4 | 5228.6 | 44.4 | 37.5 | 90.2 | 91.9 | 83.4 | 95.6 | 41.2 | 25.1 | 5929.3 | 5173.6 | 5298.2 | 9488 | 7691 | 8096.8 | 1.6 | 1.487 | 1.528 | 0.76 | 0.659 | 0.687 | -6.67 | -4.43 | 5.28 | 0.661 | 0.622 | 0.739 | 3.58 | -4.24 | 5.47 | 0.616 | 0.697 | 0.745 | 4.57 | 5.01 | -4.05 | 0.651 | 0.661 | 0.741 | 4.6 | 5.26 | 3.08 | Poor_Mixed | 5173.6 | 7691 | 1.487 | 0.76 | 6.67 | 0.745 | 5.47 | 0.4568 | 0.7065 | 0.5038 | 0.576 | 1 | 0.4639 | 0.488 | 0.591 | 0.591 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1023 | 849.9 | 562 | 108.6 | 121.9 | 14.9 | 861 | 4731 | 58.5 | 21.3 | 79.6 | 81.6 | 71.3 | 84.5 | 37.4 | 13.8 | 9163.1 | 9485.2 | 9451.7 | 17110 | 18334.2 | 17318 | 1.867 | 1.933 | 1.832 | 0.532 | 0.5 | 0.546 | -3.32 | 2.49 | 2.5 | 0.542 | 0.52 | 0.572 | 2 | 3.48 | 2.35 | 0.526 | 0.545 | 0.546 | 2.72 | 2.4 | 2.53 | 0.544 | 0.541 | 0.5 | 2.78 | 2 | 2.01 | Poor_DGA | 9163.1 | 17110 | 1.832 | 0.546 | 3.32 | 0.572 | 3.48 | 0.45 | 0.9458 | 0.8241 | 0.9244 | 1 | 0.8605 | 0.8146 | 0.7817 | 0.7817 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1024 | 432 | 325.1 | 81.7 | 81.7 | 10.3 | 601.8 | 3855 | 53.7 | 26 | 79.7 | 81.4 | 72.9 | 85.3 | 36.9 | 15.1 | 8599.7 | 8441.7 | 9188.5 | 15948.2 | 15469.6 | 17478 | 1.855 | 1.833 | 1.902 | 0.6 | 0.516 | 0.588 | -3.86 | -2.81 | 3.37 | 0.509 | 0.614 | 0.562 | 2.74 | -3.06 | 3.37 | 0.549 | 0.57 | 0.624 | -2.96 | -2.86 | 3.59 | 0.522 | 0.525 | 0.566 | 2 | 2.6 | 2.95 | Fair_Mixed | 8441.7 | 15469.6 | 1.833 | 0.6 | 3.86 | 0.624 | 3.59 | 0.6497 | 0.8536 | 0.8089 | 0.8908 | 1 | 0.745 | 0.7428 | 0.7883 | 0.7883 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1025 | 1491.4 | 844.5 | 139.2 | 177.1 | 33.8 | 1206 | 7835.8 | 35.6 | 46.6 | 105.9 | 108.1 | 94.1 | 117.1 | 44.2 | 32.3 | 1364.4 | 1309.2 | 690 | 1502.5 | 1375.3 | 1200 | 1.101 | 1.05 | 1.739 | 0.975 | 0.898 | 0.946 | 9.62 | 8.44 | 9.84 | 0.925 | 0.931 | 0.764 | 6.59 | -7.46 | 7.25 | 0.93 | 0.888 | 0.878 | 6.7 | 7.35 | -8.5 | 0.895 | 0.87 | 0.847 | 7.14 | -6.52 | 9.35 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.975 | 9.84 | 0.931 | 9.35 | 0.1219 | 0.6147 | 0.1236 | 0.3098 | 1 | 0.0751 | 0.1791 | 0.3348 | 0.3348 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1026 | 165.4 | 121.9 | 74.2 | 55.5 | 1.3 | 350 | 2500 | 58.7 | 20 | 77.3 | 75 | 70.8 | 82.7 | 35.1 | 12.6 | 9662.3 | 9534.6 | 10000 | 19308.3 | 19069.3 | 20000 | 1.998 | 2 | 2 | 0.519 | 0.51 | 0.52 | 2.2 | 2.2 | 3.28 | 0.505 | 0.5 | 0.535 | 2.17 | 2.15 | 2.68 | 0.507 | 0.514 | 0.5 | 2.5 | 2.45 | -2 | 0.5 | 0.5 | 0.52 | -2.64 | 3 | 2.46 | Good_Mixed | 9534.6 | 19069.3 | 1.998 | 0.52 | 3.28 | 0.535 | 3 | 0.9348 | 1 | 0.9428 | 0.953 | 1 | 0.8859 | 0.9156 | 0.9445 | 0.9445 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1027 | 513.5 | 268.8 | 81.3 | 68.1 | 1.1 | 1555.4 | 18435.2 | 33.3 | 45.7 | 79.4 | 79.9 | 74.2 | 86.5 | 37 | 18.6 | 5142 | 4285.1 | 5641.6 | 7693.8 | 6085.3 | 8620.6 | 1.496 | 1.42 | 1.528 | 0.676 | 0.619 | 0.678 | -4.65 | 3.82 | 4.99 | 0.544 | 0.587 | 0.509 | 3.22 | 3.28 | 3.98 | 0.563 | 0.528 | 0.513 | 3.25 | 2.98 | 2.33 | 0.509 | 0.572 | 0.564 | 3.31 | 2.44 | 2.11 | Critical_Oil | 4285.1 | 6085.3 | 1.42 | 0.678 | 4.99 | 0.587 | 3.98 | 0.6545 | 0.6232 | 0.8071 | 0.7902 | 1 | 0.5615 | 0.775 | 0.7367 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | Moisture_PPM
1028 | 183.3 | 288.6 | 80 | 60.5 | 68.6 | 454.1 | 3464.5 | 33.2 | 45.6 | 86 | 85.5 | 76.7 | 92.5 | 37.4 | 18.7 | 4896.9 | 5446.5 | 5710.7 | 7341.5 | 8625.9 | 8731.8 | 1.499 | 1.584 | 1.529 | 0.64 | 0.713 | 0.666 | 3.62 | 5.7 | 4.45 | 0.615 | 0.592 | 0.568 | 3.47 | -3.41 | 4.27 | 0.646 | 0.606 | 0.613 | 2.63 | -3.4 | 4.47 | 0.578 | 0.634 | 0.586 | -3.16 | 3.03 | 4.35 | Critical_Oil | 4896.9 | 7341.5 | 1.499 | 0.713 | 5.7 | 0.646 | 4.47 | 0.5914 | 0.6241 | 0.6598 | 0.7872 | 1 | 0.5409 | 0.6257 | 0.6764 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1029 | 100 | 120 | 67.4 | 50 | 1 | 350 | 2563.3 | 57.9 | 21.7 | 80.1 | 80 | 72.1 | 84 | 35.1 | 14.6 | 9561.4 | 8463.9 | 10000 | 18988.9 | 16047.7 | 19908.5 | 1.986 | 1.896 | 1.991 | 0.551 | 0.523 | 0.529 | -3.07 | 2.15 | 2.78 | 0.543 | 0.535 | 0.5 | -2.01 | 3.49 | 2.47 | 0.568 | 0.522 | 0.529 | 2.14 | 2.88 | 2 | 0.58 | 0.52 | 0.511 | 2.67 | 3.34 | 2.55 | Good_Mixed | 8463.9 | 16047.7 | 1.896 | 0.551 | 3.07 | 0.58 | 3.49 | 0.9989 | 0.9355 | 0.8389 | 0.904 | 1 | 0.8395 | 0.8187 | 0.916 | 0.916 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1030 | 328.1 | 245.7 | 80.2 | 72.9 | 2.1 | 502.6 | 3697.2 | 26.2 | 25.1 | 79.3 | 79.1 | 74.3 | 85.9 | 36.9 | 16.1 | 1292.3 | 690 | 690 | 1344 | 703.8 | 735.2 | 1.04 | 1.02 | 1.066 | 0.709 | 0.687 | 0.711 | 5.35 | 4.35 | -5.52 | 0.554 | 0.59 | 0.535 | 2.61 | 2.76 | 3.8 | 0.57 | 0.561 | 0.586 | 3.38 | 3.35 | 3.49 | 0.658 | 0.584 | 0.542 | 3.46 | 3.82 | 3.34 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.711 | 5.52 | 0.658 | 3.82 | 0.8065 | 0.285 | 0.8179 | 0.8635 | 0.85 | 0.4833 | 0.6871 | 0.6881 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
1031 | 831.3 | 518.5 | 102.8 | 115.1 | 15 | 865.7 | 5258.1 | 56.5 | 25.3 | 79.2 | 77.1 | 71.8 | 84 | 35.5 | 14.8 | 8573.8 | 9189.6 | 9830.2 | 15591.2 | 17649.1 | 18617.7 | 1.818 | 1.921 | 1.894 | 0.563 | 0.556 | 0.553 | -3.77 | -2.96 | 2.47 | 0.553 | 0.554 | 0.5 | -2.49 | 2.37 | 2.92 | 0.5 | 0.521 | 0.521 | 2.2 | -3.35 | -2.38 | 0.553 | 0.529 | 0.525 | -2.25 | 2.47 | -2.35 | Poor_DGA | 8573.8 | 15591.2 | 1.818 | 0.563 | 3.77 | 0.554 | 3.35 | 0.4607 | 0.865 | 0.876 | 0.8988 | 1 | 0.7716 | 0.8402 | 0.7708 | 0.7708 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1032 | 189.6 | 160.8 | 75.3 | 64.9 | 2 | 395.8 | 3230.9 | 59.5 | 20 | 79.6 | 77.3 | 74 | 86.1 | 36.1 | 13.7 | 9299 | 9759 | 9382.3 | 17756 | 19499.7 | 17949.2 | 1.909 | 1.998 | 1.913 | 0.515 | 0.529 | 0.571 | 2.68 | 2.34 | 2.95 | 0.538 | 0.54 | 0.5 | 2.26 | 2.81 | 2.05 | 0.542 | 0.5 | 0.533 | 2.41 | -2.8 | -2.65 | 0.51 | 0.537 | 0.501 | 2 | 2.15 | 2 | Good_Mixed | 9299 | 17756 | 1.909 | 0.571 | 2.95 | 0.542 | 2.81 | 0.8692 | 1 | 0.8382 | 0.9269 | 1 | 0.8356 | 0.8719 | 0.9014 | 0.9014 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1033 | 1249 | 774.2 | 128.4 | 171 | 31.5 | 1226 | 7368.4 | 38 | 41.5 | 102.1 | 101.9 | 91.6 | 111.5 | 42.9 | 31.3 | 2983.4 | 2357.9 | 2077.6 | 3707.4 | 2842.6 | 2534.3 | 1.243 | 1.206 | 1.22 | 0.959 | 0.895 | 0.984 | 9.33 | -8.28 | 8.45 | 0.684 | 0.873 | 0.799 | 6.95 | 5.39 | 7.22 | 0.81 | 0.786 | 0.847 | 6.59 | 6.18 | 6.26 | 0.81 | 0.873 | 0.852 | 7.45 | 8.75 | 6.82 | Very Poor_Mixed | 2077.6 | 2534.3 | 1.206 | 0.984 | 9.33 | 0.873 | 8.75 | 0.1747 | 0.6645 | 0.2308 | 0.3483 | 1 | 0.1017 | 0.2592 | 0.3848 | 0.3848 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1034 | 217.3 | 189.5 | 65 | 59 | 2.5 | 362.6 | 3046.8 | 60 | 22.6 | 78 | 78 | 73 | 82 | 36 | 11.6 | 9402.8 | 9046.4 | 9746.3 | 17626.7 | 17212.9 | 18914.4 | 1.875 | 1.903 | 1.941 | 0.762 | 0.72 | 0.75 | 5.87 | 4.49 | 5.56 | 0.564 | 0.529 | 0.572 | 3.63 | 3.06 | 3.54 | 0.603 | 0.586 | 0.595 | 2.12 | 2.77 | 3.46 | 0.571 | 0.539 | 0.529 | 2 | 2.61 | 2.93 | Fair_Winding_TD_Cap | 9046.4 | 17212.9 | 1.875 | 0.762 | 5.87 | 0.603 | 3.63 | 0.8722 | 0.915 | 0.8752 | 0.9744 | 1 | 0.4333 | 0.7266 | 0.8156 | 0.8156 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1035 | 937.2 | 550.3 | 107.1 | 122.4 | 19.5 | 912.3 | 5520.9 | 46.5 | 32.5 | 89.9 | 93.5 | 81.6 | 99.2 | 39 | 23.4 | 5348.5 | 4650.1 | 4712.9 | 8313.9 | 6716 | 6869.4 | 1.554 | 1.444 | 1.458 | 0.674 | 0.721 | 0.676 | 5.23 | 5.53 | 4.62 | 0.666 | 0.703 | 0.721 | 4.79 | 4.11 | 4.87 | 0.672 | 0.694 | 0.659 | -4.96 | 4.24 | 4.21 | 0.648 | 0.596 | 0.648 | 4.67 | -3.43 | 5.45 | Poor_Mixed | 4650.1 | 6716 | 1.444 | 0.721 | 5.53 | 0.721 | 5.45 | 0.4015 | 0.7641 | 0.5033 | 0.6348 | 1 | 0.4916 | 0.4999 | 0.593 | 0.593 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1036 | 860.2 | 548.3 | 107.2 | 126.1 | 18.1 | 937.4 | 5531.9 | 43.3 | 36.2 | 89.4 | 89.7 | 81.3 | 96.8 | 39.7 | 23.3 | 4152.5 | 4879.5 | 5096.2 | 6127.4 | 6759.9 | 7584 | 1.476 | 1.385 | 1.488 | 0.747 | 0.74 | 0.729 | 5.34 | -5.9 | 6.37 | 0.661 | 0.718 | 0.71 | 4.33 | 3.97 | 4.87 | 0.66 | 0.669 | 0.723 | 4.68 | 5.46 | 5.48 | 0.713 | 0.677 | 0.632 | 5.29 | 4.7 | 4.17 | Poor_Mixed | 4152.5 | 6127.4 | 1.385 | 0.747 | 6.37 | 0.723 | 5.48 | 0.4095 | 0.7208 | 0.5407 | 0.6382 | 1 | 0.406 | 0.4684 | 0.576 | 0.576 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1037 | 1407.3 | 865.4 | 138.8 | 178.6 | 32.9 | 1243.3 | 8635 | 35.2 | 44.9 | 104.9 | 103.8 | 94.3 | 114.1 | 43.1 | 31.3 | 1853.4 | 2487.8 | 2383.5 | 1946.1 | 2952.7 | 2993.1 | 1.05 | 1.187 | 1.256 | 0.938 | 0.895 | 0.99 | 8.62 | 8.5 | 9.57 | 0.772 | 0.761 | 0.885 | 5.93 | -6.8 | 6.58 | 0.918 | 0.781 | 0.75 | 8.86 | -7.04 | 7.82 | 0.94 | 0.926 | 0.778 | -6.11 | 6.99 | 6.18 | Very Poor_Mixed | 1853.4 | 1946.1 | 1.05 | 0.99 | 9.57 | 0.94 | 8.86 | 0.1141 | 0.6309 | 0.1746 | 0.3483 | 1 | 0.0945 | 0.2393 | 0.3554 | 0.3554 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1038 | 446.8 | 286 | 87.9 | 90.5 | 2.5 | 556 | 3592.7 | 53.8 | 75.4 | 75 | 76.8 | 72.8 | 81.9 | 35.8 | 13 | 2135.9 | 1577 | 764.8 | 2440.3 | 1725.4 | 780 | 1.143 | 1.094 | 1.02 | 0.721 | 0.741 | 0.723 | 5.92 | 6.05 | 5.37 | 0.5 | 0.509 | 0.565 | -2.35 | 2 | 2.4 | 0.513 | 0.535 | 0.537 | 2 | -2.39 | 2.4 | 0.561 | 0.531 | 0.529 | 2.48 | 2.36 | -2.37 | Critical_IR_PI | 764.8 | 780 | 1.02 | 0.741 | 6.05 | 0.565 | 2.48 | 0.7475 | 0.5833 | 0.9305 | 0.9438 | 0.925 | 0.4199 | 0.8406 | 0.7552 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
1039 | 1625 | 856.4 | 139.6 | 170.5 | 33.8 | 1263.2 | 7976.9 | 35.6 | 45.8 | 108 | 108.3 | 94.8 | 118.4 | 44 | 32.7 | 1478.3 | 2038.7 | 1128.1 | 1640.5 | 2266.7 | 1242.4 | 1.11 | 1.112 | 1.101 | 0.966 | 0.985 | 0.969 | -9.02 | 9.42 | 8.83 | 0.779 | 0.922 | 0.795 | 7.74 | -8.99 | -7.17 | 0.742 | 0.925 | 0.717 | 6.69 | -7.92 | 7.02 | 0.849 | 0.858 | 0.757 | 6.89 | 7.36 | 8.76 | Very Poor_Mixed | 1128.1 | 1242.4 | 1.101 | 0.985 | 9.42 | 0.925 | 8.99 | 0.1081 | 0.6222 | 0.102 | 0.2943 | 1 | 0.0627 | 0.2339 | 0.3375 | 0.3375 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1040 | 991 | 625.3 | 109.6 | 122.8 | 18.2 | 910.6 | 5655 | 60 | 20 | 80.7 | 80.7 | 76.3 | 89.3 | 36.2 | 15.5 | 9990.2 | 9598.2 | 8745.9 | 18905.2 | 19118.3 | 17278.5 | 1.892 | 1.992 | 1.976 | 0.548 | 0.584 | 0.539 | -2.28 | 3.13 | -3.32 | 0.525 | 0.521 | 0.542 | 2.36 | 2.66 | 2.8 | 0.53 | 0.52 | 0.51 | -3.11 | 3.22 | 2.91 | 0.5 | 0.543 | 0.535 | -2.82 | 2.78 | 2.22 | Poor_DGA | 8745.9 | 17278.5 | 1.892 | 0.584 | 3.32 | 0.543 | 3.22 | 0.3934 | 1 | 0.7631 | 0.88 | 1 | 0.7846 | 0.8293 | 0.7578 | 0.7578 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1041 | 713.8 | 333.4 | 86.8 | 91.5 | 1 | 601 | 4471 | 52.7 | 28.7 | 81.3 | 83.8 | 75.3 | 88.9 | 37.2 | 10 | 8417.8 | 10000 | 8805.6 | 15183 | 19702.9 | 15953.5 | 1.804 | 1.97 | 1.812 | 0.579 | 1.045 | 0.518 | 3.12 | -2 | 2.94 | 0.6 | 0.547 | 0.941 | 4.42 | 3.21 | 8.58 | 0.636 | 0.595 | 0.623 | 3.28 | -3.09 | -2.39 | 0.547 | 0.537 | 0.617 | 3.04 | 3.02 | 4.1 | Critical_Bushing_TD_Cap | 8417.8 | 15183 | 1.804 | 1.045 | 3.12 | 0.941 | 8.58 | 0.7838 | 0.8136 | 0.7377 | 1 | 1 | 0.6839 | 0.6037 | 0.7818 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_LV_TanDelta_pct
1042 | 1024 | 581.9 | 115.3 | 138.9 | 21.8 | 966 | 5958.6 | 60 | 21 | 77.8 | 79.7 | 71.7 | 81.4 | 36.3 | 14.5 | 10000 | 9484.6 | 9498.7 | 19517.7 | 16907.8 | 18708.4 | 1.952 | 1.783 | 1.97 | 0.542 | 0.533 | 0.5 | 2.52 | 3.19 | 2.32 | 0.549 | 0.501 | 0.559 | 2.85 | 3.12 | -2.1 | 0.552 | 0.533 | 0.502 | 2.32 | 2.62 | 2 | 0.502 | 0.501 | 0.544 | 2.2 | 2.58 | 2 | Poor_DGA | 9484.6 | 16907.8 | 1.783 | 0.542 | 3.19 | 0.559 | 3.12 | 0.3455 | 0.9543 | 0.8745 | 0.9067 | 1 | 0.8688 | 0.8553 | 0.7693 | 0.7693 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1043 | 537.7 | 315.5 | 83.2 | 72 | 1.7 | 671 | 3723.9 | 50.7 | 30.2 | 80.7 | 80.3 | 74.3 | 86.9 | 37.5 | 18.5 | 8143.1 | 8391 | 8561.8 | 14674.7 | 15186.2 | 15435.8 | 1.802 | 1.81 | 1.803 | 0.617 | 0.655 | 0.62 | 4.3 | 4.58 | -18.79 | 0.564 | 0.613 | 0.566 | 4.19 | 4.32 | 2.86 | 0.54 | 0.5 | 0.99 | -3.64 | 2.64 | 9.3 | 0.531 | 0.612 | 0.608 | 3.9 | 2.86 | 3.79 | Critical_Bushing_TD_Cap | 8143.1 | 14674.7 | 1.802 | 0.655 | 18.79 | 0.99 | 9.3 | 0.7668 | 0.7933 | 0.7868 | 0.7933 | 1 | 0.4935 | 0.6334 | 0.7484 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
1044 | 926.2 | 503.9 | 105 | 121.1 | 18.3 | 901.7 | 5506.4 | 44.8 | 33.9 | 93.8 | 91.7 | 83.2 | 101.2 | 41.1 | 25.2 | 5817.5 | 6240.9 | 5954 | 8813.5 | 9811.2 | 9077.3 | 1.515 | 1.572 | 1.525 | 0.751 | 0.725 | 0.789 | 5.81 | 5.17 | 6.9 | 0.708 | 0.624 | 0.711 | 3.89 | 6.03 | 5.02 | 0.611 | 0.599 | 0.654 | 4.75 | -4.19 | 3.85 | 0.625 | 0.611 | 0.639 | 4.36 | -5.67 | 4.6 | Poor_Mixed | 5817.5 | 8813.5 | 1.515 | 0.789 | 6.9 | 0.711 | 6.03 | 0.419 | 0.7473 | 0.4559 | 0.5725 | 1 | 0.3879 | 0.5267 | 0.5778 | 0.5778 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1045 | 864.4 | 499.2 | 101.9 | 94.7 | 17.5 | 814.2 | 4902.5 | 47.2 | 33.2 | 92.6 | 92 | 83.1 | 98.1 | 39.6 | 24.1 | 5927.7 | 5787 | 5447.3 | 9834.1 | 9280.7 | 8037.8 | 1.659 | 1.604 | 1.476 | 0.747 | 0.74 | 0.72 | -6.26 | 5.27 | 5.04 | 0.644 | 0.754 | 0.711 | 3.55 | -5.25 | 4.8 | 0.637 | 0.681 | 0.743 | -4.9 | 5.51 | 5.63 | 0.609 | 0.614 | 0.687 | -4.09 | -5.05 | 5.5 | Poor_Mixed | 5447.3 | 8037.8 | 1.476 | 0.747 | 6.26 | 0.754 | 5.63 | 0.4754 | 0.7556 | 0.4875 | 0.6108 | 1 | 0.428 | 0.4771 | 0.5946 | 0.5946 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1046 | 966.2 | 577.3 | 111 | 123.6 | 24.4 | 785.7 | 5874.8 | 56.1 | 24.4 | 80.4 | 80.6 | 74.9 | 85.2 | 36 | 10 | 8498.2 | 10000 | 8223.8 | 15930.9 | 19623.6 | 15367.3 | 1.875 | 1.962 | 1.869 | 0.629 | 0.559 | 0.603 | 4.18 | 3.45 | -3.45 | 0.566 | 0.591 | 0.567 | 2.45 | 2.53 | 3.22 | 0.583 | 0.548 | 0.557 | 2.16 | 2.86 | 2.82 | 0.528 | 0.599 | 0.533 | 2.96 | 3.2 | 2.22 | Poor_DGA | 8223.8 | 15367.3 | 1.869 | 0.629 | 4.18 | 0.599 | 3.22 | 0.377 | 0.8804 | 0.7984 | 1 | 1 | 0.6783 | 0.7367 | 0.7173 | 0.7173 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1047 | 841.9 | 530.5 | 106.6 | 118.6 | 16.6 | 706.1 | 5088.1 | 44.7 | 34.3 | 91.9 | 89.1 | 82.1 | 96.7 | 39.6 | 23.8 | 6504.1 | 6809.4 | 7215 | 10902.7 | 11182.9 | 12056.2 | 1.676 | 1.642 | 1.671 | 0.782 | 0.717 | 0.764 | 6.48 | -5.31 | 6.28 | 0.703 | 0.641 | 0.668 | 5.35 | 6.08 | 5.85 | 0.676 | 0.696 | 0.729 | 5.26 | 5.18 | 5.46 | 0.709 | 0.752 | 0.622 | 5.68 | 4.62 | 4.3 | Poor_Mixed | 6504.1 | 10902.7 | 1.642 | 0.782 | 6.48 | 0.752 | 6.08 | 0.4637 | 0.7426 | 0.5243 | 0.6212 | 1 | 0.3848 | 0.4453 | 0.5825 | 0.5825 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1048 | 1551.7 | 775 | 129.2 | 178.4 | 33.7 | 1112.1 | 7299.4 | 33.5 | 44.3 | 100.4 | 102.5 | 93 | 112.1 | 43.3 | 31.2 | 840.4 | 2793.6 | 2257.5 | 1200 | 3308.6 | 2448.1 | 1.428 | 1.184 | 1.084 | 0.932 | 0.906 | 0.904 | -8.48 | 8.81 | 8.3 | 0.739 | 0.768 | 0.813 | 8.59 | -7.11 | -8.13 | 0.816 | 0.885 | 0.876 | 6.33 | 6.81 | 6.53 | 0.891 | 0.824 | 0.853 | 6.41 | 6.61 | 7.91 | Very Poor_Mixed | 840.4 | 1200 | 1.084 | 0.932 | 8.81 | 0.891 | 8.59 | 0.1496 | 0.6367 | 0.2234 | 0.3521 | 1 | 0.131 | 0.2343 | 0.3743 | 0.3743 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1049 | 612.3 | 413 | 87.9 | 92 | 9.6 | 700.4 | 4357.4 | 51.5 | 28.2 | 84.8 | 87.7 | 78.3 | 92.3 | 36.7 | 19 | 8582.7 | 7944 | 7417.4 | 15566 | 13685.2 | 12812.9 | 1.814 | 1.723 | 1.727 | 0.606 | 0.662 | 0.631 | -3.84 | 3.63 | 4.46 | 0.592 | 0.547 | 0.59 | 3.71 | 3.83 | 3.27 | 0.637 | 0.553 | 0.661 | 3.76 | 4.33 | -3.14 | 0.589 | 0.672 | 0.66 | 3.46 | 3.29 | 3.19 | Fair_Mixed | 7417.4 | 12812.9 | 1.723 | 0.662 | 4.46 | 0.672 | 4.33 | 0.5967 | 0.8207 | 0.6465 | 0.778 | 1 | 0.6176 | 0.62 | 0.7093 | 0.7093 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1050 | 183.5 | 150.1 | 67.2 | 57.7 | 3.9 | 352.1 | 2586.9 | 57.6 | 21.8 | 75 | 75 | 70.3 | 82 | 35.3 | 15.1 | 9227.7 | 9388.8 | 9850 | 18136.3 | 18493.7 | 19379.2 | 1.965 | 1.97 | 1.967 | 0.563 | 0.565 | 0.506 | -3.2 | -2.22 | 2.43 | 0.5 | 0.5 | 0.51 | -2.17 | 2 | 2 | 0.517 | 0.518 | 0.5 | -2.13 | 2.59 | -2.69 | 0.523 | 0.571 | 0.618 | -3.67 | -2 | 4.61 | Fair_Bushing_TD_Cap | 9227.7 | 18136.3 | 1.965 | 0.565 | 3.2 | 0.618 | 4.61 | 0.8601 | 0.9331 | 0.9841 | 0.8908 | 1 | 0.8324 | 0.8556 | 0.9005 | 0.9005 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1051 | 1029.6 | 551.2 | 107.6 | 116.7 | 17.2 | 861.5 | 5167.1 | 47.8 | 34.6 | 90.5 | 88.8 | 79.2 | 94.7 | 39.2 | 25.7 | 6433.6 | 6143.2 | 5348.6 | 10965.7 | 9182.3 | 7953 | 1.704 | 1.495 | 1.487 | 0.639 | 0.762 | 0.73 | 5.06 | -5.91 | 5.25 | 0.645 | 0.61 | 0.643 | 5.69 | -3.94 | 4.5 | 0.711 | 0.594 | 0.649 | -5.33 | 4.54 | 5.16 | 0.741 | 0.7 | 0.599 | 4.22 | -6.26 | 4.13 | Poor_Mixed | 5348.6 | 7953 | 1.487 | 0.762 | 5.91 | 0.741 | 6.26 | 0.4234 | 0.7391 | 0.567 | 0.5549 | 1 | 0.4594 | 0.5062 | 0.5944 | 0.5944 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1052 | 1559.6 | 883.7 | 140.3 | 169.7 | 27.6 | 1234.2 | 7824.3 | 36.7 | 44.6 | 106 | 104.4 | 94.1 | 114.8 | 43.6 | 29.7 | 2687.8 | 1953.6 | 840.8 | 3218.4 | 2380.7 | 1200 | 1.197 | 1.219 | 1.427 | 0.946 | 0.875 | 0.956 | -8.62 | -8.63 | 9.14 | 0.711 | 0.852 | 0.825 | 8.79 | 5.61 | 8.23 | 0.811 | 0.815 | 0.781 | 8.49 | -7.37 | 7.78 | 0.888 | 0.871 | 0.706 | 8.25 | 7.88 | 7.47 | Very Poor_Mixed | 840.8 | 1200 | 1.197 | 0.956 | 9.14 | 0.888 | 8.79 | 0.1434 | 0.6338 | 0.1592 | 0.4089 | 1 | 0.1099 | 0.2375 | 0.3664 | 0.3664 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1053 | 1398.4 | 828.1 | 126 | 162.2 | 32.3 | 1221.8 | 7476.7 | 35.4 | 42.9 | 104.4 | 105.2 | 91.7 | 111.8 | 44 | 29.9 | 2018 | 2042.7 | 2075 | 2442.7 | 2516.6 | 2350.1 | 1.21 | 1.232 | 1.133 | 0.942 | 0.99 | 0.845 | 7.97 | -9.32 | 7.93 | 0.689 | 0.711 | 0.927 | -6.68 | 6.32 | 6.52 | 0.748 | 0.797 | 0.752 | -8.01 | 5.5 | 5.39 | 0.824 | 0.719 | 0.704 | 8.07 | 6.67 | 6.34 | Very Poor_Mixed | 2018 | 2350.1 | 1.133 | 0.99 | 9.32 | 0.927 | 8.07 | 0.1627 | 0.6504 | 0.1893 | 0.4014 | 1 | 0.1306 | 0.3194 | 0.3935 | 0.3935 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1054 | 1600.3 | 848.7 | 138.9 | 171.1 | 27.9 | 1260.2 | 7631.8 | 33.4 | 45.3 | 108.4 | 106.5 | 93.9 | 115.7 | 44.7 | 33.3 | 2355.2 | 2090.9 | 825 | 2526.8 | 2454.4 | 1200 | 1.073 | 1.174 | 1.455 | 0.987 | 0.952 | 0.942 | 8.95 | 8.61 | -8.89 | 0.746 | 0.794 | 0.783 | -7.06 | -5.49 | 5.55 | 0.937 | 0.953 | 0.786 | 6.93 | 6.28 | 8.68 | 0.846 | 0.802 | 0.833 | -6.69 | 7.65 | -9.44 | Very Poor_Mixed | 825 | 1200 | 1.073 | 0.987 | 8.95 | 0.953 | 9.44 | 0.1424 | 0.627 | 0.1231 | 0.2709 | 1 | 0.0851 | 0.2368 | 0.3512 | 0.3512 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1055 | 375.5 | 267.9 | 83.3 | 76.5 | 5.4 | 541 | 4315.1 | 31.4 | 45.2 | 83.5 | 78.9 | 75.7 | 88.1 | 36 | 13.6 | 5177.2 | 6066.7 | 4692 | 8291.5 | 4145.6 | 6730.1 | 1.602 | 0.683 | 1.434 | 0.616 | 0.614 | 0.638 | 4.8 | 3.98 | 4.43 | 0.509 | 0.5 | 0.5 | 3.3 | 2.77 | 2.46 | 0.5 | 0.526 | 0.533 | 2.51 | 2.53 | 2.89 | 0.533 | 0.515 | 0.522 | -2 | -2.79 | 2 | Critical_Oil | 4692 | 4145.6 | 0.683 | 0.638 | 4.8 | 0.533 | 3.3 | 0.7229 | 0.628 | 0.7679 | 0.9294 | 0.8187 | 0.6028 | 0.8812 | 0.7534 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
1056 | 1625.8 | 816 | 138.3 | 183 | 33.5 | 1271.9 | 8050.8 | 36.3 | 43.2 | 102.9 | 104.3 | 91.1 | 111.9 | 44.4 | 30.5 | 1850.4 | 2224 | 1092.9 | 2085.9 | 2503.8 | 1200 | 1.127 | 1.126 | 1.098 | 0.877 | 0.881 | 0.942 | 7.6 | 7.82 | 9.72 | 0.76 | 0.862 | 0.769 | 7.7 | 8.23 | 5.6 | 0.818 | 0.837 | 0.808 | -7.88 | -7.9 | 6.86 | 0.759 | 0.724 | 0.779 | -7.12 | 8.01 | 6.04 | Very Poor_Mixed | 1092.9 | 1200 | 1.098 | 0.942 | 9.72 | 0.862 | 8.23 | 0.1024 | 0.6474 | 0.2028 | 0.3787 | 1 | 0.1492 | 0.2679 | 0.3716 | 0.3716 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1057 | 655.3 | 365.1 | 92.4 | 98.2 | 13.4 | 646.4 | 4287.5 | 50.5 | 27.3 | 84.3 | 84.4 | 76 | 89 | 38.1 | 20.2 | 6557.5 | 6339.8 | 5534 | 10921.7 | 10534.6 | 8676.4 | 1.666 | 1.662 | 1.568 | 0.634 | 0.606 | 0.628 | -3.51 | -3.91 | 4.41 | 0.582 | 0.585 | 0.652 | 4.65 | 3.66 | -3.74 | 0.622 | 0.608 | 0.661 | 4 | -3.43 | 3.68 | 0.586 | 0.552 | 0.645 | -4.13 | 3.08 | 2.93 | Fair_Mixed | 5534 | 8676.4 | 1.568 | 0.634 | 4.41 | 0.661 | 4.65 | 0.5659 | 0.8337 | 0.6989 | 0.7404 | 1 | 0.6306 | 0.6129 | 0.707 | 0.707 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1058 | 1520.7 | 864.3 | 137.8 | 176.7 | 30.2 | 1232.2 | 8297.4 | 34 | 46.3 | 104.4 | 100.6 | 91.9 | 113.1 | 43 | 31.6 | 1932.3 | 2071.3 | 1561.2 | 2179.8 | 2449.7 | 1639.2 | 1.128 | 1.183 | 1.05 | 0.861 | 0.923 | 0.932 | 8.45 | 8.77 | 8.77 | 0.814 | 0.891 | 0.827 | 8.32 | 6.21 | 5.86 | 0.915 | 0.764 | 0.748 | -6.67 | 7.31 | 8.74 | 0.768 | 0.833 | 0.806 | -5.56 | 8.77 | 6.82 | Very Poor_Mixed | 1561.2 | 1639.2 | 1.05 | 0.932 | 8.77 | 0.915 | 8.77 | 0.1262 | 0.6175 | 0.2149 | 0.3368 | 1 | 0.1306 | 0.2459 | 0.3665 | 0.3665 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1059 | 1766 | 970 | 148.1 | 197 | 34.3 | 1370.9 | 8843.4 | 55.2 | 23.7 | 84 | 81.6 | 77.6 | 89.3 | 36.4 | 14.7 | 154 | 7856.6 | 6956.8 | 236.6 | 13471.7 | 11456.1 | 1.536 | 1.715 | 1.647 | 0.674 | 0.641 | 0.619 | 4.51 | 4.76 | 4.23 | 0.562 | 0.5 | 0.562 | 3.33 | 2.45 | 3.04 | 0.54 | 0.589 | 0.537 | -2.26 | 3.34 | 2.95 | 0.547 | 0.559 | 0.55 | -3.19 | -3.05 | 2.72 | Critical_DGA | 154 | 236.6 | 1.536 | 0.674 | 4.76 | 0.589 | 3.34 | 0.0319 | 0.8931 | 0.7192 | 0.9014 | 0.85 | 0.5735 | 0.7628 | 0.5857 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1060 | 838.6 | 585.8 | 108.3 | 129.2 | 18.8 | 922.2 | 5485.8 | 56.3 | 25 | 76.9 | 78.7 | 72.3 | 83.2 | 36 | 11.4 | 10000 | 8819.2 | 8895.7 | 19411.7 | 16367.5 | 16552.5 | 1.941 | 1.856 | 1.861 | 0.555 | 0.549 | 0.567 | -2.66 | 2.8 | 2.66 | 0.502 | 0.53 | 0.542 | 2.74 | 2.94 | 3.29 | 0.545 | 0.546 | 0.504 | -2.38 | 2.63 | -2.17 | 0.547 | 0.54 | 0.516 | 2.48 | 2.51 | 2.77 | Poor_DGA | 8819.2 | 16367.5 | 1.856 | 0.567 | 2.8 | 0.547 | 3.29 | 0.4013 | 0.87 | 0.88 | 0.9783 | 1 | 0.7957 | 0.8206 | 0.7608 | 0.7608 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1061 | 475.3 | 352.3 | 79.2 | 88.8 | 3.6 | 618.7 | 4024.1 | 30.8 | 49.2 | 80.3 | 82.1 | 108.2 | 88.7 | 36.7 | 16.3 | 4232.5 | 4672.4 | 4662.4 | 6302.6 | 6447.2 | 6639.6 | 1.489 | 1.38 | 1.424 | 0.681 | 0.664 | 0.674 | -4.15 | 5.11 | 4.8 | 0.603 | 0.569 | 0.595 | 3.04 | 3.51 | 2.63 | 0.667 | 0.674 | 0.664 | 2.86 | 2.45 | 4.35 | 0.641 | 0.555 | 0.535 | 3.59 | -4.39 | 3.32 | Critical_Oil | 4232.5 | 6302.6 | 1.38 | 0.681 | 5.11 | 0.674 | 4.39 | 0.7103 | 0.5906 | 0.6129 | 0.8578 | 1 | 0.5333 | 0.6311 | 0.7009 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Moisture_PPM
1062 | 561.1 | 324.4 | 82.3 | 146.5 | 57.3 | 586.4 | 4454.5 | 60 | 20.6 | 105.5 | 107.3 | 92.9 | 115.7 | 43.5 | 12.3 | 8552.3 | 10000 | 10000 | 17104.5 | 19045.4 | 20000 | 2 | 1.905 | 2 | 0.604 | 0.66 | 0.705 | 3.73 | 4.9 | -5.31 | 0.5 | 0.502 | 0.545 | 3.18 | 2.59 | 3.09 | 0.537 | 0.549 | 0.549 | 3.1 | -3.81 | -2.89 | 0.52 | 0.518 | 0.512 | 2.15 | 2.75 | 3.45 | Critical_Thermal | 8552.3 | 17104.5 | 1.905 | 0.705 | 5.31 | 0.549 | 3.81 | 0.4288 | 0.9672 | 0.1489 | 0.9597 | 1 | 0.5551 | 0.8222 | 0.6718 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1063 | 874.2 | 580.9 | 109.7 | 124.6 | 18.9 | 865.6 | 4737.8 | 46 | 35.4 | 91.2 | 92.8 | 84.3 | 98.6 | 40.5 | 25.7 | 5632.3 | 5470.2 | 5447.8 | 8981.7 | 7989.8 | 8532.4 | 1.595 | 1.461 | 1.566 | 0.719 | 0.702 | 0.743 | -6.36 | -4.75 | 5.33 | 0.718 | 0.685 | 0.732 | 5.23 | -3.98 | -3.77 | 0.71 | 0.723 | 0.688 | 5.34 | 5.41 | 4.22 | 0.7 | 0.776 | 0.726 | 5.24 | 3.78 | 3.76 | Poor_Mixed | 5447.8 | 7989.8 | 1.461 | 0.743 | 6.36 | 0.776 | 5.41 | 0.4161 | 0.7299 | 0.4756 | 0.5549 | 1 | 0.4434 | 0.4393 | 0.5681 | 0.5681 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1064 | 695.4 | 445.8 | 90.7 | 95.4 | 15.1 | 693.6 | 5123.2 | 49.8 | 30 | 86.5 | 82.3 | 77.4 | 90.9 | 38.9 | 19.8 | 6769.3 | 7178.4 | 6550.2 | 11176.5 | 12263.3 | 10916.5 | 1.651 | 1.708 | 1.667 | 0.643 | 0.652 | 0.681 | 4.97 | 4.26 | 4.4 | 0.647 | 0.625 | 0.65 | 3.75 | 4.43 | 4.71 | 0.586 | 0.653 | 0.633 | -5.01 | 3.67 | 4.62 | 0.619 | 0.563 | 0.673 | 2.8 | -4.63 | -4.21 | Fair_Mixed | 6550.2 | 10916.5 | 1.651 | 0.681 | 4.97 | 0.673 | 5.01 | 0.5313 | 0.796 | 0.6747 | 0.753 | 1 | 0.5561 | 0.5667 | 0.6733 | 0.6733 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1065 | 1595.6 | 899.3 | 135.9 | 179.5 | 34.3 | 1187.8 | 8156.6 | 34.6 | 47.8 | 105.5 | 106.3 | 92 | 114 | 44.9 | 34.2 | 1336.1 | 3525 | 1950.6 | 1478.8 | 4426.9 | 2158.2 | 1.107 | 1.256 | 1.106 | 0.983 | 0.94 | 0.949 | -9.11 | 9.31 | 9.05 | 0.934 | 0.866 | 0.824 | 7.21 | -9.84 | -8.79 | 0.902 | 0.902 | 0.802 | 9.36 | 9.21 | 6.34 | 0.831 | 0.859 | 0.865 | 5.6 | -6.98 | 8.56 | Very Poor_Mixed | 1336.1 | 1478.8 | 1.106 | 0.983 | 9.31 | 0.934 | 9.84 | 0.1048 | 0.6035 | 0.1578 | 0.2355 | 1 | 0.07 | 0.1753 | 0.3275 | 0.3275 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1066 | 926.2 | 525.9 | 106 | 115.9 | 14.4 | 776.2 | 4624.7 | 44.8 | 35.2 | 93.3 | 93.3 | 83.9 | 102.2 | 40.3 | 25.8 | 5346.8 | 5990 | 6511.9 | 7932.3 | 9442.7 | 10484.1 | 1.484 | 1.576 | 1.61 | 0.772 | 0.706 | 0.774 | -6.12 | 5.71 | 6.1 | 0.634 | 0.707 | 0.673 | -5.76 | 5.56 | -4.49 | 0.654 | 0.685 | 0.655 | 4.52 | 4.24 | 3.79 | 0.714 | 0.654 | 0.703 | 5.89 | 4.14 | 3.58 | Poor_Mixed | 5346.8 | 7932.3 | 1.484 | 0.774 | 6.12 | 0.714 | 5.89 | 0.4709 | 0.7322 | 0.4448 | 0.5513 | 1 | 0.3904 | 0.4841 | 0.5794 | 0.5794 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1067 | 870.8 | 488.6 | 97.6 | 117 | 20.6 | 821.1 | 5332.9 | 47 | 32.6 | 92 | 94.8 | 83.4 | 98.3 | 39.8 | 23.4 | 4828.6 | 5542.1 | 4747.8 | 6692.5 | 8296.2 | 7029.6 | 1.386 | 1.497 | 1.481 | 0.742 | 0.765 | 0.735 | 5.15 | -6.23 | 5.9 | 0.679 | 0.705 | 0.731 | -5.02 | 4.55 | 4.31 | 0.702 | 0.61 | 0.565 | -3.45 | -3.53 | -4.9 | 0.626 | 0.607 | 0.661 | 4.36 | 5.03 | 3.71 | Poor_Mixed | 4747.8 | 6692.5 | 1.386 | 0.765 | 6.23 | 0.731 | 5.03 | 0.4325 | 0.7629 | 0.4695 | 0.6348 | 1 | 0.4048 | 0.5287 | 0.5902 | 0.5902 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1068 | 1592.9 | 887.7 | 139.3 | 178.7 | 34.3 | 1378.6 | 8402.9 | 30.8 | 48.4 | 104.2 | 108.4 | 93 | 114.4 | 44.4 | 31.2 | 1792.2 | 1508.2 | 1770.9 | 2018.9 | 1583.6 | 2106.2 | 1.126 | 1.05 | 1.189 | 0.986 | 0.99 | 0.99 | 9.25 | -9.22 | 9.62 | 0.838 | 0.866 | 0.73 | 7.74 | 7.19 | 8.32 | 0.92 | 0.792 | 0.736 | 8.66 | 5.09 | 7.16 | 0.909 | 0.808 | 0.865 | 6.72 | 8.69 | 5.84 | Very Poor_Mixed | 1508.2 | 1583.6 | 1.05 | 0.99 | 9.62 | 0.92 | 8.69 | 0.0801 | 0.5979 | 0.1496 | 0.3521 | 1 | 0.0389 | 0.2326 | 0.3317 | 0.3317 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1069 | 220.4 | 151.2 | 67.7 | 55 | 4 | 380.9 | 3299.5 | 57.6 | 22.9 | 83.2 | 83.6 | 76.8 | 88.5 | 35 | 10 | 8205.7 | 9107.9 | 8236.5 | 15549.4 | 17361.1 | 14899.1 | 1.895 | 1.906 | 1.809 | 0.729 | 0.797 | 0.719 | 5.91 | 6.69 | 6.35 | 0.516 | 0.62 | 0.623 | 2.68 | -2.75 | 3.47 | 0.5 | 0.584 | 0.536 | -3.12 | -3.41 | 3.22 | 0.668 | 0.543 | 0.617 | 2.93 | 2.55 | 3.25 | Poor_Winding_TD_Cap | 8205.7 | 14899.1 | 1.809 | 0.797 | 6.69 | 0.668 | 3.47 | 0.8479 | 0.9088 | 0.7251 | 1 | 1 | 0.3741 | 0.7132 | 0.7843 | 0.7843 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1070 | 859.7 | 640.4 | 106.7 | 124.5 | 20.9 | 865.9 | 5130.4 | 60 | 20 | 80.4 | 76.1 | 72.8 | 84.9 | 37 | 13.2 | 8305.1 | 9720.8 | 9667 | 15603.1 | 18499 | 18678.2 | 1.879 | 1.903 | 1.932 | 0.589 | 0.508 | 0.5 | 3.02 | 2.02 | -2 | 0.503 | 0.512 | 0.533 | 2.5 | 2.18 | 2.57 | 0.526 | 0.53 | 0.516 | 2.27 | -2.9 | 2.26 | 0.543 | 0.5 | 0.581 | -2.29 | 2.21 | 2.01 | Poor_DGA | 8305.1 | 15603.1 | 1.879 | 0.589 | 3.02 | 0.581 | 2.9 | 0.3974 | 1 | 0.8564 | 0.939 | 1 | 0.8938 | 0.8518 | 0.7904 | 0.7904 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1071 | 394.5 | 256.6 | 76.6 | 70.4 | 2.4 | 489.1 | 3616.1 | 52.4 | 23.4 | 77 | 80.3 | 71.8 | 84.7 | 36.6 | 16.5 | 8858.6 | 9560.3 | 8531.3 | 16490.8 | 17562.2 | 14965.9 | 1.862 | 1.837 | 1.754 | 0.789 | 0.741 | 0.765 | 6.64 | -5.48 | 6.19 | 0.523 | 0.531 | 0.527 | 3.05 | 3 | -2.59 | 0.562 | 0.565 | 0.51 | 2.72 | 2.2 | -2.79 | 0.543 | 0.51 | 0.557 | 2.4 | 2.19 | 3.18 | Poor_Winding_TD_Cap | 8531.3 | 14965.9 | 1.754 | 0.789 | 6.64 | 0.565 | 3.18 | 0.7994 | 0.8988 | 0.8587 | 0.8522 | 1 | 0.3712 | 0.8006 | 0.7923 | 0.7923 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1072 | 187.2 | 231.7 | 70.3 | 55.4 | 1 | 394 | 2969.4 | 59.7 | 22.7 | 78.7 | 77.8 | 72.6 | 82.6 | 35.3 | 10.7 | 9095.2 | 9463.5 | 8702.9 | 17159 | 18767.3 | 15730.7 | 1.887 | 1.983 | 1.808 | 0.531 | 0.53 | 0.511 | -2 | 2.75 | 2.32 | 0.518 | 0.5 | 0.632 | 2.27 | 2.09 | 4.72 | 0.5 | 0.515 | 0.526 | 2.48 | -2.26 | -2.31 | 0.531 | 0.556 | 0.518 | -2 | -2.35 | 2 | Fair_Bushing_TD_Cap | 8702.9 | 15730.7 | 1.808 | 0.531 | 2.75 | 0.632 | 4.72 | 0.9461 | 0.9129 | 0.8739 | 0.9909 | 1 | 0.8845 | 0.8428 | 0.9185 | 0.9185 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1073 | 277.9 | 257.3 | 74.3 | 64.3 | 1 | 2465.7 | 20401 | 50.5 | 31.3 | 79.7 | 77.1 | 71.2 | 81.8 | 35.7 | 12.3 | 8157.8 | 8589.8 | 8683 | 14888.7 | 15644.7 | 16646.9 | 1.825 | 1.821 | 1.917 | 0.605 | 0.624 | 0.639 | -3.51 | -2.69 | -3.29 | 0.585 | 0.563 | 0.5 | -3.47 | 3.78 | -3.08 | 0.657 | 0.543 | 0.571 | 3.72 | 2.88 | 4.83 | 0.575 | 0.571 | 0.969 | 3.07 | 4.72 | 9.39 | Critical_Bushing_TD_Cap | 8157.8 | 14888.7 | 1.821 | 0.639 | 3.51 | 0.969 | 9.39 | 0.7102 | 0.7791 | 0.8875 | 0.9597 | 1 | 0.6802 | 0.6215 | 0.7749 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
1074 | 1418.6 | 773.6 | 135.1 | 160.9 | 24.8 | 1222.6 | 7662.2 | 36.6 | 44.8 | 101.2 | 99.7 | 92.8 | 113 | 43.8 | 32.5 | 1692.1 | 2430.2 | 2238.3 | 2011.3 | 2933.1 | 2753.6 | 1.189 | 1.207 | 1.23 | 0.938 | 0.933 | 0.824 | 8.47 | 8.88 | 8.05 | 0.758 | 0.784 | 0.708 | 5.37 | 7.66 | 8.8 | 0.777 | 0.745 | 0.774 | -7.99 | 7.2 | 5.79 | 0.73 | 0.838 | 0.756 | 6.55 | 7.3 | 7.31 | Very Poor_Mixed | 1692.1 | 2011.3 | 1.189 | 0.938 | 8.88 | 0.838 | 8.8 | 0.1946 | 0.6318 | 0.228 | 0.302 | 1 | 0.1462 | 0.3002 | 0.3969 | 0.3969 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1075 | 100 | 129.3 | 65 | 58.2 | 2.3 | 391.8 | 2727.9 | 59 | 20 | 76.8 | 80.8 | 72.5 | 85.7 | 35.7 | 11.1 | 9126.5 | 9440 | 9556.6 | 16855.2 | 17489.4 | 18481 | 1.847 | 1.853 | 1.934 | 0.513 | 0.548 | 0.5 | -2.17 | 2.87 | 2.09 | 0.615 | 0.757 | 0.563 | 2.99 | -5.25 | 3.17 | 0.552 | 0.53 | 0.593 | 2.6 | 2.86 | -3.7 | 0.542 | 0.538 | 0.586 | 3.24 | 3.26 | 3.02 | Fair_Bushing_TD_Cap | 9126.5 | 16855.2 | 1.847 | 0.548 | 2.87 | 0.757 | 5.25 | 0.8956 | 1 | 0.8496 | 0.984 | 1 | 0.9035 | 0.6778 | 0.8866 | 0.8866 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1076 | 1766 | 982.4 | 148.3 | 188.9 | 34.3 | 1379 | 8516.7 | 12.2 | 22.7 | 77.4 | 78.3 | 72.8 | 83.3 | 36.5 | 16.8 | 10000 | 8993.3 | 9132.4 | 19274.3 | 17483.1 | 17863.7 | 1.927 | 1.944 | 1.956 | 0.552 | 0.622 | 0.604 | 3.56 | 3.76 | -3.35 | 0.592 | 0.568 | 0.558 | 2.61 | 3.41 | -2.71 | 0.557 | 0.568 | 0.536 | 3.12 | 2.85 | -2.93 | 0.576 | 0.567 | 0.567 | 3.14 | 2.9 | 2.87 | Critical_DGA | 8993.3 | 17483.1 | 1.927 | 0.622 | 3.76 | 0.592 | 3.41 | 0.0404 | 0.3296 | 0.8712 | 0.8436 | 1 | 0.6925 | 0.7184 | 0.5652 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
1077 | 889.7 | 512.1 | 112.3 | 121.5 | 20.4 | 879.8 | 6009.7 | 45.4 | 35.2 | 88.3 | 88.5 | 81.8 | 96.3 | 38.4 | 24.4 | 6160.7 | 5598.4 | 5942 | 9787.7 | 8562.2 | 9391.5 | 1.589 | 1.529 | 1.581 | 0.596 | 0.686 | 0.781 | 3.62 | -5.15 | -6.51 | 0.701 | 0.646 | 0.656 | 4.83 | -4.35 | 4.93 | 0.71 | 0.649 | 0.606 | 4.89 | 5.68 | -6.04 | 0.649 | 0.61 | 0.671 | 5.48 | 5.49 | 5.8 | Poor_Mixed | 5598.4 | 8562.2 | 1.529 | 0.781 | 6.51 | 0.71 | 6.04 | 0.4 | 0.7322 | 0.5635 | 0.6005 | 1 | 0.5036 | 0.4875 | 0.5925 | 0.5925 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1078 | 1011.7 | 530.3 | 98.3 | 124.6 | 12.6 | 815.4 | 5756.6 | 44 | 36 | 90.3 | 90.9 | 80.3 | 95.6 | 40.6 | 25 | 6052.5 | 6819.1 | 6133 | 9630 | 11260.4 | 9733.4 | 1.591 | 1.651 | 1.587 | 0.728 | 0.761 | 0.778 | 5.59 | -6.84 | 6.53 | 0.592 | 0.663 | 0.667 | 4.08 | 3.3 | -3.71 | 0.631 | 0.689 | 0.651 | 5.23 | 4.39 | 4.75 | 0.651 | 0.687 | 0.675 | 4.75 | 4.99 | 4.8 | Poor_Mixed | 6052.5 | 9630 | 1.587 | 0.778 | 6.84 | 0.689 | 5.23 | 0.4577 | 0.7231 | 0.5336 | 0.5796 | 1 | 0.3673 | 0.517 | 0.588 | 0.588 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1079 | 931.4 | 466.4 | 99.4 | 119.1 | 19.2 | 827.1 | 5107.5 | 50.6 | 33.1 | 89.4 | 90.7 | 83.2 | 96.8 | 38.6 | 23.4 | 6967.4 | 5915.6 | 5752.3 | 12234.6 | 9138.7 | 9523.4 | 1.756 | 1.545 | 1.656 | 0.754 | 0.786 | 0.755 | 5.73 | -5.99 | 6.12 | 0.718 | 0.595 | 0.641 | 3.08 | 4.68 | 4.54 | 0.686 | 0.729 | 0.696 | -5.2 | 3.95 | -3.85 | 0.687 | 0.699 | 0.704 | -3.25 | 4.7 | -5.39 | Poor_Mixed | 5752.3 | 9138.7 | 1.545 | 0.786 | 6.12 | 0.729 | 5.39 | 0.4366 | 0.7568 | 0.5288 | 0.6348 | 1 | 0.3795 | 0.4895 | 0.5858 | 0.5858 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1080 | 773.8 | 568.7 | 98.6 | 117.5 | 13.7 | 776.8 | 5466.2 | 47.6 | 34.9 | 92.4 | 91.8 | 82.3 | 97.9 | 39.1 | 23.8 | 5443.7 | 5293.1 | 5218.5 | 7573 | 8091 | 7927.8 | 1.391 | 1.529 | 1.519 | 0.774 | 0.737 | 0.768 | 6.41 | -5.97 | -6.52 | 0.626 | 0.696 | 0.701 | 5.25 | 5.11 | 5.21 | 0.671 | 0.738 | 0.652 | -6.7 | 5.38 | 4 | 0.622 | 0.654 | 0.703 | 4.48 | 5.19 | 5.31 | Poor_Mixed | 5218.5 | 7573 | 1.391 | 0.774 | 6.52 | 0.738 | 6.7 | 0.4785 | 0.7356 | 0.4992 | 0.6212 | 1 | 0.3647 | 0.468 | 0.5842 | 0.5842 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1081 | 1064.2 | 574.3 | 114.6 | 128.6 | 22.5 | 937.1 | 6115.8 | 56.3 | 20.2 | 77.5 | 78 | 73.1 | 82.7 | 36.4 | 10 | 9565.7 | 9370 | 9043.4 | 18115.4 | 18277.4 | 17397.8 | 1.894 | 1.951 | 1.924 | 0.506 | 0.504 | 0.545 | 2.59 | 2 | 3.04 | 0.591 | 0.581 | 0.589 | 3.81 | 2.73 | -3.2 | 0.587 | 0.568 | 0.563 | -3.61 | 3.23 | 2 | 0.608 | 0.629 | 0.598 | 2.89 | -2.15 | 3.84 | Poor_DGA | 9043.4 | 17397.8 | 1.894 | 0.545 | 3.04 | 0.629 | 3.84 | 0.3512 | 0.984 | 0.874 | 1 | 1 | 0.8913 | 0.6716 | 0.7489 | 0.7489 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1082 | 104.2 | 197.4 | 66.8 | 59.8 | 1 | 456 | 3292.4 | 59 | 21.6 | 76.1 | 81.2 | 72 | 82.1 | 36.1 | 14.1 | 4816.4 | 5230.6 | 4026.5 | 6816.3 | 7482.1 | 5553.6 | 1.415 | 1.43 | 1.379 | 0.592 | 0.664 | 0.61 | 4.62 | 5.22 | 3.13 | 0.521 | 0.5 | 0.506 | 2.47 | 2.39 | 2 | 0.5 | 0.544 | 0.507 | 2.54 | 2.9 | 2.04 | 0.537 | 0.581 | 0.541 | -2.47 | -2.84 | 2 | Poor_IR_PI | 4026.5 | 5553.6 | 1.379 | 0.664 | 5.22 | 0.581 | 2.9 | 0.9416 | 0.938 | 0.8753 | 0.9169 | 1 | 0.6112 | 0.8594 | 0.8816 | 0.8816 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1083 | 1015.1 | 602.4 | 103.3 | 142 | 22.8 | 877.2 | 5563.9 | 45 | 32.9 | 90.7 | 92.3 | 84.4 | 97.8 | 40.2 | 24.5 | 5768.6 | 6710.5 | 5381.2 | 8835.2 | 11441.7 | 8670 | 1.532 | 1.705 | 1.611 | 0.797 | 0.714 | 0.744 | -6.47 | 5.25 | 5.9 | 0.62 | 0.728 | 0.677 | 4.65 | 5.23 | 5.99 | 0.718 | 0.729 | 0.723 | 4.82 | -5.99 | 5.45 | 0.706 | 0.705 | 0.725 | 4.25 | 4.7 | 4.8 | Poor_Mixed | 5381.2 | 8670 | 1.532 | 0.797 | 6.47 | 0.729 | 5.99 | 0.3594 | 0.7593 | 0.4874 | 0.597 | 1 | 0.3956 | 0.4347 | 0.5532 | 0.5532 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1084 | 730 | 442.1 | 100.6 | 107.6 | 16.6 | 737.7 | 4739.6 | 46.3 | 35.2 | 87.9 | 88.9 | 80.4 | 96.4 | 38.7 | 25 | 4639.1 | 5380 | 5512.8 | 6858.2 | 8083.7 | 8085.1 | 1.478 | 1.503 | 1.467 | 0.816 | 0.773 | 0.772 | -6.51 | 6.37 | 6.27 | 0.691 | 0.64 | 0.713 | 3.76 | 4.2 | 5.63 | 0.664 | 0.631 | 0.665 | 4.17 | 3.61 | -5.15 | 0.708 | 0.625 | 0.677 | 5.57 | 4.34 | 4.68 | Poor_Mixed | 4639.1 | 6858.2 | 1.467 | 0.816 | 6.51 | 0.713 | 5.63 | 0.4971 | 0.7322 | 0.5703 | 0.5796 | 1 | 0.3379 | 0.4969 | 0.5949 | 0.5949 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1085 | 1631.5 | 928.2 | 137.3 | 188.1 | 29.4 | 1275.6 | 8440.9 | 33.6 | 47.2 | 107.3 | 109.3 | 94.7 | 118.3 | 43.5 | 31 | 2144.9 | 3178.9 | 1667.3 | 2438.6 | 3959.7 | 1834.2 | 1.137 | 1.246 | 1.1 | 0.934 | 0.943 | 0.933 | 8.85 | 8.57 | 9.17 | 0.901 | 0.966 | 0.818 | 6.88 | -8.71 | 8.62 | 0.934 | 0.69 | 0.757 | 8.64 | -8.57 | -9.84 | 0.761 | 0.741 | 0.875 | -7.24 | -6.87 | 7.67 | Very Poor_Mixed | 1667.3 | 1834.2 | 1.1 | 0.943 | 9.17 | 0.966 | 9.84 | 0.0994 | 0.609 | 0.1051 | 0.3597 | 1 | 0.0986 | 0.2097 | 0.338 | 0.338 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1086 | 1200.6 | 696.7 | 119.9 | 147.9 | 23.5 | 1001.6 | 6872.1 | 57 | 23.5 | 75 | 76.3 | 70 | 80 | 35 | 10.9 | 8358.7 | 8814.1 | 8176.8 | 15285.8 | 16733.1 | 15065.5 | 1.829 | 1.898 | 1.842 | 0.604 | 0.513 | 0.556 | 2.76 | 2.95 | 3.09 | 0.563 | 0.566 | 0.556 | -2.54 | 2 | 2.93 | 0.547 | 0.508 | 0.5 | 2.58 | 2.74 | 2.65 | 0.503 | 0.541 | 0.586 | 2.45 | 2.94 | 2.42 | Poor_DGA | 8176.8 | 15065.5 | 1.829 | 0.604 | 3.09 | 0.586 | 2.94 | 0.2839 | 0.8969 | 0.9788 | 0.9875 | 1 | 0.7877 | 0.8074 | 0.7415 | 0.7415 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1087 | 287.3 | 279.2 | 72.2 | 108.6 | 3.1 | 524.6 | 2607.1 | 54.5 | 26.2 | 95 | 94.4 | 84.4 | 102.1 | 40.4 | 11.4 | 8914.1 | 8067.8 | 7571.1 | 16428.9 | 14718.5 | 13330.1 | 1.843 | 1.824 | 1.761 | 0.534 | 0.543 | 0.509 | 2.71 | 2.66 | 2 | 0.537 | 0.599 | 0.603 | 2.94 | 2.98 | 2.51 | 0.516 | 0.547 | 0.533 | 2.61 | 3.67 | 2.91 | 0.562 | 0.571 | 0.571 | 2.76 | -3.18 | 2.36 | Poor_Thermal | 7571.1 | 13330.1 | 1.761 | 0.543 | 2.71 | 0.603 | 3.67 | 0.7513 | 0.8505 | 0.4241 | 0.9783 | 1 | 0.8691 | 0.7381 | 0.7957 | 0.7957 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1088 | 465.1 | 330 | 72.2 | 75.5 | 3 | 551.3 | 3815.5 | 55.3 | 23.1 | 75.4 | 76.9 | 71.9 | 81.1 | 35.4 | 10.1 | 9249.7 | 8634 | 8440.4 | 16640.1 | 15673.9 | 15525.1 | 1.799 | 1.815 | 1.839 | 0.781 | 0.795 | 0.831 | 7.11 | 6.49 | 7.33 | 0.522 | 0.567 | 0.577 | -3.54 | -2.29 | 2.5 | 0.544 | 0.538 | 0.626 | 2 | 2.94 | 3.68 | 0.575 | 0.567 | 0.576 | -3.07 | 3.4 | -2.3 | Poor_Winding_TD_Cap | 8440.4 | 15525.1 | 1.799 | 0.831 | 7.33 | 0.626 | 3.68 | 0.7562 | 0.9047 | 0.9344 | 0.9992 | 1 | 0.2941 | 0.7282 | 0.7733 | 0.7733 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1089 | 454.6 | 269.6 | 87.1 | 80.8 | 4.9 | 434 | 3516.8 | 53.7 | 29.2 | 76.6 | 129.2 | 70 | 80 | 36 | 12.1 | 843.4 | 1133.9 | 690 | 902.6 | 1156.6 | 704.6 | 1.07 | 1.02 | 1.021 | 0.796 | 0.712 | 0.743 | 6.53 | 5.55 | -6.46 | 0.542 | 0.583 | 0.563 | 3.79 | 3.75 | -2.2 | 0.547 | 0.589 | 0.572 | 3.2 | -4.1 | 3.22 | 0.612 | 0.551 | 0.572 | 2.31 | 2.6 | 2.21 | Critical_IR_PI | 690 | 704.6 | 1.02 | 0.796 | 6.53 | 0.612 | 4.1 | 0.7382 | 0.8067 | 0.7214 | 0.964 | 0.85 | 0.3799 | 0.7087 | 0.7185 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1090 | 845.7 | 488.2 | 96.2 | 98.6 | 15.4 | 810.1 | 5159.4 | 47.9 | 31.2 | 86 | 85.4 | 80 | 93.8 | 38.1 | 23.5 | 6556.8 | 5836.1 | 6642.6 | 11095.2 | 9710.2 | 10735.3 | 1.692 | 1.664 | 1.616 | 0.654 | 0.674 | 0.674 | -4.28 | 5.37 | 4.88 | 0.671 | 0.674 | 0.609 | 4.03 | 4.63 | 3.24 | 0.594 | 0.694 | 0.584 | 4.16 | 3.9 | 4.8 | 0.618 | 0.61 | 0.669 | 4.44 | 4.01 | 3.79 | Poor_Mixed | 5836.1 | 9710.2 | 1.616 | 0.674 | 5.37 | 0.694 | 4.8 | 0.4897 | 0.7804 | 0.6273 | 0.6314 | 1 | 0.5299 | 0.5586 | 0.6451 | 0.6451 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1091 | 199.4 | 251.8 | 75.8 | 68.8 | 1 | 383 | 3252.5 | 30.6 | 49.4 | 81.9 | 85.6 | 77.8 | 89 | 38 | 15.5 | 4067.7 | 5518.6 | 4779.8 | 5709.1 | 7826.6 | 6812.4 | 1.404 | 1.418 | 1.425 | 0.675 | 0.728 | 0.682 | 4.12 | 5.37 | -14.94 | 0.595 | 0.533 | 0.565 | 3.3 | -4.72 | -3.35 | 0.604 | 0.558 | 0.574 | 3.19 | -3.15 | 3.06 | 0.524 | 0.551 | 0.583 | -3.79 | 3.3 | -2.55 | Critical_Oil | 4067.7 | 5709.1 | 1.404 | 0.728 | 14.94 | 0.604 | 4.72 | 0.9193 | 0.5888 | 0.6964 | 0.88 | 1 | 0.417 | 0.7039 | 0.7592 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
1092 | 209 | 178.7 | 71.5 | 63.8 | 2.5 | 450.1 | 3515.9 | 56 | 22.8 | 79.3 | 78.2 | 73 | 84.6 | 37.2 | 10.4 | 8826.9 | 9131 | 8958 | 16960.3 | 16731.5 | 16695.4 | 1.921 | 1.832 | 1.864 | 0.61 | 0.58 | 0.574 | 3.61 | -2.85 | 2.94 | 0.507 | 0.558 | 0.567 | -2.13 | 3.66 | -3.21 | 0.863 | 0.507 | 0.57 | -7.64 | 3.73 | 3.29 | 0.533 | 0.542 | 0.555 | -2.01 | -2.9 | 3.21 | Poor_Bushing_TD_Cap | 8826.9 | 16695.4 | 1.832 | 0.61 | 3.61 | 0.863 | 7.64 | 0.8437 | 0.9108 | 0.8419 | 0.9955 | 1 | 0.7241 | 0.7094 | 0.8432 | 0.8432 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1093 | 191.9 | 177.4 | 66.3 | 71.4 | 1 | 452.5 | 3100 | 30.6 | 49.4 | 83.8 | 81.6 | 73.8 | 89.1 | 36.9 | 15.9 | 4887.5 | 4971.1 | 4919.8 | 6707.3 | 7041.9 | 7295 | 1.372 | 1.417 | 1.483 | 0.697 | 0.653 | 0.601 | 5.16 | -4.02 | 3.95 | 0.612 | 0.603 | 0.593 | 3.33 | -2.47 | 2.82 | 0.567 | 0.553 | 0.519 | -23.42 | 3.36 | 3.69 | 0.546 | 0.569 | 0.575 | -2.23 | 2.57 | 3.24 | Critical_Oil | 4887.5 | 6707.3 | 1.372 | 0.697 | 5.16 | 0.612 | 23.42 | 0.9188 | 0.5888 | 0.7475 | 0.869 | 1 | 0.5768 | 0.6853 | 0.7827 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
1094 | 1619.4 | 862.4 | 144.4 | 182.6 | 33.7 | 1233.3 | 8009.8 | 51.3 | 29.2 | 80.5 | 78.7 | 74.2 | 85.6 | 36.2 | 17.3 | 7124.1 | 7563.7 | 7526.3 | 11633.8 | 13048 | 13419.7 | 1.633 | 1.725 | 1.783 | 0.582 | 0.591 | 0.565 | 3.29 | 2.73 | -13.49 | 0.599 | 0.608 | 0.56 | 3.36 | 4.06 | -2.97 | 0.535 | 0.606 | 0.617 | -3.08 | 3.5 | 3.49 | 0.605 | 0.538 | 0.631 | 3.36 | -3.1 | 4.26 | Critical_DGA | 7124.1 | 11633.8 | 1.633 | 0.591 | 13.49 | 0.631 | 4.26 | 0.0972 | 0.8067 | 0.8169 | 0.8291 | 1 | 0.6151 | 0.6585 | 0.6089 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1095 | 1628.8 | 925.2 | 148.3 | 194.5 | 34.2 | 1379 | 8618.7 | 52.3 | 29.3 | 81.9 | 87 | 75.8 | 89.8 | 37 | 15.2 | 8809.4 | 8911.6 | 8088 | 16119.1 | 8409.8 | 14598.4 | 1.83 | 0.944 | 1.805 | 0.585 | 0.558 | 0.539 | -3.53 | 2.65 | 3.24 | 0.5 | 0.608 | 0.607 | 2.74 | 2.42 | 2.86 | 0.551 | 0.542 | 0.608 | -2.25 | -2.82 | 3.09 | 0.595 | 0.511 | 0.567 | 3.5 | 3.39 | -2.57 | Critical_DGA | 8088 | 8409.8 | 0.944 | 0.585 | 3.53 | 0.608 | 3.5 | 0.0508 | 0.8054 | 0.7024 | 0.8882 | 0.8187 | 0.7627 | 0.7422 | 0.5954 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1096 | 299.6 | 236.2 | 76.9 | 66.3 | 1 | 538.1 | 3408 | 41.2 | 37.8 | 75 | 76.2 | 72.5 | 83.2 | 35.5 | 14.4 | 6450.5 | 6334.7 | 7141 | 10412.1 | 9709.8 | 11887.6 | 1.614 | 1.533 | 1.665 | 0.552 | 0.593 | 0.602 | 3.24 | 2.79 | -4.32 | 0.551 | 0.518 | 0.533 | 2.9 | 2 | 2.6 | 0.517 | 0.558 | 0.5 | -2.26 | 2.81 | -3.17 | 0.506 | 0.538 | 0.523 | -2.76 | 2.46 | -2.86 | Poor_Oil | 6334.7 | 9709.8 | 1.533 | 0.602 | 4.32 | 0.558 | 3.17 | 0.8862 | 0.7032 | 0.935 | 0.9092 | 1 | 0.7128 | 0.8333 | 0.8547 | 0.8547 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1097 | 212.7 | 221.1 | 67.8 | 58.3 | 4.4 | 396.1 | 2770.3 | 57.2 | 22.1 | 81 | 80 | 72.2 | 85 | 36.3 | 14.6 | 8079.5 | 8217.9 | 8670.9 | 14510.6 | 15628.6 | 16515.9 | 1.796 | 1.902 | 1.905 | 0.827 | 0.847 | 0.782 | 7.24 | -7.17 | 6.31 | 0.522 | 0.544 | 0.505 | 2.91 | 2.73 | 3.2 | 0.612 | 0.524 | 0.551 | 2.83 | 2.62 | -3.12 | 0.573 | 0.598 | 0.557 | 2.9 | 3.67 | -3.28 | Poor_Winding_TD_Cap | 8079.5 | 14510.6 | 1.796 | 0.847 | 7.24 | 0.612 | 3.67 | 0.8279 | 0.926 | 0.8203 | 0.904 | 1 | 0.2852 | 0.7484 | 0.78 | 0.78 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1098 | 1105.9 | 608.7 | 113.5 | 142.4 | 21 | 998.6 | 6359.6 | 55.6 | 24.6 | 81.1 | 83.5 | 74.4 | 88.4 | 36.2 | 13.4 | 9496.5 | 9619.2 | 8911.6 | 18368.9 | 18265.9 | 17025.1 | 1.934 | 1.899 | 1.91 | 0.545 | 0.649 | 0.592 | -2.59 | -3.62 | 2.62 | 0.537 | 0.531 | 0.607 | -2.9 | 2.43 | -3.21 | 0.518 | 0.561 | 0.548 | 2.33 | -2.6 | 2.78 | 0.55 | 0.528 | 0.559 | 2.88 | 2.38 | -3.63 | Poor_DGA | 8911.6 | 17025.1 | 1.899 | 0.649 | 3.62 | 0.607 | 3.63 | 0.3306 | 0.8768 | 0.7562 | 0.9342 | 1 | 0.7326 | 0.7647 | 0.7104 | 0.7104 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1099 | 1644.6 | 937.1 | 146.4 | 182.8 | 31.7 | 1307 | 7979.2 | 36.4 | 43.6 | 103.1 | 103.4 | 91 | 112.5 | 43.4 | 29.3 | 2702.1 | 3017 | 2271.3 | 3250.2 | 3740.1 | 2598.6 | 1.203 | 1.24 | 1.144 | 0.893 | 0.963 | 0.944 | 9.02 | -8.82 | 8.46 | 0.796 | 0.803 | 0.814 | -5.25 | 6.29 | 7.54 | 0.819 | 0.831 | 0.881 | 4.25 | -5.73 | 7.76 | 0.73 | 0.92 | 0.759 | -8.27 | -7.34 | 6.43 | Very Poor_Mixed | 2271.3 | 2598.6 | 1.144 | 0.963 | 9.02 | 0.92 | 8.27 | 0.0867 | 0.6435 | 0.2115 | 0.4238 | 1 | 0.106 | 0.2677 | 0.3642 | 0.3642 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1100 | 424.4 | 293.1 | 85.2 | 156.2 | 2.4 | 560.9 | 3766.5 | 56.1 | 23 | 105.9 | 106.3 | 93.8 | 114.5 | 45.2 | 13.5 | 9410 | 9232.4 | 9044.1 | 17779.3 | 17309 | 17209.3 | 1.889 | 1.875 | 1.903 | 0.65 | 0.661 | 0.619 | 4.24 | 3.82 | 5.08 | 0.582 | 0.53 | 2.322 | 3.49 | 2.86 | 3.32 | 0.614 | 0.593 | 0.602 | 4.61 | 3.87 | -4.93 | 0.645 | 0.611 | 0.607 | -2.96 | 2.91 | -3.72 | Critical_Thermal | 9044.1 | 17209.3 | 1.875 | 0.661 | 5.08 | 2.322 | 4.93 | 0.6872 | 0.9067 | 0.1408 | 0.9318 | 1 | 0.5822 | 0.5896 | 0.6889 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H4
1101 | 156.8 | 122 | 70.2 | 51.3 | 1.4 | 350 | 2866.8 | 53.9 | 25 | 77.7 | 75 | 73.3 | 81.4 | 35.8 | 11.9 | 9308.6 | 9641.9 | 9568.5 | 16903.7 | 18383 | 18183.8 | 1.816 | 1.907 | 1.9 | 0.503 | 0.5 | 0.5 | -2.7 | -2.04 | -2.38 | 0.506 | 0.562 | 0.759 | 2.29 | 3.51 | 6.15 | 0.537 | 0.607 | 0.556 | 3.43 | 2.58 | 2.42 | 0.531 | 0.525 | 0.594 | 2.81 | 3.07 | 2.63 | Poor_Bushing_TD_Cap | 9308.6 | 16903.7 | 1.816 | 0.503 | 2.7 | 0.759 | 6.15 | 0.9402 | 0.87 | 0.9192 | 0.9682 | 1 | 0.9589 | 0.7134 | 0.9024 | 0.9024 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1102 | 784.7 | 480.6 | 96.5 | 105.2 | 16.3 | 813.3 | 5233.3 | 49.9 | 30.4 | 88 | 89.2 | 80.9 | 96.4 | 39.6 | 24.4 | 7435.9 | 7878.6 | 6694.8 | 12763.4 | 13507.4 | 11219.5 | 1.716 | 1.714 | 1.676 | 0.66 | 0.669 | 0.605 | 4.74 | 4.73 | 4.1 | 0.64 | 0.62 | 0.669 | 3.92 | -4.62 | 4.62 | 0.639 | 0.662 | 0.643 | 3.49 | 4.39 | 4.67 | 0.683 | 0.633 | 0.602 | 3.76 | 4.71 | -3.62 | Poor_Mixed | 6694.8 | 11219.5 | 1.676 | 0.669 | 4.74 | 0.683 | 4.71 | 0.4811 | 0.7907 | 0.5588 | 0.6005 | 1 | 0.5728 | 0.5426 | 0.6389 | 0.6389 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1103 | 292.5 | 266 | 76.3 | 67.1 | 1 | 454.9 | 3015.9 | 31 | 84.5 | 79.1 | 81.3 | 74.3 | 86.3 | 37.3 | 12 | 4199.4 | 5458.6 | 4795.7 | 5751.2 | 8361 | 7010 | 1.37 | 1.532 | 1.462 | 0.72 | 0.689 | 0.649 | 4.57 | 5.04 | 4.29 | 0.58 | 0.576 | 0.553 | 3.88 | 3.03 | 4.07 | 0.633 | 0.629 | 0.569 | 2.31 | 3.51 | 3.87 | 0.578 | 0.579 | 0.586 | 2.28 | 3.9 | 2.81 | Critical_Oil | 4199.4 | 5751.2 | 1.37 | 0.72 | 5.04 | 0.633 | 4.07 | 0.8983 | 0.5833 | 0.7965 | 0.9661 | 1 | 0.5245 | 0.6669 | 0.776 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1104 | 1699.7 | 859.8 | 147.5 | 189.1 | 34.3 | 1282.7 | 8090.4 | 32.1 | 47 | 108.3 | 105.7 | 96.2 | 118.7 | 44.6 | 33.9 | 2053.4 | 2701 | 950.8 | 2359.3 | 3294.1 | 1200 | 1.149 | 1.22 | 1.262 | 0.946 | 0.953 | 0.935 | 9.51 | 9.47 | 8.05 | 0.869 | 0.879 | 0.901 | -5.83 | -6.94 | -8.52 | 0.733 | 0.893 | 0.8 | 6.66 | 7.75 | -7.21 | 0.832 | 0.919 | 0.747 | 6.8 | 6.47 | -6.51 | Very Poor_Mixed | 950.8 | 1200 | 1.149 | 0.953 | 9.51 | 0.919 | 8.52 | 0.0749 | 0.6109 | 0.1011 | 0.2473 | 1 | 0.086 | 0.2306 | 0.3281 | 0.3281 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1105 | 846.7 | 509.9 | 106.8 | 120.4 | 21 | 783.4 | 5073.8 | 45.9 | 32.5 | 94 | 89.6 | 81 | 99.3 | 39.6 | 24.2 | 6840.5 | 5803.2 | 5952.3 | 11148.5 | 8814.9 | 9060.9 | 1.63 | 1.519 | 1.522 | 0.691 | 0.709 | 0.675 | 5.87 | 5.43 | -5.06 | 0.585 | 0.722 | 0.619 | -5.39 | 5.59 | 4.08 | 0.636 | 0.638 | 0.609 | 5.91 | 4.85 | 5.35 | 0.717 | 0.653 | 0.638 | 3.4 | 4.12 | 5.15 | Poor_Mixed | 5803.2 | 8814.9 | 1.519 | 0.709 | 5.87 | 0.722 | 5.91 | 0.4271 | 0.7641 | 0.5018 | 0.6074 | 1 | 0.4716 | 0.5163 | 0.598 | 0.598 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1106 | 507.3 | 293.6 | 81.2 | 82.8 | 10.1 | 506 | 3599.4 | 60 | 20 | 75 | 79.1 | 73.1 | 82.3 | 35.5 | 13.5 | 9889.7 | 8978.3 | 10000 | 19504 | 17263 | 19694.9 | 1.972 | 1.923 | 1.969 | 0.5 | 0.5 | 0.521 | -2.05 | 2.64 | -2.03 | 0.553 | 0.531 | 0.5 | -2 | 2.72 | 2.43 | 0.565 | 0.525 | 0.522 | -2.35 | -2.74 | 2.13 | 0.5 | 0.5 | 0.509 | 2.63 | -2.32 | 2.19 | Fair_DGA | 8978.3 | 17263 | 1.923 | 0.521 | 2.64 | 0.565 | 2.74 | 0.6637 | 1 | 0.9042 | 0.9318 | 1 | 0.9518 | 0.8722 | 0.8732 | 0.8732 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1107 | 483.2 | 301.4 | 79.8 | 77.7 | 3.7 | 568 | 3599.5 | 59.6 | 21.8 | 79.8 | 82.9 | 73.3 | 85.7 | 35.6 | 14.8 | 8643.5 | 10000 | 9292.5 | 16261.6 | 20000 | 17619.3 | 1.881 | 2 | 1.896 | 0.561 | 0.57 | 0.595 | 2.74 | 2.65 | -3.59 | 0.521 | 0.5 | 0.618 | 2.81 | 2.2 | 2.36 | 0.511 | 0.563 | 0.561 | 2.25 | 4.23 | 2.1 | 0.837 | 0.572 | 0.553 | 6.34 | 2.53 | 2.77 | Poor_Bushing_TD_Cap | 8643.5 | 16261.6 | 1.881 | 0.595 | 3.59 | 0.837 | 6.34 | 0.737 | 0.9331 | 0.797 | 0.8988 | 1 | 0.7507 | 0.726 | 0.8166 | 0.8166 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1108 | 879.8 | 554.1 | 104 | 103.9 | 17.3 | 825.3 | 5064.8 | 44.4 | 35.3 | 93.2 | 93 | 82 | 98.9 | 41.3 | 25.1 | 6091.2 | 4672.8 | 5128.7 | 9497 | 6624.5 | 7553.5 | 1.559 | 1.418 | 1.473 | 0.719 | 0.753 | 0.702 | -5.18 | 6.03 | 5.43 | 0.651 | 0.7 | 0.641 | -3.53 | -5.16 | 3.97 | 0.623 | 0.679 | 0.614 | 3.63 | 5.66 | 4.14 | 0.603 | 0.737 | 0.633 | 3.58 | -5.12 | 3.95 | Poor_Mixed | 4672.8 | 6624.5 | 1.418 | 0.753 | 6.03 | 0.737 | 5.66 | 0.455 | 0.731 | 0.4692 | 0.576 | 1 | 0.4365 | 0.5276 | 0.5933 | 0.5933 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1109 | 677.8 | 442.5 | 92.4 | 102.9 | 14.4 | 710.1 | 5062.2 | 47.6 | 31.9 | 88.1 | 88.1 | 77.2 | 95.5 | 40.1 | 22.3 | 6452.5 | 6312.6 | 7093 | 10300.3 | 9470.6 | 11841.8 | 1.596 | 1.5 | 1.67 | 0.699 | 0.646 | 0.666 | 4.36 | 4.89 | 5.7 | 0.647 | 0.705 | 0.609 | 3.38 | -4.69 | -5.11 | 0.593 | 0.611 | 0.614 | -4.19 | -4.39 | 4.71 | 0.597 | 0.651 | 0.537 | 4.77 | 4.25 | 4.26 | Poor_Mixed | 6312.6 | 9470.6 | 1.5 | 0.699 | 5.7 | 0.705 | 5.11 | 0.5273 | 0.7716 | 0.592 | 0.6719 | 1 | 0.5195 | 0.5746 | 0.6533 | 0.6533 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1110 | 167.7 | 172.6 | 66.1 | 50.1 | 1.8 | 391.2 | 2590.6 | 54.7 | 25 | 75.4 | 77.4 | 71.2 | 80.1 | 36.4 | 15.1 | 9285.1 | 8753 | 8747.4 | 18287.1 | 15944.5 | 16312.7 | 1.97 | 1.822 | 1.865 | 0.597 | 0.524 | 0.563 | 2.86 | 2.54 | 3.02 | 0.596 | 0.506 | 0.545 | -3.62 | 3.55 | 2.43 | 0.532 | 0.51 | 0.727 | 2 | 3.52 | 5.53 | 0.53 | 0.606 | 0.564 | 2.41 | 2.6 | -2.74 | Poor_Bushing_TD_Cap | 8747.4 | 15944.5 | 1.822 | 0.597 | 3.02 | 0.727 | 5.53 | 0.9131 | 0.87 | 0.9362 | 0.8908 | 1 | 0.7871 | 0.7299 | 0.8724 | 0.8724 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1111 | 868.6 | 521.2 | 100 | 109.1 | 18.3 | 868.5 | 5700.9 | 45.4 | 35.3 | 90 | 90.9 | 82.3 | 99.4 | 39.9 | 25.9 | 6055.2 | 6067.8 | 5666 | 9900.6 | 9261.6 | 8712.4 | 1.635 | 1.526 | 1.538 | 0.678 | 0.727 | 0.711 | 5.45 | 5.75 | 5.83 | 0.609 | 0.688 | 0.662 | 3.9 | 3.73 | -4.35 | 0.669 | 0.668 | 0.6 | -5.66 | 3.66 | 5.98 | 0.666 | 0.686 | 0.638 | 4.99 | 4.51 | -3.59 | Poor_Mixed | 5666 | 8712.4 | 1.526 | 0.727 | 5.83 | 0.688 | 5.98 | 0.439 | 0.731 | 0.5081 | 0.5478 | 1 | 0.4466 | 0.5189 | 0.5916 | 0.5916 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1112 | 664.6 | 422.3 | 93.3 | 98.2 | 3.5 | 657.2 | 4464.7 | 35.4 | 45.8 | 82.8 | 80.2 | 76.1 | 91.6 | 37.3 | 15.2 | 5564.4 | 5807.7 | 5028.1 | 8309.1 | 8743.7 | 7107.5 | 1.493 | 1.506 | 1.414 | 0.664 | 0.661 | 0.568 | 4.77 | 4.78 | 3.61 | 0.5 | 1.154 | 0.5 | -2.97 | 2.17 | -2.33 | 0.519 | 0.5 | 0.528 | 2.02 | 2.24 | 2.24 | 0.506 | 0.553 | 0.5 | 2 | -2.17 | 2.28 | Critical_Oil | 5028.1 | 7107.5 | 1.414 | 0.664 | 4.78 | 1.154 | 2.97 | 0.6593 | 0.6222 | 0.7346 | 0.8882 | 1 | 0.5986 | 0.8455 | 0.7534 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1113 | 1672.7 | 882 | 143.2 | 185 | 34.3 | 1262.7 | 8066.5 | 34 | 47.6 | 101.8 | 105.8 | 89.9 | 111.8 | 44.3 | 30.5 | 2816.2 | 2058.5 | 2083.8 | 3520.5 | 2416.1 | 2403.7 | 1.25 | 1.174 | 1.154 | 0.893 | 0.965 | 0.946 | 9.45 | 9.47 | 9.21 | 0.915 | 0.796 | 0.781 | 7.39 | -6.76 | 7.4 | 0.768 | 0.905 | 0.791 | -6.02 | 8.73 | 7.86 | 0.868 | 0.889 | 0.717 | 7.31 | -7.07 | 9.05 | Very Poor_Mixed | 2058.5 | 2403.7 | 1.154 | 0.965 | 9.47 | 0.915 | 9.05 | 0.0837 | 0.6053 | 0.2089 | 0.3787 | 1 | 0.0744 | 0.2279 | 0.3448 | 0.3448 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1114 | 1661.6 | 940.9 | 145.5 | 184.1 | 34.3 | 1345.6 | 8448.1 | 30.8 | 46.3 | 106 | 107.3 | 95.4 | 116.2 | 44.4 | 33.8 | 2447.3 | 1793.7 | 1395 | 2869.6 | 2151.2 | 1510.4 | 1.173 | 1.199 | 1.083 | 0.958 | 0.971 | 0.903 | 9.84 | 9.21 | 8.12 | 0.827 | 0.817 | 0.795 | -8.68 | 7.73 | 6.71 | 0.887 | 0.718 | 0.881 | 7.72 | 5.85 | 6.8 | 0.907 | 0.873 | 0.781 | 8.27 | 6.55 | 8.88 | Very Poor_Mixed | 1395 | 1510.4 | 1.083 | 0.971 | 9.84 | 0.907 | 8.88 | 0.063 | 0.6175 | 0.1232 | 0.2513 | 1 | 0.0844 | 0.223 | 0.3267 | 0.3267 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1115 | 1637.6 | 857.5 | 138.4 | 177.2 | 34.3 | 1325.1 | 8382.2 | 35.2 | 46.9 | 105.5 | 107.3 | 95 | 115.6 | 43.4 | 31.2 | 2639.4 | 2145.2 | 1900.4 | 3164.7 | 2503.3 | 2178.6 | 1.199 | 1.167 | 1.146 | 0.937 | 0.911 | 0.935 | 8.72 | 8.97 | 8.69 | 0.788 | 0.806 | 0.735 | 8.62 | -5.32 | 9.22 | 0.706 | 0.759 | 0.765 | 7.48 | 8.93 | 6.54 | 0.783 | 0.802 | 0.764 | 8.18 | 6.99 | 7.15 | Very Poor_Mixed | 1900.4 | 2178.6 | 1.146 | 0.937 | 8.97 | 0.806 | 9.22 | 0.0882 | 0.6119 | 0.1384 | 0.3521 | 1 | 0.1082 | 0.2797 | 0.3524 | 0.3524 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1116 | 246.4 | 232.9 | 72.4 | 66.6 | 1 | 432.3 | 2854 | 30.6 | 47.8 | 87.6 | 86.6 | 78 | 89.5 | 38.8 | 18.1 | 4800.4 | 4677.6 | 4083.9 | 7044.3 | 6496 | 5911.3 | 1.467 | 1.389 | 1.447 | 0.707 | 0.665 | 0.705 | 4.69 | 3.98 | 5.01 | 0.583 | 2.357 | 0.532 | 3.71 | 3.1 | 2.32 | 0.551 | 0.571 | 0.55 | 2.94 | 2.33 | 2.12 | 0.597 | 0.561 | 0.542 | 2.88 | 3.63 | 2.97 | Critical_Oil | 4083.9 | 5911.3 | 1.389 | 0.707 | 5.01 | 2.357 | 3.71 | 0.9145 | 0.6035 | 0.6384 | 0.8054 | 1 | 0.5225 | 0.6795 | 0.7606 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1117 | 453.8 | 231.4 | 80.4 | 69.4 | 1.8 | 529.2 | 3907.5 | 52 | 28.6 | 79.7 | 79.3 | 73.8 | 87.5 | 37.6 | 12.1 | 1912.5 | 3635.4 | 1903.6 | 2129.8 | 4626.8 | 2196.6 | 1.114 | 1.273 | 1.154 | 0.726 | 0.653 | 0.705 | 5.36 | -4.52 | -5.52 | 0.569 | 0.569 | 0.592 | 3.63 | 3.59 | -4.27 | 2.131 | 0.618 | 0.613 | 3.75 | 3.51 | -4.55 | 0.621 | 0.592 | 0.622 | 3.88 | 3.29 | 3.37 | Critical_IR_PI | 1903.6 | 2129.8 | 1.114 | 0.726 | 5.52 | 2.131 | 4.55 | 0.8046 | 0.815 | 0.8047 | 0.964 | 1 | 0.4877 | 0.5786 | 0.7601 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1118 | 1617.6 | 871.5 | 139.3 | 181.9 | 34.3 | 1343.2 | 7548.9 | 35.6 | 46.5 | 101.8 | 102.7 | 92.7 | 113.4 | 43.4 | 31.8 | 1783.8 | 2064.7 | 1892.8 | 1965 | 2515.4 | 2096.8 | 1.102 | 1.218 | 1.108 | 0.966 | 0.937 | 0.89 | -8.42 | 8.61 | 8.21 | 0.819 | 0.882 | 0.916 | 8.27 | -6.86 | -6.2 | 0.819 | 0.802 | 0.959 | 9.09 | 8.71 | 6.64 | 0.83 | 0.905 | 0.909 | 8.52 | 6.05 | 7.19 | Very Poor_Mixed | 1783.8 | 1965 | 1.102 | 0.966 | 8.61 | 0.959 | 9.09 | 0.0923 | 0.6156 | 0.2087 | 0.3291 | 1 | 0.1255 | 0.1855 | 0.3452 | 0.3452 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1119 | 1709.8 | 979.8 | 148.3 | 197 | 34.3 | 1358.3 | 8488.9 | 51.8 | 27.7 | 76 | 77.3 | 70.8 | 80.2 | 35 | 16.4 | 9367.6 | 7851.9 | 8808.1 | 17518.1 | 14168 | 17419.5 | 1.87 | 1.804 | 1.978 | 0.549 | 0.577 | 0.556 | 2.54 | 3.31 | -2.45 | 0.572 | 0.516 | 0.526 | 2.15 | 14.14 | 2.86 | 0.567 | 0.56 | 0.51 | 2 | -2.3 | 2.96 | 0.552 | 0.54 | 0.531 | 2.91 | -2.65 | 2.79 | Critical_DGA | 7851.9 | 14168 | 1.804 | 0.577 | 3.31 | 0.572 | 14.14 | 0.0407 | 0.8279 | 0.9382 | 0.855 | 1 | 0.7873 | 0.7641 | 0.6538 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
1120 | 1654 | 886.2 | 141.7 | 170.3 | 33.3 | 1228.1 | 8240.8 | 35.4 | 45.2 | 106.2 | 108.3 | 96 | 117.5 | 45.6 | 31.8 | 1813.6 | 1394.6 | 2080.3 | 2253.4 | 1464.3 | 2422.8 | 1.243 | 1.05 | 1.165 | 0.928 | 0.933 | 0.954 | -9.32 | 9.23 | 9.84 | 0.802 | 0.804 | 0.922 | 6.73 | 6.74 | -8.61 | 0.823 | 0.752 | 0.805 | -8.01 | -7.62 | 8.53 | 0.966 | 0.73 | 0.928 | 6.12 | 7.28 | -6.89 | Very Poor_Mixed | 1394.6 | 1464.3 | 1.05 | 0.954 | 9.84 | 0.966 | 8.61 | 0.1039 | 0.628 | 0.098 | 0.3291 | 1 | 0.0674 | 0.2219 | 0.337 | 0.337 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1121 | 870.1 | 549.8 | 101.5 | 130.6 | 22.2 | 845.6 | 5987.9 | 47.1 | 34.7 | 92.1 | 90.8 | 84.6 | 97.7 | 39.7 | 24.8 | 5315.2 | 6301.1 | 4392 | 8237.4 | 9746.2 | 6460 | 1.55 | 1.547 | 1.471 | 0.743 | 0.714 | 0.767 | 5.37 | 5.08 | -6.08 | 0.663 | 0.575 | 0.748 | -5.26 | 5.12 | 5.68 | 0.64 | 0.692 | 0.667 | 2.91 | -5.07 | 4.41 | 0.694 | 0.666 | 0.696 | 4.01 | 5.68 | 4.76 | Poor_Mixed | 4392 | 6460 | 1.471 | 0.767 | 6.08 | 0.748 | 5.68 | 0.3909 | 0.7379 | 0.4905 | 0.5865 | 1 | 0.424 | 0.4884 | 0.5719 | 0.5719 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1122 | 463.2 | 329 | 84.3 | 76.1 | 2.7 | 570.4 | 3829.1 | 50.9 | 29.3 | 85.2 | 83.5 | 76.3 | 90.2 | 37.2 | 14.4 | 6982.7 | 7427.1 | 7936.6 | 12071.4 | 13325.1 | 14162.2 | 1.729 | 1.794 | 1.784 | 0.577 | 0.544 | 0.604 | 4.06 | -19.63 | -3.72 | 0.984 | 0.516 | 0.585 | 9.51 | 3.91 | 3.9 | 0.53 | 0.603 | 0.504 | -3.01 | -3.25 | 2.91 | 0.566 | 0.623 | 0.599 | 3.66 | 2.54 | 3.18 | Critical_Bushing_TD_Cap | 6982.7 | 12071.4 | 1.729 | 0.604 | 19.63 | 0.984 | 9.51 | 0.7518 | 0.8054 | 0.696 | 0.9092 | 1 | 0.5852 | 0.6413 | 0.757 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
1123 | 1566.3 | 931 | 135.3 | 177.9 | 32.1 | 1232.6 | 7817.2 | 35.2 | 45.1 | 104.1 | 101.8 | 93.8 | 113.1 | 45.4 | 31.7 | 2251.1 | 2283 | 2279.3 | 2471.2 | 2397.2 | 2570 | 1.098 | 1.05 | 1.128 | 0.925 | 0.986 | 0.961 | 8.52 | 9.33 | 8.84 | 0.703 | 0.753 | 0.725 | 4.74 | -7.59 | -6.68 | 0.882 | 0.718 | 0.733 | 5.78 | 7.48 | 7.19 | 0.863 | 0.76 | 0.874 | 6.22 | 6.02 | 7.43 | Very Poor_Mixed | 2251.1 | 2397.2 | 1.05 | 0.986 | 9.33 | 0.882 | 7.59 | 0.1143 | 0.6289 | 0.1816 | 0.3329 | 1 | 0.0832 | 0.3047 | 0.3653 | 0.3653 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1124 | 1644.5 | 952.2 | 144.6 | 183.8 | 34.3 | 1255.9 | 8175.6 | 34.8 | 44.7 | 106.8 | 104.6 | 92.6 | 112.7 | 44 | 30.1 | 3456.2 | 1885.7 | 920.6 | 4282.2 | 2009.3 | 1200 | 1.239 | 1.066 | 1.303 | 0.923 | 0.972 | 0.947 | 8.39 | 8.99 | -8.73 | 0.913 | 0.89 | 0.88 | -6.42 | -7.45 | 9.14 | 0.843 | 0.97 | 0.843 | 6.39 | 7.34 | -7.78 | 0.906 | 0.871 | 0.908 | 6.74 | 6.69 | 5.83 | Very Poor_Mixed | 920.6 | 1200 | 1.066 | 0.972 | 8.99 | 0.97 | 9.14 | 0.0773 | 0.6328 | 0.1698 | 0.3938 | 1 | 0.0996 | 0.1804 | 0.3383 | 0.3383 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1125 | 1257.5 | 769.8 | 126 | 155.4 | 31 | 1044.7 | 7203.3 | 41 | 43.2 | 100.7 | 99 | 88 | 105.7 | 42.6 | 33.4 | 3836.1 | 1790.8 | 2247.1 | 4976.4 | 2351.1 | 2889.6 | 1.297 | 1.313 | 1.286 | 0.868 | 0.853 | 0.863 | -8.34 | 8.12 | 7.74 | 0.704 | 0.736 | 0.712 | 6.54 | -6.2 | 6.98 | 0.716 | 0.855 | 0.749 | 5.89 | 6.9 | 13.01 | 0.797 | 0.892 | 0.765 | -5.5 | 4.89 | 5.93 | Critical_Mixed | 1790.8 | 2351.1 | 1.286 | 0.868 | 8.34 | 0.892 | 13.01 | 0.2146 | 0.6474 | 0.3077 | 0.267 | 1 | 0.1922 | 0.3154 | 0.4191 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
1126 | 505.9 | 362 | 85.7 | 91.6 | 14.2 | 688.9 | 4320.5 | 49.8 | 29 | 87.5 | 90.5 | 81 | 96.4 | 39.1 | 22.6 | 7392.2 | 5169.2 | 6197.8 | 12875.7 | 8015.5 | 9343.3 | 1.742 | 1.551 | 1.508 | 0.691 | 0.745 | 0.671 | -4.64 | 5.97 | 4.53 | 0.612 | 0.672 | 0.704 | -4.33 | -4.95 | 3.77 | 0.63 | 0.636 | 0.583 | 3.64 | 3.3 | 3.9 | 0.656 | 0.58 | 0.644 | 4.34 | 4.51 | -4.12 | Fair_Mixed | 5169.2 | 8015.5 | 1.508 | 0.745 | 5.97 | 0.704 | 4.95 | 0.5787 | 0.8095 | 0.5561 | 0.6619 | 1 | 0.4858 | 0.5601 | 0.6594 | 0.6594 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1127 | 446.9 | 310.1 | 83.9 | 74.7 | 8 | 606.2 | 3295.7 | 56.4 | 27.3 | 83 | 85.2 | 76.3 | 88.7 | 37.1 | 16.4 | 7148.1 | 8208.7 | 7602.1 | 12317.7 | 15189.4 | 13145.6 | 1.723 | 1.85 | 1.729 | 0.614 | 0.643 | 0.651 | 3.67 | 5.01 | -4.8 | 0.569 | 0.58 | 0.581 | -2.41 | 3.7 | 2.49 | 0.592 | 0.607 | 0.571 | 2.85 | -3.92 | 3.76 | 0.624 | 0.622 | 0.617 | -3.74 | 4.3 | 2.02 | Fair_Mixed | 7148.1 | 12317.7 | 1.723 | 0.651 | 5.01 | 0.624 | 4.3 | 0.6821 | 0.8337 | 0.7079 | 0.855 | 1 | 0.5834 | 0.6546 | 0.7436 | 0.7436 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1128 | 343.1 | 252.7 | 81.2 | 82.3 | 2.7 | 466 | 3687.5 | 57.5 | 22.6 | 86.5 | 88.3 | 78.8 | 93.3 | 38.2 | 10.2 | 9743.6 | 9458.7 | 10000 | 18857.2 | 18917.4 | 7435.3 | 1.935 | 2 | 0.744 | 0.674 | 0.629 | 0.754 | -4.67 | 4.2 | 6.22 | 0.638 | 0.603 | 0.983 | 4.78 | 4 | 9.6 | 0.591 | 0.593 | 0.628 | 2 | -3.44 | -3.18 | 0.544 | 0.553 | 0.604 | 2.72 | 3.18 | 2.67 | Critical_Bushing_TD_Cap | 9458.7 | 7435.3 | 0.744 | 0.754 | 6.22 | 0.983 | 9.6 | 0.7833 | 0.915 | 0.6134 | 0.9981 | 0.8125 | 0.5047 | 0.5892 | 0.7236 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_TV
1129 | 546.6 | 334.5 | 91.8 | 91.9 | 12.4 | 605.4 | 3945.5 | 53 | 28.3 | 82.6 | 82.6 | 77.6 | 90.3 | 38 | 17.8 | 6520.4 | 7226 | 8256.6 | 10913.2 | 11941 | 14256.7 | 1.674 | 1.653 | 1.727 | 0.624 | 0.593 | 0.549 | 4.4 | 3.3 | 3.48 | 0.6 | 0.648 | 0.626 | -3.22 | 4.65 | -4.49 | 0.649 | 0.622 | 0.631 | 3.75 | 4.36 | 3.56 | 0.61 | 0.675 | 0.63 | 4.85 | 4.67 | -3.17 | Fair_Mixed | 6520.4 | 10913.2 | 1.653 | 0.624 | 4.4 | 0.675 | 4.85 | 0.602 | 0.8193 | 0.7083 | 0.8143 | 1 | 0.6877 | 0.5627 | 0.7179 | 0.7179 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1130 | 374.9 | 227.2 | 77.1 | 146.3 | 2.2 | 476.7 | 3679.7 | 57.2 | 53 | 105.3 | 107.1 | 94.7 | 117.3 | 44.4 | 13.6 | 8917.9 | 8780 | 9830.9 | 16456.6 | 16245.2 | 19257 | 1.845 | 1.85 | 1.959 | 0.588 | 0.611 | 0.627 | 2.96 | 3.31 | 3.48 | 0.517 | 0.51 | 0.566 | 2.95 | -3.38 | -3.25 | 0.5 | 0.5 | 0.514 | 3.37 | 2.49 | 2.26 | 0.5 | 0.582 | 0.546 | 2.85 | -2.74 | 2 | Critical_Thermal | 8780 | 16245.2 | 1.845 | 0.627 | 3.48 | 0.582 | 3.38 | 0.7321 | 0.5833 | 0.1266 | 0.9294 | 1 | 0.6905 | 0.8466 | 0.7212 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1131 | 1766 | 982.4 | 148.3 | 197 | 33 | 1354 | 8587.5 | 50.1 | 28.7 | 81.5 | 82.7 | 73.8 | 89.8 | 37.1 | 15.2 | 8584.8 | 7770.6 | 9413.9 | 15601 | 14586.9 | 18413.2 | 1.817 | 1.877 | 1.956 | 0.605 | 0.647 | 0.632 | 4.11 | -23.93 | 3.85 | 0.555 | 0.63 | 0.574 | -2.98 | -3.39 | 3.06 | 0.557 | 0.62 | 0.538 | -2.17 | 2.68 | -3.54 | 0.53 | 0.563 | 0.557 | -2.93 | 2 | -2.2 | Critical_DGA | 7770.6 | 14586.9 | 1.817 | 0.647 | 23.93 | 0.63 | 3.54 | 0.0412 | 0.8136 | 0.7522 | 0.8882 | 1 | 0.5148 | 0.7259 | 0.5903 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1132 | 246.8 | 226.9 | 72.4 | 58.4 | 1 | 381.7 | 2666.7 | 48.5 | 31.9 | 80.7 | 82 | 75.9 | 86.1 | 36.1 | 15.5 | 7712.2 | 8389.1 | 8876.4 | 13722.2 | 15413.5 | 16556.2 | 1.779 | 1.837 | 1.865 | 0.607 | 0.619 | 0.577 | 3.75 | -2.69 | 2.86 | 0.5 | 0.512 | 0.54 | 2 | 2 | 2.57 | 0.52 | 0.5 | 0.524 | 2.41 | 2 | 2.43 | 0.508 | 0.509 | 0.5 | -2.28 | 2 | 2 | Poor_Oil | 7712.2 | 13722.2 | 1.779 | 0.619 | 3.75 | 0.54 | 2.57 | 0.938 | 0.7716 | 0.7718 | 0.88 | 1 | 0.7106 | 0.9136 | 0.8722 | 0.8722 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1133 | 1081.7 | 530.9 | 102 | 118.7 | 16.4 | 852.3 | 5949.8 | 45.7 | 34.9 | 92.8 | 92.5 | 83.4 | 97 | 40.3 | 26 | 5105.2 | 4871.1 | 4738.9 | 7164.4 | 6899.2 | 7367 | 1.403 | 1.416 | 1.555 | 0.729 | 0.719 | 0.72 | -6.98 | -5.41 | 5.44 | 0.735 | 0.681 | 0.733 | 4.22 | 5.7 | -5.03 | 0.612 | 0.628 | 0.712 | 4.46 | 5.03 | 5.66 | 0.688 | 0.727 | 0.716 | 4.7 | 5.24 | 5.56 | Poor_Mixed | 4738.9 | 6899.2 | 1.403 | 0.729 | 6.98 | 0.735 | 5.7 | 0.4219 | 0.7356 | 0.4821 | 0.5442 | 1 | 0.4164 | 0.4498 | 0.5684 | 0.5684 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1134 | 232.2 | 238.3 | 77.5 | 164.6 | 51.2 | 427 | 3726.3 | 53 | 25.8 | 105.9 | 103 | 94.7 | 115.6 | 44.7 | 12.4 | 8295.2 | 6378 | 7679.9 | 14197.1 | 10357.1 | 13104.6 | 1.711 | 1.624 | 1.706 | 0.61 | 0.59 | 0.606 | 4.27 | -3.84 | 3.79 | 0.577 | 0.632 | 0.631 | 3.51 | 4.44 | 3.88 | 0.596 | 0.63 | 0.579 | 4.26 | 4.51 | -4.43 | 0.604 | 0.662 | 0.693 | 3.88 | 3.99 | 4.56 | Critical_Thermal | 6378 | 10357.1 | 1.624 | 0.61 | 4.27 | 0.693 | 4.56 | 0.4875 | 0.8568 | 0.1524 | 0.9575 | 1 | 0.653 | 0.5751 | 0.6428 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1135 | 1555.3 | 813.2 | 129.6 | 169.4 | 33 | 1183.3 | 7905.9 | 34.9 | 44.6 | 99.4 | 101 | 93.4 | 110.1 | 43 | 31 | 1803.2 | 2739.6 | 1962.9 | 1974.3 | 3229.6 | 2420.9 | 1.095 | 1.179 | 1.233 | 0.884 | 0.906 | 0.948 | 8.63 | 9.03 | 9.47 | 0.756 | 0.707 | 0.845 | 4.38 | 7.75 | 4.93 | 0.881 | 0.883 | 0.861 | -5.79 | 6.44 | -5.4 | 0.901 | 0.854 | 0.8 | 8.08 | -5.47 | 7.6 | Very Poor_Mixed | 1803.2 | 1974.3 | 1.095 | 0.948 | 9.47 | 0.901 | 8.08 | 0.1398 | 0.6338 | 0.2477 | 0.3597 | 1 | 0.1062 | 0.2657 | 0.3765 | 0.3765 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1136 | 626.5 | 336.5 | 94.5 | 92.1 | 13 | 675.6 | 4369.9 | 60 | 21.3 | 76.1 | 78.2 | 70 | 82 | 35 | 14 | 9291.7 | 9900.8 | 9446.6 | 17670.5 | 19801.5 | 18804.6 | 1.902 | 2 | 1.991 | 0.522 | 0.5 | 0.5 | 2 | 2.11 | 2 | 0.536 | 0.507 | 0.5 | -2.22 | 2 | 2.54 | 0.5 | 0.518 | 0.531 | -3.18 | -2.17 | 2 | 0.563 | 0.5 | 0.522 | -2 | 2 | 2.31 | Fair_DGA | 9291.7 | 17670.5 | 1.902 | 0.522 | 2.11 | 0.563 | 3.18 | 0.575 | 0.9458 | 0.9298 | 0.9194 | 1 | 0.9685 | 0.8891 | 0.8518 | 0.8518 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1137 | 289.9 | 179.1 | 67.8 | 58.1 | 1 | 423.8 | 2931.3 | 58.8 | 20.7 | 79.5 | 79.2 | 71.6 | 85.2 | 36.3 | 10.3 | 8473.1 | 9852.6 | 10000 | 16379.6 | 19492 | 20000 | 1.933 | 1.978 | 2 | 0.5 | 0.5 | 0.514 | 2 | 2 | -2 | 0.552 | 0.534 | 0.711 | 2.52 | 2.64 | -4.11 | 0.505 | 0.5 | 0.544 | 3.17 | 2.24 | 2.46 | 0.58 | 0.535 | 0.537 | 2 | 2.68 | 2 | Fair_Bushing_TD_Cap | 8473.1 | 16379.6 | 1.933 | 0.514 | 2 | 0.711 | 4.11 | 0.9331 | 0.9638 | 0.8449 | 0.9968 | 1 | 0.9791 | 0.783 | 0.9213 | 0.9213 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_HV_B_TanDelta_pct
1138 | 1392.5 | 839.8 | 127.1 | 167.3 | 29.7 | 1183.1 | 7354.1 | 34.3 | 47.5 | 104.4 | 103.1 | 88.5 | 110.2 | 44.4 | 29.7 | 3027 | 2920.7 | 1702.8 | 3781.6 | 3821.2 | 1991.3 | 1.249 | 1.308 | 1.169 | 0.865 | 0.895 | 0.894 | 7.93 | -8.66 | -8.33 | 0.917 | 0.773 | 0.803 | -6.55 | -7.07 | 7.61 | 0.813 | 0.798 | 0.881 | 6.11 | 7.62 | 8.08 | 0.821 | 0.849 | 0.924 | 9.01 | 7.29 | 6.22 | Very Poor_Mixed | 1702.8 | 1991.3 | 1.169 | 0.895 | 8.66 | 0.924 | 9.01 | 0.1743 | 0.6062 | 0.2247 | 0.4089 | 1 | 0.1631 | 0.2186 | 0.3814 | 0.3814 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1139 | 100 | 121.9 | 68.1 | 50.4 | 3.4 | 359.1 | 2642.1 | 58.3 | 21.7 | 77.7 | 76.8 | 72.3 | 83.5 | 35.1 | 14.1 | 8306.3 | 9673.9 | 9254.9 | 15702.4 | 19346.7 | 17272.4 | 1.89 | 2 | 1.866 | 0.508 | 0.506 | 0.507 | -2.81 | 2.34 | 3.11 | 0.5 | 0.5 | 0.533 | 2.44 | 2.54 | 2.36 | 0.504 | 0.6 | 0.5 | 2.25 | 2.36 | -2.74 | 0.529 | 0.54 | 0.556 | -2 | 2.21 | 2.47 | Good_Mixed | 8306.3 | 15702.4 | 1.866 | 0.508 | 3.11 | 0.6 | 2.74 | 0.8959 | 0.9355 | 0.893 | 0.9169 | 1 | 0.8972 | 0.861 | 0.912 | 0.912 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1140 | 825.9 | 385 | 98.4 | 102 | 16.8 | 705.5 | 4703.9 | 50.2 | 31.3 | 85.4 | 84.7 | 76.4 | 93.5 | 39.2 | 20.6 | 6984 | 6871.3 | 6258.9 | 11745.5 | 11831.3 | 9793.9 | 1.682 | 1.722 | 1.565 | 0.67 | 0.65 | 0.706 | 5.15 | 4.91 | 4.65 | 0.638 | 0.692 | 0.592 | 3.82 | -3.81 | 3.56 | 0.672 | 0.619 | 0.574 | 4.57 | 3.26 | 4.86 | 0.64 | 0.628 | 0.642 | 3.11 | -4.16 | 3.46 | Poor_Mixed | 6258.9 | 9793.9 | 1.565 | 0.706 | 5.15 | 0.692 | 4.86 | 0.5065 | 0.7791 | 0.6566 | 0.7276 | 1 | 0.5188 | 0.5729 | 0.6579 | 0.6579 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1141 | 584.7 | 357.1 | 87.8 | 96.2 | 12.1 | 622.6 | 4507.4 | 52.7 | 27.7 | 86.1 | 83.3 | 78.1 | 88.2 | 38.5 | 18.9 | 7778.9 | 7695.7 | 7250.3 | 13736.9 | 13580.6 | 12049.7 | 1.766 | 1.765 | 1.662 | 0.578 | 0.655 | 0.613 | 3 | -5.06 | 3.69 | 0.649 | 0.606 | 0.663 | 4.03 | 4.74 | 4.4 | 0.617 | 0.577 | 0.609 | -2.53 | 3.97 | 3.85 | 0.655 | 0.622 | 0.592 | 4.45 | 4.35 | 3.51 | Fair_Mixed | 7250.3 | 12049.7 | 1.662 | 0.655 | 5.06 | 0.663 | 4.74 | 0.5892 | 0.8279 | 0.6808 | 0.7811 | 1 | 0.6437 | 0.584 | 0.709 | 0.709 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1142 | 173.3 | 120 | 65 | 50 | 3.4 | 354.3 | 2807.3 | 59.3 | 20 | 78.8 | 77.9 | 71.3 | 80.7 | 35 | 11.4 | 10000 | 9436.7 | 10000 | 19899.5 | 18063.4 | 19394.9 | 1.99 | 1.914 | 1.939 | 0.539 | 0.523 | 0.52 | 2.6 | 2.39 | 2 | 0.552 | 0.537 | 0.546 | 2 | 2.41 | 2.16 | 0.5 | 0.5 | 0.548 | 2.42 | 2.1 | 2.2 | 0.5 | 0.532 | 0.5 | 2.57 | 2.29 | 2.32 | Good_Mixed | 9436.7 | 18063.4 | 1.914 | 0.539 | 2.6 | 0.552 | 2.57 | 0.8905 | 1 | 0.8944 | 0.9783 | 1 | 0.8783 | 0.8801 | 0.9224 | 0.9224 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1143 | 1528.1 | 878.5 | 130.6 | 183.3 | 32 | 1173.8 | 7326.8 | 37.5 | 42.6 | 101 | 102.3 | 89.8 | 111.1 | 42.3 | 33.8 | 3279.1 | 3485 | 2128.6 | 3156 | 4319.5 | 2313.9 | 0.962 | 1.239 | 1.087 | 0.829 | 0.865 | 0.823 | 7.01 | 8.03 | 6.82 | 0.846 | 0.76 | 0.715 | -7.11 | -6.75 | 6.73 | 0.755 | 0.797 | 0.795 | 4.87 | 8.26 | -5.03 | 0.896 | 0.801 | 0.825 | 7.6 | 6.21 | 5 | Critical_Mixed | 2128.6 | 2313.9 | 0.962 | 0.865 | 8.03 | 0.896 | 8.26 | 0.1351 | 0.6534 | 0.2514 | 0.2513 | 0.8187 | 0.2496 | 0.2896 | 0.3679 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1144 | 284.2 | 179.5 | 75.8 | 56.4 | 1.9 | 430.3 | 2500 | 32.3 | 49.2 | 79.2 | 78.9 | 70.2 | 80.8 | 35.7 | 15.7 | 6616.1 | 5193.2 | 6387.1 | 10401.1 | 7702.5 | 4558.6 | 1.572 | 1.483 | 0.714 | 0.663 | 0.689 | 0.642 | 4.76 | 5.13 | 4.23 | 0.507 | 0.505 | 0.532 | 3.1 | 3.03 | 3.21 | 0.523 | 0.53 | 0.524 | 2.48 | -2.42 | 3.23 | 0.586 | 0.55 | 0.551 | 3.32 | 2.74 | -2.91 | Critical_Oil | 5193.2 | 4558.6 | 0.714 | 0.689 | 5.13 | 0.586 | 3.32 | 0.8701 | 0.5906 | 0.8907 | 0.8746 | 0.8125 | 0.5407 | 0.7967 | 0.7703 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
1145 | 140.4 | 154.1 | 68.7 | 50 | 1 | 363.4 | 3002.7 | 60 | 20 | 77.1 | 76 | 71.4 | 83.1 | 35.5 | 10.3 | 9413.7 | 10000 | 8585.7 | 18636.6 | 19964.7 | 16000.5 | 1.98 | 1.996 | 1.864 | 0.512 | 0.51 | 0.569 | 2 | 2.27 | 3.12 | 0.527 | 0.546 | 0.523 | 2 | 2.09 | -2.16 | 0.5 | 0.526 | 0.5 | -2.06 | 2.62 | 2.63 | 0.52 | 0.526 | 0.526 | 2.01 | 2 | 2.28 | Good_Mixed | 8585.7 | 16000.5 | 1.864 | 0.569 | 3.12 | 0.546 | 2.63 | 0.9816 | 1 | 0.9179 | 0.9968 | 1 | 0.8717 | 0.8758 | 0.9467 | 0.9467 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1146 | 448.3 | 249.6 | 79.9 | 71.2 | 6.5 | 481 | 3821.8 | 54 | 26.6 | 81.1 | 81.7 | 75.3 | 87.8 | 36.6 | 18.2 | 7411.5 | 7910.6 | 7622 | 13581 | 13948.1 | 13479.1 | 1.832 | 1.763 | 1.768 | 0.595 | 0.611 | 0.627 | 3.99 | 3.79 | -3.76 | 0.57 | 0.545 | 0.584 | 3.42 | 4.2 | 3.77 | 0.56 | 0.558 | 0.608 | 3.44 | -3.15 | -2.87 | 0.526 | 0.606 | 0.584 | -3.42 | 2.31 | 3.6 | Fair_Mixed | 7411.5 | 13479.1 | 1.763 | 0.627 | 3.99 | 0.608 | 4.2 | 0.7273 | 0.8443 | 0.7644 | 0.8024 | 1 | 0.6497 | 0.6933 | 0.7754 | 0.7754 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1147 | 132.1 | 198.7 | 65 | 59 | 1 | 358.1 | 3254.5 | 54.3 | 28.5 | 75 | 76.1 | 70.2 | 80.7 | 35.1 | 12.4 | 8924 | 8694.6 | 8009.7 | 16375 | 16645.2 | 15090.8 | 1.835 | 1.914 | 1.884 | 0.5 | 0.591 | 0.534 | 2 | 3.2 | -2.72 | 0.52 | 0.527 | 0.521 | -2.41 | 2.23 | 2.49 | 0.5 | 0.5 | 0.5 | -2.35 | -2 | -2.16 | 0.511 | 0.512 | 0.524 | 2.39 | 2.38 | 2.01 | Fair_Oil | 8009.7 | 15090.8 | 1.835 | 0.591 | 3.2 | 0.527 | 2.49 | 0.9593 | 0.8164 | 0.974 | 0.9575 | 1 | 0.8493 | 0.9045 | 0.9248 | 0.9248 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1148 | 1475.3 | 895.5 | 144.8 | 191.7 | 30 | 1322.4 | 7894.3 | 35.3 | 45.3 | 102.7 | 103.1 | 89.9 | 111.7 | 43.3 | 31.2 | 2178.4 | 1352.4 | 2909.6 | 2478.3 | 1457.7 | 3521 | 1.138 | 1.078 | 1.21 | 0.89 | 0.916 | 0.846 | 8.61 | -8.64 | 7.94 | 0.879 | 0.837 | 0.73 | 6.05 | 6.79 | 5.7 | 0.728 | 0.821 | 0.869 | -6.55 | 6 | -9.07 | 0.756 | 0.752 | 0.821 | 5.62 | 5.67 | 5.64 | Very Poor_Mixed | 1352.4 | 1457.7 | 1.078 | 0.916 | 8.64 | 0.879 | 9.07 | 0.1045 | 0.627 | 0.2265 | 0.3521 | 1 | 0.1592 | 0.2912 | 0.3763 | 0.3763 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1149 | 1339.8 | 780.6 | 126.2 | 154 | 32.1 | 1141.6 | 7402.8 | 39.1 | 40.6 | 98.9 | 99.8 | 87.7 | 108.1 | 42.8 | 32.2 | 2248.7 | 2932 | 1996 | 2691.3 | 3750.9 | 2330.7 | 1.197 | 1.279 | 1.168 | 0.874 | 0.846 | 0.844 | -13.83 | 7.69 | 7.43 | 0.712 | 0.709 | 0.782 | 8.01 | 6.31 | 4.93 | 0.781 | 0.811 | 0.77 | 8.71 | 8.2 | 5.47 | 0.688 | 0.775 | 0.757 | 6.24 | 4.88 | -7.64 | Critical_Mixed | 1996 | 2330.7 | 1.168 | 0.874 | 13.83 | 0.811 | 8.71 | 0.1899 | 0.6737 | 0.3019 | 0.3137 | 1 | 0.1822 | 0.3243 | 0.4181 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1150 | 1628.3 | 877 | 141.4 | 175.4 | 34.3 | 1257.6 | 8284.2 | 55.8 | 24.1 | 80.8 | 82.1 | 76.2 | 89 | 36.9 | 18 | 8326.5 | 9021.9 | 9096 | 15788.6 | 17975.9 | 5038.9 | 1.896 | 1.992 | 0.554 | 0.616 | 0.695 | 0.611 | 3.57 | 5.3 | -4.47 | 0.575 | 0.528 | 0.601 | 2.71 | 3.66 | -3.47 | 0.538 | 0.588 | 0.617 | 3.56 | 3.69 | 2.43 | 0.559 | 0.614 | 0.631 | 4.24 | -2.69 | 3.76 | Critical_DGA | 8326.5 | 5038.9 | 0.554 | 0.695 | 5.3 | 0.631 | 4.24 | 0.0945 | 0.8857 | 0.7495 | 0.8084 | 0.8125 | 0.5831 | 0.6735 | 0.5782 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1151 | 529.6 | 295.1 | 81.9 | 90.8 | 2.5 | 586.3 | 4058.9 | 30.6 | 49.3 | 83.6 | 83.6 | 73.6 | 87 | 36.4 | 13.4 | 5734.1 | 4620.6 | 5214.1 | 8743 | 6598.3 | 7176.5 | 1.525 | 1.428 | 1.376 | 0.643 | 0.701 | 0.604 | 3.57 | -18.03 | -4.41 | 0.5 | 0.5 | 0.521 | -2.41 | 2.22 | 2.27 | 0.532 | 0.5 | 0.525 | 2.7 | 2.74 | -2.43 | 0.575 | 0.509 | 0.5 | 2.54 | 2.1 | 2.56 | Critical_Oil | 4620.6 | 6598.3 | 1.376 | 0.701 | 18.03 | 0.575 | 2.74 | 0.7347 | 0.5897 | 0.748 | 0.9342 | 1 | 0.4934 | 0.8894 | 0.7651 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
1152 | 448.8 | 322.8 | 83.1 | 79.8 | 2.2 | 612 | 3875.3 | 26.7 | 26.4 | 82 | 81.3 | 76 | 86.9 | 37.2 | 15.2 | 1907.4 | 1045.5 | 1506.5 | 2271.7 | 1111.8 | 1732.7 | 1.191 | 1.063 | 1.15 | 0.644 | 0.701 | 0.685 | 4.7 | 5.69 | 6.36 | 0.532 | 0.543 | 0.5 | -2.84 | -3.11 | -2.44 | 0.551 | 0.568 | 0.509 | 2 | 2.89 | 2.13 | 0.599 | 0.517 | 0.538 | 2.74 | 3.22 | 2 | Critical_IR_PI | 1045.5 | 1111.8 | 1.063 | 0.701 | 6.36 | 0.599 | 3.22 | 0.7558 | 0.264 | 0.7565 | 0.8882 | 1 | 0.4797 | 0.8082 | 0.7133 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1153 | 193.7 | 120 | 68.5 | 50 | 1 | 352.3 | 2796.8 | 58.6 | 20.1 | 78.2 | 78.2 | 72.7 | 87.2 | 36.2 | 13.3 | 967.8 | 1700.2 | 1349.6 | 584.6 | 1869.3 | 1481.5 | 0.604 | 1.099 | 1.098 | 0.694 | 0.729 | 0.64 | -5.05 | 5.17 | 4.13 | 0.518 | 0.552 | 0.526 | 2.8 | -2.44 | -2.42 | 0.584 | 0.586 | 0.568 | -2 | 2.72 | 2 | 0.519 | 0.553 | 0.513 | 2.46 | 3.21 | -2.94 | Critical_IR_PI | 967.8 | 584.6 | 0.604 | 0.729 | 5.17 | 0.586 | 3.21 | 0.9845 | 0.9898 | 0.8469 | 0.9367 | 0.7437 | 0.515 | 0.7859 | 0.829 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_HV
1154 | 1582.9 | 863.5 | 137 | 159.5 | 34.3 | 1240.3 | 7460 | 36.3 | 44 | 103.2 | 106.4 | 90.7 | 114 | 43.6 | 31.6 | 2854.6 | 1238.2 | 2123.7 | 3490.6 | 1382.8 | 2488.9 | 1.223 | 1.117 | 1.172 | 0.973 | 0.881 | 0.927 | 8.81 | 8.34 | 8.55 | 0.645 | 0.782 | 0.715 | 8.08 | -5.58 | 7.42 | 0.81 | 0.783 | 0.827 | 7.03 | 6.7 | 5.72 | 0.828 | 0.827 | 0.934 | -7.05 | 8.48 | 7.94 | Very Poor_Mixed | 1238.2 | 1382.8 | 1.117 | 0.973 | 8.81 | 0.934 | 8.48 | 0.1287 | 0.6396 | 0.187 | 0.3368 | 1 | 0.1206 | 0.2725 | 0.3704 | 0.3704 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1155 | 541.6 | 364 | 89.4 | 88.2 | 9.1 | 699.3 | 4065.2 | 53.2 | 27.4 | 83.7 | 83.8 | 77.8 | 91.8 | 37.2 | 16.6 | 7721.2 | 7216.5 | 7165.3 | 13898.7 | 12063.6 | 12908.1 | 1.8 | 1.672 | 1.801 | 0.626 | 0.617 | 0.616 | 4.15 | 4.06 | -3.64 | 0.604 | 0.557 | 0.575 | 3.63 | 4.01 | -4.46 | 0.582 | 0.561 | 0.591 | 3.24 | 2.95 | 3.34 | 0.666 | 0.583 | 0.625 | 3.8 | 3 | 3.13 | Fair_Mixed | 7165.3 | 12063.6 | 1.672 | 0.626 | 4.15 | 0.666 | 4.46 | 0.6188 | 0.8323 | 0.6862 | 0.8493 | 1 | 0.6331 | 0.6466 | 0.7307 | 0.7307 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1156 | 329.8 | 169.1 | 76.3 | 65.2 | 4.5 | 485.3 | 3009.1 | 58.5 | 20 | 77.8 | 77.2 | 73.9 | 81 | 35.4 | 11 | 9810.2 | 9891.4 | 9882.9 | 19099.8 | 19649 | 19627.7 | 1.947 | 1.986 | 1.986 | 0.503 | 0.548 | 0.524 | 2.26 | 2.29 | 2.02 | 0.5 | 0.528 | 0.5 | 2 | -2 | 2 | 0.512 | 0.512 | 0.505 | 2.38 | -2.66 | 2.07 | 0.572 | 0.506 | 0.523 | 2.24 | 2.87 | 2 | Good_Mixed | 9810.2 | 19099.8 | 1.947 | 0.548 | 2.29 | 0.572 | 2.87 | 0.789 | 1 | 0.8856 | 0.9858 | 1 | 0.9005 | 0.8941 | 0.9021 | 0.9021 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1157 | 520 | 283.4 | 84.5 | 74.8 | 9.3 | 621.3 | 4441.8 | 53.3 | 28.4 | 85.8 | 84.8 | 76.2 | 90.3 | 36.3 | 18.7 | 7459.6 | 7063.2 | 8168.9 | 13250.1 | 12183.8 | 14420.8 | 1.776 | 1.725 | 1.765 | 0.614 | 0.588 | 0.672 | 3.48 | -3.15 | 4.2 | 0.528 | 0.598 | 0.548 | -2.34 | 3.67 | 3.3 | 0.604 | 0.589 | 0.614 | 3.74 | 3.02 | 3.38 | 0.581 | 0.544 | 0.559 | 3.28 | 3.41 | 3.7 | Fair_Mixed | 7063.2 | 12183.8 | 1.725 | 0.672 | 4.2 | 0.614 | 3.74 | 0.6546 | 0.8178 | 0.6868 | 0.7872 | 1 | 0.6511 | 0.6904 | 0.7453 | 0.7453 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1158 | 337.7 | 269.4 | 78 | 67.7 | 2.2 | 567.7 | 3539.4 | 54 | 25.9 | 84.3 | 85.9 | 78.3 | 91.4 | 38.6 | 14.5 | 690 | 931.4 | 1040.9 | 728.3 | 950.1 | 1119.9 | 1.056 | 1.02 | 1.076 | 0.69 | 0.663 | 0.702 | 5.14 | 12.66 | 5.01 | 0.5 | 0.519 | 0.544 | 2 | 2 | -2.35 | 0.582 | 0.521 | 0.51 | 2.51 | 2.5 | -2.68 | 0.531 | 0.539 | 0.5 | -2 | 2.71 | 2.51 | Critical_IR_PI | 690 | 728.3 | 1.02 | 0.702 | 12.66 | 0.582 | 2.71 | 0.7996 | 0.8552 | 0.6567 | 0.9067 | 0.85 | 0.4132 | 0.8561 | 0.7615 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_LV_CapChange_pct
1159 | 1454.5 | 823.9 | 137.3 | 169.2 | 32.7 | 1145.2 | 8148.5 | 30.6 | 49.4 | 104.8 | 105.4 | 94.9 | 112.6 | 43.3 | 32.4 | 2337.5 | 2014.4 | 1225.6 | 2686.8 | 2277.3 | 1387 | 1.149 | 1.131 | 1.132 | 0.899 | 0.917 | 0.881 | 8.51 | -8.85 | 8.16 | 0.869 | 0.694 | 0.906 | 5.94 | 6.04 | 7.46 | 0.799 | 0.882 | 0.822 | 7.44 | 7.45 | 6.74 | 0.829 | 0.818 | 0.906 | 8.23 | 6.45 | -5.15 | Very Poor_Mixed | 1225.6 | 1387 | 1.131 | 0.917 | 8.85 | 0.906 | 8.23 | 0.1425 | 0.5888 | 0.169 | 0.3059 | 1 | 0.1427 | 0.2424 | 0.3621 | 0.3621 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1160 | 933.4 | 517.1 | 106.8 | 121.9 | 16.8 | 842.3 | 5271.8 | 48.4 | 32.1 | 89.3 | 91 | 82.8 | 98.5 | 39.4 | 24.8 | 4881.4 | 5738.4 | 3607.4 | 7591.1 | 8777.1 | 5295.4 | 1.555 | 1.53 | 1.468 | 0.775 | 0.712 | 0.828 | 5.5 | 6.37 | 6.27 | 0.73 | 0.693 | 0.73 | 4.94 | -3.98 | 5.51 | 0.646 | 0.779 | 0.625 | 4.04 | 5.12 | 6.12 | 0.795 | 0.67 | 0.697 | 4.62 | 4.53 | 4.89 | Poor_Mixed | 3607.4 | 5295.4 | 1.468 | 0.828 | 6.37 | 0.795 | 6.12 | 0.4341 | 0.7691 | 0.5166 | 0.5865 | 1 | 0.3699 | 0.4412 | 0.573 | 0.573 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1161 | 380 | 274.3 | 86.8 | 69 | 1.2 | 500.1 | 3886.6 | 49 | 30.7 | 82.2 | 85.1 | 76.9 | 88.5 | 36.9 | 16.2 | 7746.5 | 7254.4 | 7648.7 | 14031.6 | 12999.6 | 13554.6 | 1.811 | 1.792 | 1.772 | 0.924 | 0.933 | 0.975 | 9.39 | 9.81 | 8.95 | 2.162 | 0.547 | 0.601 | -2.28 | -3.18 | 3.35 | 0.601 | 0.556 | 0.604 | 2 | 3.5 | 3.51 | 0.571 | 0.613 | 0.585 | 3.56 | 3.44 | -2.95 | Critical_Winding_TD_Cap | 7254.4 | 12999.6 | 1.772 | 0.975 | 9.81 | 2.162 | 3.56 | 0.8347 | 0.7868 | 0.7126 | 0.8607 | 1 | 0.0677 | 0.6315 | 0.7005 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_R_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1162 | 1587.5 | 924.9 | 141.2 | 182.8 | 33.3 | 1365.6 | 7937.3 | 34.1 | 46.9 | 109.3 | 108 | 95.7 | 118.2 | 45.6 | 35 | 2111.9 | 1158.3 | 1089.9 | 2362.1 | 1216.2 | 1200 | 1.118 | 1.05 | 1.101 | 0.919 | 0.948 | 0.981 | 8.28 | 9.77 | 9.27 | 0.858 | 0.727 | 0.709 | 8.48 | 7.39 | -8.26 | 0.791 | 0.958 | 0.733 | 8.69 | -8.44 | 8.68 | 0.889 | 0.894 | 0.812 | 6.07 | 5.52 | 7.66 | Very Poor_Mixed | 1089.9 | 1200 | 1.05 | 0.981 | 9.77 | 0.958 | 8.69 | 0.0834 | 0.6119 | 0.0809 | 0.2038 | 1 | 0.0781 | 0.2302 | 0.3249 | 0.3249 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1163 | 818.8 | 501.8 | 105.2 | 135.6 | 19.6 | 735.6 | 5048.1 | 47.2 | 33.8 | 89.4 | 94.3 | 81.4 | 97 | 39.3 | 24.4 | 6794.6 | 5163.1 | 5219.8 | 10586.8 | 7562.4 | 8049.9 | 1.558 | 1.465 | 1.542 | 0.761 | 0.737 | 0.708 | -6.07 | -5.64 | 5.16 | 0.676 | 0.765 | 0.614 | -5.4 | -5.76 | 5.77 | 0.731 | 0.687 | 0.663 | 5.22 | 5.67 | 6.15 | 0.683 | 0.641 | 0.741 | 5.85 | -5.49 | 4.34 | Poor_Mixed | 5163.1 | 7562.4 | 1.465 | 0.761 | 6.07 | 0.765 | 6.15 | 0.4316 | 0.7485 | 0.512 | 0.6005 | 1 | 0.4229 | 0.438 | 0.577 | 0.577 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1164 | 1494.1 | 815.6 | 130.5 | 170.5 | 25.1 | 1095.4 | 7109.9 | 38 | 41.7 | 102.8 | 102.9 | 91.7 | 110.4 | 43.4 | 34.4 | 1714.9 | 3226.7 | 156.3 | 1999.7 | 3964.5 | 214.2 | 1.166 | 1.229 | 1.37 | 0.827 | 0.856 | 0.88 | 6.89 | 8.19 | -7.75 | 0.818 | 0.849 | 0.695 | 5.14 | -6.67 | 6.09 | 0.697 | 0.802 | 0.784 | -5.15 | -7.35 | 4.85 | 0.851 | 0.827 | 0.823 | 5.21 | 6.25 | 5.53 | Critical_Mixed | 156.3 | 214.2 | 1.166 | 0.88 | 8.19 | 0.851 | 7.35 | 0.1995 | 0.6624 | 0.2225 | 0.2276 | 0.85 | 0.2213 | 0.3149 | 0.3867 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1165 | 236.6 | 160.4 | 67.6 | 64.4 | 2.4 | 431.8 | 3061 | 57.1 | 26 | 77.6 | 79.5 | 74.5 | 83.2 | 36.1 | 10 | 5479.5 | 6227.7 | 5446.5 | 8292.9 | 9037.3 | 8470.7 | 1.513 | 1.451 | 1.555 | 0.618 | 0.61 | 0.65 | -3.56 | 4.08 | 4.2 | 0.5 | 0.533 | 0.516 | 2.04 | 2 | -2.44 | 0.528 | 0.508 | 0.5 | 2.39 | 2 | -2 | 0.527 | 0.5 | 0.5 | 2 | 2 | 2.77 | Poor_IR_PI | 5446.5 | 8292.9 | 1.451 | 0.65 | 4.2 | 0.533 | 2.77 | 0.8528 | 0.8536 | 0.8466 | 1 | 1 | 0.6267 | 0.9194 | 0.8635 | 0.8635 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1166 | 1441 | 872.8 | 137.4 | 165.9 | 28.9 | 1144.6 | 7921.7 | 36.1 | 46.1 | 105.6 | 102.8 | 91.1 | 112.5 | 44.5 | 31.8 | 2180.4 | 2820.7 | 1843.4 | 2430.5 | 3536.8 | 2110.1 | 1.115 | 1.254 | 1.145 | 0.976 | 0.881 | 0.967 | 9.01 | 8.72 | 8.83 | 0.926 | 0.84 | 0.824 | 6.28 | -7.82 | 7.94 | 0.886 | 0.881 | 0.896 | 9.22 | 7.62 | -8.23 | 0.836 | 0.966 | 0.915 | -6.93 | 7.5 | 8.8 | Very Poor_Mixed | 1843.4 | 2110.1 | 1.115 | 0.976 | 9.01 | 0.966 | 9.22 | 0.1612 | 0.6194 | 0.1924 | 0.3291 | 1 | 0.0965 | 0.1622 | 0.353 | 0.353 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1167 | 848.5 | 536.7 | 99.2 | 108 | 17 | 721.7 | 5629.1 | 45.6 | 34.1 | 92.8 | 91.3 | 81.2 | 101.2 | 40 | 22.9 | 5746.6 | 6132.7 | 5275.4 | 8798.7 | 9459.3 | 7909.6 | 1.531 | 1.542 | 1.499 | 0.756 | 0.761 | 0.702 | 5.72 | 5.42 | -5.95 | 0.623 | 0.644 | 0.69 | 5.21 | 3.47 | -4.28 | 0.702 | 0.647 | 0.686 | 4.8 | 4.89 | 4.11 | 0.683 | 0.635 | 0.642 | -4.98 | 5.3 | 4.82 | Poor_Mixed | 5275.4 | 7909.6 | 1.499 | 0.761 | 5.95 | 0.702 | 5.3 | 0.4681 | 0.7449 | 0.4848 | 0.6518 | 1 | 0.4151 | 0.502 | 0.596 | 0.596 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1168 | 177 | 194.4 | 72 | 63 | 1.9 | 388.3 | 3185.7 | 56.7 | 22 | 76.1 | 77.1 | 71.7 | 81.5 | 36.7 | 11.6 | 10000 | 10000 | 8619.1 | 19760.8 | 20000 | 16378.2 | 1.976 | 2 | 1.9 | 0.5 | 0.532 | 0.531 | -2.06 | 2 | 2.84 | 0.556 | 0.5 | 0.512 | -2.16 | 2.96 | -3.02 | 0.501 | 0.543 | 0.56 | 2 | 2.24 | 2.87 | 0.598 | 0.517 | 0.541 | -4.01 | -3.35 | 2.42 | Fair_Bushing_TD_Cap | 8619.1 | 16378.2 | 1.9 | 0.532 | 2.84 | 0.598 | 4.01 | 0.8759 | 0.9283 | 0.9161 | 0.9744 | 1 | 0.9068 | 0.8123 | 0.9039 | 0.9039 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1169 | 153.3 | 196.8 | 78 | 52.3 | 1.2 | 411.6 | 2710.5 | 54.4 | 22.8 | 76.7 | 77.6 | 72.4 | 84.8 | 36.5 | 13.4 | 9185.1 | 9853.2 | 9265.5 | 17709.2 | 19244.8 | 17539.2 | 1.928 | 1.953 | 1.893 | 0.772 | 0.743 | 0.673 | 6.46 | 5.58 | 6.2 | 0.506 | 0.5 | 0.532 | -2.66 | 2.8 | 2 | 0.578 | 0.5 | 0.517 | 3.01 | 2.77 | 2.94 | 0.553 | 0.554 | 0.549 | 2.85 | 2.68 | 2.84 | Poor_Winding_TD_Cap | 9185.1 | 17539.2 | 1.893 | 0.772 | 6.46 | 0.578 | 3.01 | 0.922 | 0.9108 | 0.8817 | 0.9342 | 1 | 0.404 | 0.8257 | 0.8399 | 0.8399 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
1170 | 179.2 | 169.6 | 69.1 | 56.4 | 1.4 | 434.4 | 2500 | 59.6 | 22.8 | 76.5 | 77.5 | 70.9 | 81 | 35.2 | 13.9 | 9602.2 | 8742.4 | 9873.5 | 18816.1 | 16965.1 | 19746.7 | 1.96 | 1.941 | 2 | 0.644 | 0.712 | 0.647 | 4.56 | 5 | -4.35 | 0.5 | 0.529 | 0.526 | -3.02 | -4.09 | 2.27 | 0.531 | 0.599 | 0.552 | -2.67 | 2.36 | -2.34 | 0.587 | 0.5 | 0.613 | 2.43 | -2.98 | 2 | Fair_Winding_TD_Cap | 8742.4 | 16965.1 | 1.941 | 0.712 | 5 | 0.613 | 4.09 | 0.9043 | 0.9108 | 0.9242 | 0.9219 | 1 | 0.5424 | 0.7937 | 0.8527 | 0.8527 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
1171 | 335 | 271.8 | 78.2 | 94.5 | 1 | 468.4 | 3512.1 | 58.9 | 65.2 | 80.4 | 78.8 | 74.2 | 90 | 36.2 | 19.9 | 8172.1 | 9658.8 | 10000 | 14277.5 | 18671.7 | 18904.9 | 1.747 | 1.933 | 1.89 | 0.575 | 0.583 | 0.503 | 3.35 | -3.55 | 2 | 0.539 | 0.933 | 0.598 | -2.94 | 8.67 | 3.65 | 0.542 | 0.559 | 0.576 | 2.73 | 2.15 | 2.74 | 0.55 | 0.649 | 0.569 | 3.16 | 4.02 | 2.96 | Critical_Bushing_TD_Cap | 8172.1 | 14277.5 | 1.747 | 0.583 | 3.55 | 0.933 | 8.67 | 0.854 | 0.5833 | 0.7949 | 0.7499 | 1 | 0.8012 | 0.6379 | 0.7875 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1172 | 1188.6 | 769.3 | 118.4 | 149.4 | 22.1 | 987.8 | 6142.6 | 57.1 | 24.3 | 80.4 | 79 | 72.6 | 86.6 | 36.1 | 12.1 | 10000 | 9029.7 | 8866.4 | 19528.7 | 16814.5 | 16177.6 | 1.953 | 1.862 | 1.825 | 0.523 | 0.512 | 0.5 | 2.03 | 2.61 | 2.66 | 0.5 | 0.508 | 0.52 | 2.21 | -2.29 | -2.02 | 0.577 | 0.547 | 0.508 | 3.12 | 2.12 | 2 | 0.562 | 0.534 | 0.597 | 2 | 2.69 | 3.09 | Poor_DGA | 8866.4 | 16177.6 | 1.825 | 0.523 | 2.66 | 0.597 | 3.12 | 0.2943 | 0.8821 | 0.8237 | 0.964 | 1 | 0.9155 | 0.8238 | 0.7465 | 0.7465 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1173 | 1571.2 | 824.8 | 139.8 | 184 | 33.4 | 1255 | 7473.5 | 32.1 | 45.7 | 103.2 | 100.6 | 92.9 | 112.5 | 44.1 | 33.2 | 1727.1 | 2063.9 | 1156 | 2006.7 | 2469.1 | 1213.8 | 1.162 | 1.196 | 1.05 | 0.91 | 0.892 | 0.918 | -8.64 | 8.95 | 9.38 | 0.87 | 0.765 | 0.844 | -6.02 | 8.96 | -6.82 | 0.809 | 0.804 | 0.919 | 6.79 | 6.32 | 7.18 | 0.736 | 0.709 | 0.809 | 7.44 | 7.36 | 8.88 | Very Poor_Mixed | 1156 | 1213.8 | 1.05 | 0.918 | 9.38 | 0.919 | 8.96 | 0.113 | 0.6232 | 0.2111 | 0.2748 | 1 | 0.1129 | 0.2517 | 0.359 | 0.359 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1174 | 100 | 120 | 65 | 65.4 | 1 | 350 | 2726.4 | 58.3 | 21.3 | 76.9 | 75 | 71 | 81.6 | 35.5 | 10 | 9859.4 | 8924.1 | 9164.7 | 18916.5 | 17218.6 | 17892.6 | 1.919 | 1.929 | 1.952 | 0.519 | 0.52 | 0.527 | 2.36 | 2.18 | 2.24 | 0.524 | 0.52 | 0.514 | 2 | 3.4 | -2.61 | 0.511 | 0.514 | 0.531 | 2.67 | 2 | 2.39 | 0.514 | 0.5 | 0.5 | -2.82 | 2.57 | 2.42 | Good_Mixed | 8924.1 | 17218.6 | 1.919 | 0.527 | 2.36 | 0.531 | 3.4 | 0.9703 | 0.9458 | 0.949 | 1 | 1 | 0.8929 | 0.8804 | 0.9445 | 0.9445 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1175 | 627.6 | 317.7 | 89.5 | 88.6 | 13 | 631.5 | 4364.3 | 52.7 | 26.9 | 85 | 79.9 | 76.8 | 88.3 | 37 | 19.2 | 8261.7 | 6329.3 | 8302.7 | 14439 | 10481.3 | 15068.4 | 1.748 | 1.656 | 1.815 | 0.682 | 0.671 | 0.618 | 4.72 | 3.88 | -3.91 | 0.631 | 0.562 | 0.589 | 4.3 | 4.45 | 3.69 | 0.579 | 0.624 | 0.558 | -3.66 | -3.32 | 4.25 | 0.653 | 0.636 | 0.669 | -4.18 | 3.54 | 4.22 | Fair_Mixed | 6329.3 | 10481.3 | 1.656 | 0.682 | 4.72 | 0.669 | 4.45 | 0.5905 | 0.8397 | 0.7337 | 0.7718 | 1 | 0.5809 | 0.6016 | 0.71 | 0.71 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1176 | 1007.8 | 582.3 | 106.7 | 116.7 | 22.3 | 911.5 | 5339.4 | 46 | 32.8 | 91.3 | 92.3 | 84 | 98.3 | 39.7 | 23.6 | 5830.8 | 4650.4 | 5336.7 | 9314.3 | 7399.4 | 8056.4 | 1.597 | 1.591 | 1.51 | 0.719 | 0.805 | 0.758 | 6.07 | 5.93 | 5.66 | 0.714 | 0.728 | 0.699 | 6.95 | 4.47 | 5.23 | 0.698 | 0.699 | 0.757 | 6.28 | -4.75 | 5.72 | 0.75 | 0.635 | 0.695 | 6.69 | 5.86 | 6.37 | Poor_Mixed | 4650.4 | 7399.4 | 1.51 | 0.805 | 6.07 | 0.757 | 6.95 | 0.3844 | 0.7605 | 0.4866 | 0.628 | 1 | 0.387 | 0.4038 | 0.5543 | 0.5543 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1177 | 865.1 | 492.7 | 100.9 | 123.1 | 16.9 | 882.7 | 5140 | 48.9 | 30.1 | 91.8 | 90.9 | 78.8 | 94.8 | 39.8 | 23 | 5483.9 | 6420.3 | 5837.8 | 9173.4 | 10552.7 | 9365.3 | 1.673 | 1.644 | 1.604 | 0.642 | 0.692 | 0.778 | 4.89 | 5.34 | 5.5 | 0.649 | 0.671 | 0.693 | -4.68 | 5.24 | 3.55 | 0.647 | 0.71 | 0.604 | -5.12 | -4.7 | 4.48 | 0.694 | 0.645 | 0.697 | -4.51 | 4.07 | 4.3 | Poor_Mixed | 5483.9 | 9173.4 | 1.604 | 0.778 | 5.5 | 0.71 | 5.24 | 0.441 | 0.7947 | 0.543 | 0.6484 | 1 | 0.4745 | 0.4994 | 0.6087 | 0.6087 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1178 | 100 | 120 | 65 | 50 | 1 | 350 | 2669.7 | 59.7 | 20 | 75.8 | 75.4 | 70.6 | 80 | 35 | 13.2 | 10000 | 9644.3 | 9179 | 20000 | 18941.4 | 17378.4 | 2 | 1.964 | 1.893 | 0.532 | 0.5 | 0.5 | -2.07 | 2.21 | 2 | 0.5 | 0.504 | 0.526 | -2.01 | 2 | -2.45 | 0.503 | 0.527 | 0.5 | 2 | 2 | -2 | 0.513 | 0.5 | 0.542 | 2.28 | -2.93 | 2 | Good_Mixed | 9179 | 17378.4 | 1.893 | 0.532 | 2.21 | 0.542 | 2.93 | 0.9995 | 1 | 0.9678 | 0.939 | 1 | 0.9559 | 0.9169 | 0.9725 | 0.9725 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
1179 | 1766 | 982.4 | 148.3 | 194 | 31.8 | 1370 | 9193.7 | 53.3 | 27.1 | 79.9 | 76.6 | 72.3 | 82.8 | 37 | 17.3 | 9144.8 | 9364.5 | 7397.9 | 16968.6 | 18002.4 | 12997.2 | 1.856 | 1.922 | 1.757 | 0.576 | 0.616 | 0.64 | 15.81 | 4.1 | 3.99 | 0.606 | 0.522 | 0.621 | 4.52 | 3.98 | 4.06 | 0.646 | 0.575 | 0.632 | 4.35 | 3.04 | 4.38 | 0.621 | 0.553 | 0.595 | 3.23 | -4.09 | -3.86 | Critical_DGA | 7397.9 | 12997.2 | 1.757 | 0.64 | 15.81 | 0.646 | 4.52 | 0.039 | 0.8367 | 0.8695 | 0.8291 | 1 | 0.533 | 0.6272 | 0.5861 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1180 | 313.6 | 168.4 | 67.5 | 64.4 | 2.6 | 449 | 2505.7 | 31.3 | 49.1 | 77.9 | 77.8 | 73.5 | 83.1 | 35.2 | 14.8 | 5321.4 | 4424.5 | 5874.6 | 8055.4 | 6665.9 | 9449.7 | 1.514 | 1.507 | 1.609 | 1.173 | 0.654 | 0.659 | -4.94 | 4.28 | 4.86 | 0.5 | 0.506 | 0.517 | 2.57 | 2.66 | 3.07 | 0.5 | 0.5 | 0.5 | 2.06 | 2.15 | 2 | 0.511 | 0.539 | 0.505 | 2 | 2 | -2 | Critical_Oil | 4424.5 | 6665.9 | 1.507 | 1.173 | 4.94 | 0.539 | 3.07 | 0.8389 | 0.5915 | 0.8719 | 0.8988 | 1 | 0.4596 | 0.929 | 0.8044 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | Moisture_PPM
1181 | 274.8 | 154.1 | 72.6 | 76.8 | 1.8 | 413.4 | 2803.9 | 58 | 22.4 | 83.3 | 83.2 | 74.4 | 88.7 | 37.1 | 14.6 | 901.4 | 1862.3 | 1074.1 | 779.1 | 2207.1 | 1170.6 | 0.864 | 1.185 | 1.09 | 0.743 | 0.709 | 0.714 | 5.12 | 5.45 | 5.4 | 0.566 | 0.572 | 0.6 | -2.64 | 2.72 | 2.22 | 0.528 | 0.52 | 0.5 | 2.64 | 2 | 3.08 | 0.549 | 0.514 | 0.555 | 2.93 | 3.01 | 2.82 | Critical_IR_PI | 901.4 | 779.1 | 0.864 | 0.743 | 5.45 | 0.6 | 3.08 | 0.8524 | 0.9193 | 0.7348 | 0.904 | 0.7437 | 0.451 | 0.7907 | 0.7666 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_HV
1182 | 848.5 | 554 | 101.7 | 115 | 20.3 | 742.8 | 5258.7 | 46.2 | 33 | 96.6 | 94.2 | 84 | 100.9 | 38.6 | 25.6 | 6143.6 | 6003.4 | 6840.9 | 9710.7 | 9713.4 | 10816.2 | 1.581 | 1.618 | 1.581 | 0.699 | 0.786 | 0.789 | -6.1 | 6.29 | 6.68 | 0.682 | 0.678 | 0.752 | 4.99 | 5.62 | 5.07 | 0.665 | 0.677 | 0.723 | 5.74 | 4.57 | 6.01 | 0.671 | 0.677 | 0.713 | 5.44 | -4.48 | 4.64 | Poor_Mixed | 6003.4 | 9710.7 | 1.581 | 0.789 | 6.68 | 0.752 | 6.01 | 0.4384 | 0.7581 | 0.4353 | 0.5584 | 1 | 0.3641 | 0.4433 | 0.5628 | 0.5628 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1183 | 292.8 | 168.2 | 70 | 62.6 | 2.8 | 402.2 | 2796.5 | 39.1 | 40.1 | 78.5 | 80.6 | 74 | 85.9 | 36.1 | 13.3 | 6446.9 | 5457.6 | 5221.8 | 10235 | 8502 | 4018.9 | 1.588 | 1.558 | 0.77 | 0.639 | 0.69 | 0.603 | 5.34 | 4.88 | 3.84 | 0.523 | 0.519 | 0.523 | -2.29 | 2.28 | 2.35 | 0.501 | 0.5 | 0.538 | 2 | 2 | 2.22 | 0.5 | 0.5 | 0.541 | 2 | 2.52 | 2 | Critical_Oil | 5221.8 | 4018.9 | 0.77 | 0.69 | 5.34 | 0.541 | 2.52 | 0.8454 | 0.6788 | 0.8185 | 0.9367 | 0.8125 | 0.5651 | 0.9045 | 0.7934 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
1184 | 237.7 | 260.4 | 69.1 | 70.7 | 3 | 467.2 | 3630.3 | 58.7 | 22.9 | 76.3 | 79.8 | 71.6 | 81.6 | 35.4 | 13.7 | 3771.1 | 3171.4 | 3327.5 | 5017.2 | 3991.8 | 4420.3 | 1.33 | 1.259 | 1.328 | 0.64 | 0.645 | 0.619 | 3.99 | 3.8 | 3.86 | 0.518 | 0.601 | 0.533 | -2.75 | 2.85 | 2.29 | 0.567 | 0.541 | 0.55 | 2.85 | 2.3 | 2.4 | 0.551 | 0.573 | 0.597 | -2.45 | 2.47 | -2.01 | Poor_IR_PI | 3171.4 | 3991.8 | 1.259 | 0.645 | 3.99 | 0.601 | 2.85 | 0.808 | 0.9088 | 0.894 | 0.9269 | 1 | 0.6206 | 0.7589 | 0.8303 | 0.8303 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1185 | 632.1 | 392.1 | 79.9 | 90.3 | 9.4 | 583.8 | 3722.9 | 52.2 | 27.4 | 83.1 | 83.7 | 78 | 89.7 | 38 | 17.2 | 7832.2 | 7030.4 | 6975.7 | 13306.8 | 11841 | 11577.1 | 1.699 | 1.684 | 1.66 | 0.586 | 0.611 | 0.583 | 3.68 | 3.93 | 3.34 | 0.506 | 0.604 | 0.571 | -2.94 | 4.23 | 3.12 | 0.61 | 0.602 | 0.551 | 3.26 | 3.97 | 2.96 | 0.631 | 0.608 | 0.542 | 2.84 | 3.26 | 4.55 | Fair_Mixed | 6975.7 | 11577.1 | 1.66 | 0.611 | 3.93 | 0.631 | 4.55 | 0.6277 | 0.8323 | 0.6961 | 0.832 | 1 | 0.6835 | 0.6788 | 0.7459 | 0.7459 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1186 | 1413.1 | 869.1 | 134.6 | 172.9 | 30.9 | 1093.8 | 8009 | 34.9 | 44.2 | 104.8 | 103.5 | 93.6 | 112.5 | 43 | 31.4 | 2516.6 | 2112.5 | 1509.3 | 2989.2 | 2486.1 | 1731 | 1.188 | 1.177 | 1.147 | 0.9 | 0.865 | 0.906 | 8.48 | 8.79 | 8.43 | 0.849 | 0.727 | 0.853 | 4.96 | 7.11 | 8.58 | 0.768 | 0.835 | 0.908 | 7.21 | 6.54 | 6.02 | 0.858 | 0.893 | 0.793 | 8.46 | 7.69 | 8.59 | Very Poor_Mixed | 1509.3 | 1731 | 1.147 | 0.906 | 8.79 | 0.908 | 8.59 | 0.1553 | 0.6376 | 0.1895 | 0.3444 | 1 | 0.1458 | 0.2307 | 0.3735 | 0.3735 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1187 | 100 | 146 | 65.5 | 51.3 | 1 | 350 | 2793 | 57.8 | 21.6 | 76.3 | 76.5 | 71.9 | 82.9 | 35.5 | 11.2 | 8836.9 | 9238.5 | 8759.9 | 16807.6 | 18286.3 | 16704.5 | 1.902 | 1.979 | 1.907 | 0.739 | 0.712 | 0.723 | -6.16 | 4.78 | 5.63 | 0.519 | 0.5 | 0.514 | 2.34 | 2.69 | 2.56 | 0.553 | 0.5 | 0.562 | 2 | 2 | -2 | 0.501 | 0.518 | 0.511 | 2.44 | -2 | -2.61 | Fair_Winding_TD_Cap | 8759.9 | 16704.5 | 1.902 | 0.739 | 6.16 | 0.562 | 2.69 | 0.9908 | 0.938 | 0.9171 | 0.9821 | 1 | 0.4378 | 0.8855 | 0.8817 | 0.8817 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
1188 | 320.7 | 336.4 | 84.4 | 70.6 | 10.3 | 590 | 3997.4 | 51.2 | 24.5 | 81.3 | 80.6 | 73.6 | 86 | 37.1 | 18.3 | 7968.4 | 8831.6 | 7793.9 | 14797.8 | 15945.9 | 14506.5 | 1.857 | 1.806 | 1.861 | 0.548 | 0.615 | 0.598 | 2.85 | -3.55 | 4.01 | 0.627 | 0.528 | 0.525 | -3.09 | -2.63 | -2.35 | 0.543 | 0.55 | 0.592 | 2.85 | -2.97 | 2.91 | 0.606 | 0.566 | 0.547 | 2.77 | 3.28 | 2.9 | Fair_Mixed | 7793.9 | 14506.5 | 1.806 | 0.615 | 4.01 | 0.627 | 3.28 | 0.6712 | 0.8786 | 0.7915 | 0.7993 | 1 | 0.7059 | 0.7298 | 0.7826 | 0.7826 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1189 | 1599.6 | 907.7 | 142.4 | 177.3 | 33.1 | 1207.4 | 7660 | 52.2 | 26.9 | 84.9 | 83.4 | 109 | 92.1 | 37.4 | 19.1 | 8420.7 | 8053.6 | 8973.5 | 16077.8 | 14032.9 | 16488.6 | 1.909 | 1.742 | 1.837 | 0.595 | 0.58 | 0.58 | 3.58 | 3.15 | -2.88 | 0.57 | 0.583 | 0.532 | -2.78 | 2.79 | 3.42 | 0.607 | 0.594 | 0.61 | 3.48 | 2.47 | 2.66 | 0.554 | 0.567 | 0.55 | 3.06 | 3.46 | -2.4 | Critical_DGA | 8053.6 | 14032.9 | 1.742 | 0.595 | 3.58 | 0.61 | 3.48 | 0.1096 | 0.8397 | 0.5457 | 0.7749 | 1 | 0.7227 | 0.7052 | 0.6096 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | C2H2
1190 | 100 | 184.7 | 70.1 | 153 | 2 | 350 | 2500 | 52 | 26.1 | 109.3 | 108.4 | 94.3 | 119.2 | 45.5 | 15.2 | 7002.7 | 7413.3 | 6762.2 | 4876.8 | 13212.1 | 11881.1 | 0.696 | 1.782 | 1.757 | 0.562 | 0.584 | 0.563 | 3.43 | 3.41 | 3.16 | 0.524 | 0.559 | 0.545 | -2.14 | 2.74 | 2.5 | 0.5 | 0.552 | 0.5 | 2 | 2.5 | 3.17 | 0.525 | 0.547 | 0.511 | -2.17 | 2.06 | 2.59 | Critical_Thermal | 6762.2 | 4876.8 | 0.696 | 0.584 | 3.43 | 0.559 | 3.17 | 0.8031 | 0.852 | 0.0822 | 0.8882 | 0.8187 | 0.735 | 0.8455 | 0.7418 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H4
1191 | 907.9 | 558.4 | 108.9 | 120.2 | 19.2 | 804.7 | 5525.3 | 46.4 | 34.4 | 91.7 | 92.5 | 82.6 | 98.4 | 40.4 | 25.2 | 5317.6 | 4726.5 | 5397.9 | 7951.7 | 7026.3 | 7635.1 | 1.495 | 1.487 | 1.414 | 0.704 | 0.698 | 0.692 | 5.32 | 5.03 | 5.96 | 0.609 | 0.732 | 0.655 | 4.8 | 5.56 | -4.02 | 0.594 | 0.686 | 0.745 | 3.53 | 3.99 | 4.74 | 0.738 | 0.662 | 0.678 | 4.79 | 4.35 | 3.62 | Poor_Mixed | 4726.5 | 7026.3 | 1.414 | 0.704 | 5.96 | 0.745 | 5.56 | 0.4187 | 0.7414 | 0.4866 | 0.5725 | 1 | 0.4665 | 0.4952 | 0.5854 | 0.5854 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1192 | 171.8 | 170.5 | 70.9 | 64.8 | 4 | 407.3 | 2585.4 | 57.8 | 22.7 | 77.9 | 75.6 | 73.5 | 84.6 | 35.4 | 12.8 | 6637.2 | 6050.6 | 5612.9 | 10804.6 | 9751.3 | 9103.2 | 1.628 | 1.612 | 1.622 | 0.598 | 0.629 | 0.636 | 4.23 | 3.33 | 3.93 | 0.514 | 0.561 | 0.548 | 2.68 | 3.11 | 3.1 | 0.535 | 0.512 | 0.5 | 2.96 | 2.76 | 2.44 | 0.5 | 0.537 | 0.528 | -2.58 | 2.75 | 2 | Fair_IR_PI | 5612.9 | 9103.2 | 1.612 | 0.636 | 4.23 | 0.561 | 3.11 | 0.8317 | 0.9129 | 0.8894 | 0.9484 | 1 | 0.6397 | 0.8388 | 0.8544 | 0.8544 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1193 | 1454.3 | 830 | 128.6 | 165.5 | 29.2 | 1137.6 | 7372.5 | 34.7 | 43.3 | 104.2 | 100.4 | 91.1 | 110.2 | 43.7 | 30.1 | 1270.7 | 2809.4 | 2450.8 | 1410.4 | 3779.9 | 3021.5 | 1.11 | 1.345 | 1.233 | 0.892 | 0.945 | 0.981 | -8.68 | 9.84 | 9.51 | 0.697 | 0.788 | 0.765 | -5.04 | 7.76 | 6.64 | 0.818 | 0.738 | 0.694 | 7.02 | 5.86 | 7.41 | 0.832 | 0.933 | 0.669 | 5.62 | 6.65 | 8.71 | Very Poor_Mixed | 1270.7 | 1410.4 | 1.11 | 0.981 | 9.84 | 0.933 | 8.71 | 0.1785 | 0.6465 | 0.2313 | 0.3938 | 1 | 0.0731 | 0.3091 | 0.3909 | 0.3909 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1194 | 1662.7 | 940.9 | 132.7 | 179.2 | 34.3 | 1287.2 | 8334.6 | 33.9 | 48.5 | 106.5 | 102.2 | 92.2 | 113.6 | 44.7 | 30.5 | 2604.5 | 1827.2 | 2389.2 | 2960.1 | 1958.6 | 2803 | 1.137 | 1.072 | 1.173 | 0.987 | 0.923 | 0.926 | 8.65 | -8.61 | 8.81 | 0.865 | 0.826 | 0.852 | -7.6 | 6.63 | 6.18 | 0.94 | 0.853 | 0.867 | -6.42 | 8.73 | 6.07 | 0.926 | 0.968 | 0.738 | 7.22 | 7.77 | -5.08 | Very Poor_Mixed | 1827.2 | 1958.6 | 1.072 | 0.987 | 8.81 | 0.968 | 8.73 | 0.085 | 0.597 | 0.1776 | 0.3787 | 1 | 0.1017 | 0.2083 | 0.3413 | 0.3413 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1195 | 172.5 | 157.4 | 70.8 | 64.1 | 5.1 | 397.8 | 2972 | 47.9 | 33.2 | 77.7 | 75.2 | 70.8 | 82.1 | 36.4 | 13.5 | 8462.5 | 6395.6 | 7201 | 15472.8 | 10867.9 | 13027.2 | 1.828 | 1.699 | 1.809 | 0.539 | 0.57 | 0.589 | 2.74 | -3.55 | -3.87 | 0.5 | 0.501 | 0.5 | 2.45 | 2.21 | 2.63 | 0.501 | 0.519 | 0.502 | 2.39 | -3.02 | 2.26 | 0.552 | 0.538 | 0.547 | 2.2 | 2.19 | -2.57 | Fair_Oil | 6395.6 | 10867.9 | 1.699 | 0.589 | 3.87 | 0.552 | 3.02 | 0.8183 | 0.7556 | 0.9309 | 0.9318 | 1 | 0.7393 | 0.8874 | 0.8582 | 0.8582 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1196 | 948.3 | 528.9 | 100.7 | 126.5 | 18.8 | 790.6 | 5743.8 | 45.8 | 32.7 | 92.1 | 88.7 | 84.6 | 97.1 | 39.7 | 24.7 | 5667.3 | 5766.6 | 5823.2 | 8746.3 | 8032.3 | 9181.8 | 1.543 | 1.393 | 1.577 | 0.675 | 0.728 | 0.744 | -4.64 | 5.48 | 6 | 0.733 | 0.722 | 0.679 | -5.16 | 3.77 | -5.42 | 0.671 | 0.669 | 0.645 | -4.28 | 3.6 | 4.52 | 0.591 | 0.689 | 0.693 | 5.01 | -5.32 | 4.86 | Poor_Mixed | 5667.3 | 8032.3 | 1.393 | 0.744 | 6 | 0.733 | 5.42 | 0.4207 | 0.7617 | 0.5074 | 0.59 | 1 | 0.4549 | 0.4838 | 0.5876 | 0.5876 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1197 | 100 | 149.9 | 65 | 51.7 | 1 | 359 | 2553.7 | 56.9 | 21.8 | 77.7 | 78.9 | 70 | 81.9 | 35.3 | 11.3 | 8803.4 | 9259.6 | 9806.7 | 17305.6 | 17776 | 19613.4 | 1.966 | 1.92 | 2 | 0.529 | 0.525 | 0.514 | -2 | 2.82 | 2.64 | 0.518 | 0.503 | 0.531 | 2.15 | 2.32 | 3.32 | 0.536 | 0.571 | 0.5 | 2.35 | 2.65 | 2.03 | 0.5 | 0.529 | 0.5 | -2.24 | 2.19 | 3.12 | Good_Mixed | 8803.4 | 17305.6 | 1.92 | 0.529 | 2.82 | 0.571 | 3.32 | 0.9872 | 0.9331 | 0.9048 | 0.9802 | 1 | 0.8768 | 0.8749 | 0.9385 | 0.9385 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1198 | 1442.5 | 860.3 | 138 | 174.3 | 75 | 1159.3 | 7730 | 34.5 | 47 | 104.3 | 102.1 | 92.8 | 114.1 | 44.3 | 35.4 | 1067.1 | 2036.5 | 690 | 1153.1 | 2482.5 | 752.3 | 1.081 | 1.219 | 1.09 | 0.884 | 0.928 | 0.913 | 7.67 | 9.07 | 9.08 | 0.863 | 0.754 | 0.839 | 7.81 | -5.68 | 6.75 | 0.712 | 0.789 | 0.858 | -8.14 | 7.19 | -6.31 | 0.887 | 0.819 | 0.777 | 5.88 | 9.04 | 7.96 | Critical_Mixed | 690 | 752.3 | 1.081 | 0.928 | 9.08 | 0.887 | 9.04 | 0.1284 | 0.6109 | 0.1874 | 0.1878 | 0.925 | 0.1314 | 0.2514 | 0.3452 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1199 | 219 | 213.8 | 71.9 | 64.8 | 4 | 407.9 | 2623.7 | 59.1 | 20.8 | 75 | 75 | 71.4 | 80 | 35.7 | 11.6 | 10000 | 9857.1 | 10000 | 19303.3 | 19061.5 | 19726.2 | 1.93 | 1.934 | 1.973 | 0.538 | 0.538 | 0.558 | 2.17 | -2.48 | -3.2 | 0.5 | 0.521 | 0.501 | 2.72 | 2 | 2 | 0.5 | 0.51 | 0.5 | 2 | 2 | 2.24 | 0.5 | 0.511 | 0.503 | 2.29 | 2.3 | 2.21 | Good_Mixed | 9857.1 | 19061.5 | 1.93 | 0.558 | 3.2 | 0.521 | 2.72 | 0.8205 | 0.9605 | 0.9802 | 0.9744 | 1 | 0.824 | 0.9472 | 0.913 | 0.913 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1200 | 1562.2 | 915 | 148 | 184.8 | 33 | 1363.7 | 8755.3 | 34.3 | 48.9 | 106.5 | 106.1 | 95.2 | 113.4 | 44.1 | 32 | 1827.7 | 2575.5 | 2692.1 | 1991.8 | 3165.1 | 3219.8 | 1.09 | 1.229 | 1.196 | 0.937 | 0.962 | 0.905 | 8.75 | 9.1 | 8.52 | 0.863 | 0.777 | 0.692 | 8.26 | 5.83 | 5.89 | 0.804 | 0.841 | 0.9 | 6.53 | -8.22 | 8.53 | 0.816 | 0.852 | 0.746 | 6.24 | 7.15 | 8.03 | Very Poor_Mixed | 1827.7 | 1991.8 | 1.09 | 0.962 | 9.1 | 0.9 | 8.53 | 0.0699 | 0.5933 | 0.1443 | 0.3214 | 1 | 0.1038 | 0.253 | 0.3392 | 0.3392 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1201 | 245.8 | 205.7 | 77.6 | 71.9 | 1.2 | 515.1 | 3734 | 58.8 | 20.3 | 76.9 | 78.7 | 72.6 | 81.4 | 35 | 13.3 | 5902.5 | 6159.9 | 7283.1 | 9577.1 | 10276.7 | 12388.4 | 1.623 | 1.668 | 1.701 | 0.641 | 0.555 | 0.558 | 3.54 | -3.3 | 3.24 | 0.516 | 0.572 | 0.529 | 2 | -2.7 | 3.08 | 0.5 | 0.566 | 0.518 | -2 | 2 | 2.56 | 0.5 | 0.562 | 0.546 | -2.03 | 2 | -2.97 | Fair_IR_PI | 5902.5 | 9577.1 | 1.623 | 0.641 | 3.54 | 0.572 | 3.08 | 0.8566 | 0.9791 | 0.8903 | 0.9367 | 1 | 0.717 | 0.8396 | 0.879 | 0.879 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
1202 | 1600.5 | 841.8 | 134.1 | 179.2 | 34 | 1237.9 | 8076 | 33.1 | 47.5 | 106.4 | 104 | 94.8 | 114.6 | 45 | 30.8 | 2188.8 | 945.8 | 2563.2 | 2610.5 | 1200 | 2813.6 | 1.193 | 1.269 | 1.098 | 0.954 | 0.985 | 0.947 | -9.03 | 9.35 | 9.5 | 0.885 | 0.886 | 0.838 | 8.41 | 8.92 | 7.83 | 0.705 | 0.762 | 0.816 | 8.29 | 6.35 | 5.98 | 0.799 | 0.912 | 0.918 | 8.5 | 6.67 | 9.16 | Very Poor_Mixed | 945.8 | 1200 | 1.098 | 0.985 | 9.5 | 0.918 | 9.16 | 0.1091 | 0.6062 | 0.1462 | 0.3673 | 1 | 0.06 | 0.2099 | 0.3392 | 0.3392 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1203 | 1766 | 982.4 | 147.4 | 197 | 34.3 | 1379 | 8805.1 | 57.9 | 65.5 | 77.9 | 77.9 | 72.3 | 84.4 | 35.6 | 18.6 | 7591.4 | 7456.9 | 8067.8 | 13025.4 | 13451.2 | 15000.1 | 1.716 | 1.804 | 1.859 | 0.546 | 0.588 | 0.55 | 2.48 | 3.03 | 2.94 | 0.62 | 0.558 | 0.516 | 2.95 | -3.83 | 3.57 | 0.626 | 0.599 | 0.591 | -3.15 | 3.27 | 2.72 | 0.604 | 0.582 | 0.584 | 2.84 | 2.83 | 3.03 | Critical_DGA | 7456.9 | 13025.4 | 1.716 | 0.588 | 3.03 | 0.626 | 3.83 | 0.0307 | 0.5833 | 0.8731 | 0.7902 | 1 | 0.7832 | 0.6771 | 0.596 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
1204 | 185.6 | 133.9 | 66.9 | 61.9 | 3.3 | 350 | 2631.1 | 48.5 | 33.4 | 75 | 75 | 70 | 80 | 35.5 | 11.8 | 8463.9 | 8268.8 | 8111.9 | 15391.6 | 15244.3 | 14388.5 | 1.818 | 1.844 | 1.774 | 0.575 | 0.54 | 0.581 | 3.67 | 2.06 | 2.82 | 0.554 | 0.522 | 0.563 | 2.99 | 2.26 | 2.93 | 0.506 | 0.537 | 0.533 | 2.3 | 3.07 | 2.51 | 0.5 | 0.5 | 0.536 | 2.49 | 2.45 | 2.88 | Poor_Oil | 8111.9 | 14388.5 | 1.774 | 0.581 | 3.67 | 0.563 | 3.07 | 0.8668 | 0.7532 | 0.9983 | 0.9703 | 1 | 0.778 | 0.8374 | 0.8751 | 0.8751 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1205 | 837.1 | 517.8 | 99.9 | 122 | 17.2 | 821.2 | 4944.1 | 58.3 | 20 | 77.6 | 77.7 | 71.8 | 82.8 | 35 | 10 | 9146.3 | 10000 | 8689 | 16846 | 20000 | 16214.8 | 1.842 | 2 | 1.866 | 0.545 | 0.591 | 0.531 | -2.84 | 3.08 | -2.97 | 0.554 | 0.545 | 0.535 | 3.03 | 2.83 | 2.72 | 0.533 | 0.534 | 0.553 | 2.73 | -2.56 | 2.25 | 0.565 | 0.528 | 0.505 | -2.93 | 3.37 | 3.21 | Fair_DGA | 8689 | 16214.8 | 1.842 | 0.591 | 3.08 | 0.565 | 3.37 | 0.4498 | 1 | 0.8928 | 1 | 1 | 0.7832 | 0.784 | 0.7825 | 0.7825 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1206 | 1058.5 | 566.9 | 110.1 | 131.2 | 21 | 847.6 | 6039.2 | 59.8 | 21.5 | 79.1 | 78.9 | 73.8 | 84.1 | 37 | 15.9 | 9803.8 | 10000 | 10000 | 19195.8 | 19759.3 | 19217.7 | 1.958 | 1.976 | 1.922 | 0.5 | 0.546 | 0.525 | 2 | -2.55 | 2.27 | 0.536 | 0.549 | 0.547 | 2.72 | 3.36 | 2.63 | 0.537 | 0.609 | 0.59 | 2.48 | 3.94 | 2.22 | 0.56 | 0.542 | 0.534 | 3.12 | 2.67 | 2.65 | Poor_DGA | 9803.8 | 19195.8 | 1.922 | 0.546 | 2.55 | 0.609 | 3.94 | 0.3734 | 0.9406 | 0.834 | 0.869 | 1 | 0.9032 | 0.745 | 0.7536 | 0.7536 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1207 | 707.5 | 535.9 | 105.2 | 115.3 | 15.8 | 849.3 | 5507 | 47.5 | 34.6 | 91.1 | 94 | 84.4 | 100.9 | 40.4 | 22.6 | 5122 | 5394.2 | 4507.1 | 7580.1 | 8204.8 | 6542.6 | 1.48 | 1.521 | 1.452 | 0.783 | 0.77 | 0.768 | -6.18 | -5.77 | 6.56 | 0.723 | 0.755 | 0.736 | 5.74 | 4.13 | 3.71 | 0.567 | 0.654 | 0.649 | 3.43 | 4.22 | 5.46 | 0.655 | 0.682 | 0.714 | 4.61 | 4.71 | 4.37 | Poor_Mixed | 4507.1 | 6542.6 | 1.452 | 0.783 | 6.56 | 0.755 | 5.74 | 0.4608 | 0.7391 | 0.4572 | 0.6619 | 1 | 0.3601 | 0.4873 | 0.5808 | 0.5808 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1208 | 309.4 | 205.2 | 71.6 | 69.8 | 6.1 | 399.5 | 3503.6 | 59.4 | 22.4 | 79 | 82.7 | 74.3 | 86.5 | 35.9 | 14.8 | 9141 | 8125.6 | 9571.7 | 17006.6 | 15199.7 | 18233.6 | 1.86 | 1.871 | 1.905 | 0.515 | 0.522 | 0.527 | -2 | 2.17 | 2 | 0.511 | 0.502 | 0.504 | 2 | 2.28 | 2.03 | 0.508 | 0.507 | 0.522 | -2.55 | 2.24 | 2.03 | 0.518 | 0.5 | 0.508 | 2 | 2.09 | 2.4 | Good_Mixed | 8125.6 | 15199.7 | 1.86 | 0.527 | 2.17 | 0.522 | 2.55 | 0.7736 | 0.9193 | 0.7924 | 0.8988 | 1 | 0.914 | 0.9185 | 0.8812 | 0.8812 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1209 | 1618.7 | 815.1 | 137 | 165 | 32.6 | 1116.9 | 7293.5 | 36 | 44.1 | 100.1 | 102.4 | 90.1 | 109.1 | 41.6 | 33.3 | 3615.2 | 3155 | 3419.9 | 4720.1 | 3996.9 | 4198.9 | 1.306 | 1.267 | 1.228 | 0.852 | 0.849 | 1.887 | 7.59 | -8.14 | 7.95 | 0.846 | 0.739 | 0.801 | 5.1 | 6.4 | -7.84 | 0.711 | 0.85 | 0.867 | -7.76 | -6.97 | 7.53 | 0.727 | 0.709 | 0.649 | 6.68 | 5.08 | 4.98 | Critical_Mixed | 3155 | 3996.9 | 1.228 | 1.887 | 8.14 | 0.867 | 7.84 | 0.15 | 0.6386 | 0.2691 | 0.2709 | 1 | 0.1748 | 0.3216 | 0.3969 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
1210 | 963.9 | 457.6 | 101.8 | 112 | 16.9 | 692.4 | 5009 | 48.4 | 32.1 | 88 | 87 | 83.8 | 97.9 | 39.2 | 23.9 | 6620 | 7094.3 | 5210.1 | 10445.8 | 11855.8 | 7941.1 | 1.578 | 1.671 | 1.524 | 0.727 | 0.738 | 0.757 | 4.72 | 6.3 | 5.78 | 0.621 | 0.734 | 0.617 | 5.23 | -4.48 | -5.01 | 0.596 | 0.701 | 0.723 | -4.57 | 4.39 | 5.37 | 0.707 | 0.694 | 0.733 | 5.78 | -5.59 | 4.4 | Poor_Mixed | 5210.1 | 7941.1 | 1.524 | 0.757 | 6.3 | 0.734 | 5.78 | 0.4729 | 0.7691 | 0.5504 | 0.6177 | 1 | 0.4197 | 0.4687 | 0.5996 | 0.5996 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1211 | 810.9 | 521 | 98.4 | 109.5 | 15.4 | 807.9 | 4995.9 | 46.5 | 34.1 | 87.5 | 87.1 | 79.7 | 94.4 | 39.8 | 24.5 | 5528.8 | 6222.1 | 5324.7 | 8971.1 | 9902.1 | 8047.7 | 1.623 | 1.591 | 1.511 | 0.696 | 0.679 | 0.669 | 5 | 5.51 | -4.74 | 0.569 | 0.646 | 0.648 | 4.34 | 3.62 | 4.42 | 0.621 | 0.622 | 0.611 | -4.49 | 3.96 | 4.09 | 0.637 | 0.598 | 0.592 | 3.54 | 4.69 | -3.46 | Poor_Mixed | 5324.7 | 8047.7 | 1.511 | 0.696 | 5.51 | 0.648 | 4.69 | 0.4778 | 0.7449 | 0.5933 | 0.597 | 1 | 0.5023 | 0.5872 | 0.634 | 0.634 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1212 | 536.1 | 393.3 | 89.9 | 108 | 15.5 | 685.7 | 4449.6 | 54.3 | 26.7 | 86.2 | 87.5 | 77.8 | 92 | 36.4 | 17.7 | 7986.8 | 8423.4 | 6449.6 | 14534.2 | 15494.5 | 10724.6 | 1.82 | 1.839 | 1.663 | 0.645 | 0.627 | 0.656 | -4.27 | 4.15 | 4.51 | 0.546 | 0.604 | 0.648 | -3.19 | 4.02 | -3.42 | 0.671 | 0.594 | 0.602 | 3.27 | 3.66 | 3.96 | 0.568 | 0.609 | 0.627 | 3.16 | 4.23 | 3.67 | Fair_Mixed | 6449.6 | 10724.6 | 1.663 | 0.656 | 4.51 | 0.671 | 4.23 | 0.5427 | 0.8427 | 0.6443 | 0.8173 | 1 | 0.5863 | 0.6204 | 0.6958 | 0.6958 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1213 | 1000.7 | 574.9 | 106 | 124.2 | 23.2 | 953.9 | 6279.1 | 58.8 | 23.5 | 80.2 | 77.4 | 72.5 | 84.5 | 36.2 | 16.3 | 8260.8 | 9608.6 | 9523.1 | 15298.3 | 18657.9 | 19046.2 | 1.852 | 1.942 | 2 | 0.584 | 0.568 | 0.529 | 3.8 | -2.61 | -3.02 | 0.508 | 0.553 | 0.518 | 2.57 | -2 | 2.96 | 0.5 | 0.5 | 0.521 | -2 | 3.01 | -2 | 0.53 | 0.526 | 0.533 | -2.72 | 2.47 | -2.61 | Poor_DGA | 8260.8 | 15298.3 | 1.852 | 0.584 | 3.8 | 0.553 | 3.01 | 0.3589 | 0.8969 | 0.852 | 0.8578 | 1 | 0.7647 | 0.8649 | 0.7482 | 0.7482 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1214 | 1587.7 | 857.8 | 141.8 | 184.3 | 34.2 | 1147.3 | 7949.8 | 32.7 | 49.1 | 105 | 106.5 | 92.5 | 112.3 | 43.4 | 32.7 | 1990.3 | 1763.7 | 2077.9 | 2255.3 | 2157.5 | 2358 | 1.133 | 1.223 | 1.135 | 0.983 | 0.948 | 0.951 | 9.84 | -8.84 | 9.13 | 0.954 | 0.93 | 0.764 | 6.27 | 5.44 | 8.25 | 0.869 | 0.745 | 0.981 | 6.36 | 7.76 | -9.01 | 0.863 | 0.915 | 0.818 | 7.46 | 8.29 | 8.57 | Very Poor_Mixed | 1763.7 | 2157.5 | 1.133 | 0.983 | 9.84 | 0.981 | 9.01 | 0.1089 | 0.5915 | 0.176 | 0.2943 | 1 | 0.0621 | 0.1882 | 0.3331 | 0.3331 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1215 | 897.3 | 492.4 | 98.9 | 121.3 | 13.9 | 776.2 | 4810.4 | 44.9 | 34.9 | 90.4 | 89 | 80.2 | 97 | 38.8 | 24.4 | 6254.5 | 5512.7 | 5312.5 | 9965.8 | 8244.1 | 7669 | 1.593 | 1.495 | 1.444 | 0.705 | 0.683 | 0.718 | 5.51 | 4.77 | 5.44 | 0.709 | 0.616 | 0.599 | 4.67 | 4.05 | -5.22 | 0.691 | 0.613 | 0.685 | 5.32 | 4.96 | 5.5 | 0.748 | 0.753 | 0.619 | 5.24 | 3.97 | 4.96 | Poor_Mixed | 5312.5 | 7669 | 1.444 | 0.718 | 5.51 | 0.753 | 5.5 | 0.4786 | 0.7356 | 0.5506 | 0.6005 | 1 | 0.474 | 0.4863 | 0.6069 | 0.6069 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1216 | 1766 | 982.4 | 139.4 | 191.3 | 32.5 | 1340.3 | 7825.1 | 34.5 | 42.4 | 104.6 | 107.2 | 92.6 | 114.3 | 44.4 | 31.5 | 1525.7 | 2111.9 | 2180.5 | 1755.9 | 2531.8 | 2654.7 | 1.151 | 1.199 | 1.217 | 0.931 | 0.901 | 0.873 | 8.81 | 8.63 | 8.25 | 0.713 | 0.738 | 0.921 | 6.31 | 6.8 | 5.84 | 0.929 | 0.764 | 0.818 | 6.79 | 8.76 | 8.01 | 0.907 | 0.769 | 0.678 | 9.19 | -8.96 | 6.45 | Very Poor_Mixed | 1525.7 | 1755.9 | 1.151 | 0.931 | 8.81 | 0.929 | 9.19 | 0.0666 | 0.6554 | 0.1567 | 0.3406 | 1 | 0.1381 | 0.2531 | 0.3529 | 0.3529 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1217 | 196.6 | 166.8 | 70.7 | 54.4 | 3.1 | 350 | 2554.2 | 58.7 | 20 | 75.9 | 75 | 70 | 80 | 35 | 11.5 | 9196 | 10000 | 9524.9 | 17457.7 | 19963.2 | 18886.7 | 1.898 | 1.996 | 1.983 | 0.578 | 0.5 | 0.567 | 3.1 | 2.36 | 2 | 0.546 | 0.5 | 0.512 | 2 | 2.18 | 2 | 0.54 | 0.501 | 0.528 | 2 | -2.81 | 2.56 | 0.5 | 0.535 | 0.512 | 2.64 | 2 | 2.85 | Good_Mixed | 9196 | 17457.7 | 1.898 | 0.578 | 3.1 | 0.546 | 2.85 | 0.8761 | 1 | 0.9839 | 0.9764 | 1 | 0.8482 | 0.8823 | 0.9238 | 0.9238 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1218 | 806.5 | 530.9 | 99.4 | 113.5 | 20 | 813.8 | 5102.4 | 45.5 | 33.3 | 91.8 | 89.3 | 81.9 | 97.8 | 38.6 | 23.1 | 6744.4 | 5695.7 | 6116.6 | 11000.3 | 9253.5 | 9919.9 | 1.631 | 1.625 | 1.622 | 0.712 | 0.733 | 0.722 | 5.75 | -6.11 | -5.59 | 0.673 | 0.752 | 0.731 | -4.89 | 5.1 | 3.96 | 0.758 | 0.661 | 0.664 | 4.28 | -4.38 | 4.04 | 0.657 | 0.676 | 0.642 | 4.41 | 4.69 | -5.17 | Poor_Mixed | 5695.7 | 9253.5 | 1.622 | 0.733 | 6.11 | 0.758 | 5.17 | 0.4417 | 0.7544 | 0.5256 | 0.645 | 1 | 0.4232 | 0.4708 | 0.5898 | 0.5898 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1219 | 146.2 | 155.3 | 66.9 | 67.6 | 1 | 414.3 | 3382.1 | 58.4 | 21 | 77.5 | 77.5 | 71.7 | 85.6 | 35 | 14.4 | 8732.5 | 9848.2 | 9341.1 | 16583 | 19136.2 | 18011.8 | 1.899 | 1.943 | 1.928 | 0.546 | 0.56 | 0.584 | 2.93 | -3.35 | 2.44 | 0.558 | 0.502 | 0.553 | 2 | 2.19 | -2.18 | 0.5 | 0.54 | 0.539 | 2.43 | 2.81 | -2.37 | 0.5 | 0.5 | 0.527 | -3.07 | 2.06 | 2 | Good_Mixed | 8732.5 | 16583 | 1.899 | 0.584 | 3.35 | 0.558 | 3.07 | 0.9365 | 0.9543 | 0.8828 | 0.9092 | 1 | 0.774 | 0.8737 | 0.908 | 0.908 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1220 | 1491.6 | 909.1 | 132.8 | 182 | 31.3 | 1198.8 | 7840.2 | 35.3 | 43.5 | 104.8 | 108 | 92 | 114.3 | 43.9 | 30.1 | 1890.6 | 2690.2 | 2451 | 2165.2 | 3124 | 3245 | 1.145 | 1.161 | 1.324 | 0.853 | 0.873 | 0.902 | 7.5 | 6.78 | -8.04 | 0.753 | 0.722 | 0.766 | 6.49 | -7.7 | 6.1 | 0.75 | 0.817 | 0.889 | 6.7 | 6.86 | 6.39 | 0.819 | 0.832 | 0.841 | -5.4 | 4.96 | -7.45 | Very Poor_Mixed | 1890.6 | 2165.2 | 1.145 | 0.902 | 8.04 | 0.889 | 7.7 | 0.1276 | 0.6445 | 0.1582 | 0.3938 | 1 | 0.2143 | 0.2874 | 0.3865 | 0.3865 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1221 | 1060.8 | 688.3 | 119.9 | 138 | 20.5 | 893.4 | 6787.8 | 54.7 | 28 | 76.8 | 76.6 | 72.4 | 84.2 | 35.8 | 12.9 | 8407.2 | 10000 | 8653.9 | 15039.8 | 20000 | 16219.4 | 1.789 | 2 | 1.874 | 0.5 | 0.522 | 0.539 | 2.07 | 2 | 3 | 0.56 | 0.5 | 0.589 | 2.43 | 2.26 | 3.8 | 0.586 | 0.581 | 0.604 | 3.08 | 3.41 | 3.37 | 0.609 | 0.592 | 0.527 | -2.94 | 3.68 | -3.29 | Poor_DGA | 8407.2 | 15039.8 | 1.789 | 0.539 | 3 | 0.609 | 3.8 | 0.3348 | 0.8235 | 0.8978 | 0.9461 | 1 | 0.9048 | 0.7129 | 0.7346 | 0.7346 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1222 | 189.5 | 181.6 | 71.2 | 70.3 | 1 | 500.6 | 3584 | 52.1 | 25.7 | 81.1 | 79.7 | 76.1 | 87.2 | 36 | 15.3 | 4894.8 | 6426.2 | 4474.5 | 7397.9 | 9886.3 | 6776.4 | 1.511 | 1.538 | 1.514 | 0.573 | 0.62 | 0.637 | 3.87 | 3.83 | 4.94 | 0.526 | 0.52 | 0.514 | -2.22 | 2 | 2.46 | 0.538 | 0.5 | 0.55 | -2.42 | -2.49 | -2 | 0.535 | 0.505 | 0.561 | 2.89 | 2.01 | 2.15 | Poor_IR_PI | 4474.5 | 6776.4 | 1.511 | 0.637 | 4.94 | 0.561 | 2.89 | 0.9064 | 0.8584 | 0.7813 | 0.8855 | 1 | 0.6305 | 0.8519 | 0.8536 | 0.8536 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1223 | 1064.5 | 616.8 | 114.4 | 138.6 | 27.8 | 973.2 | 6407.6 | 55.8 | 24.8 | 82.4 | 78.6 | 73.7 | 86.7 | 36.6 | 13.8 | 7928.7 | 9572.3 | 10000 | 14150.8 | 18089.8 | 19132.3 | 1.785 | 1.89 | 1.913 | 0.614 | 0.557 | 0.5 | 3.4 | 3.39 | 2.34 | 0.5 | 0.539 | 0.5 | 3.28 | 2.79 | -2.83 | 0.531 | 0.544 | 0.588 | 2.38 | 2.33 | 3.31 | 0.539 | 0.512 | 0.509 | 2.44 | 2.61 | 2.65 | Poor_DGA | 7928.7 | 14150.8 | 1.785 | 0.614 | 3.4 | 0.588 | 3.31 | 0.3026 | 0.8734 | 0.7988 | 0.9244 | 1 | 0.7972 | 0.8323 | 0.728 | 0.728 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1224 | 1593.4 | 838.6 | 135.9 | 162.2 | 33.6 | 1251.2 | 8197.1 | 35.1 | 44.8 | 102.4 | 102.3 | 92.3 | 113.7 | 45.2 | 31.4 | 2081.8 | 1696.5 | 2496.6 | 2389.6 | 1898.4 | 3113.7 | 1.148 | 1.119 | 1.247 | 0.969 | 0.927 | 0.981 | -9.13 | 9.69 | 9.42 | 0.802 | 0.796 | 0.819 | 5.89 | -8.16 | 7.67 | 0.89 | 0.808 | 0.757 | 5.2 | -6.14 | -8.39 | 0.877 | 0.756 | 0.739 | 5.56 | 5.99 | 7.27 | Very Poor_Mixed | 1696.5 | 1898.4 | 1.119 | 0.981 | 9.69 | 0.89 | 8.39 | 0.1216 | 0.6318 | 0.1952 | 0.3444 | 1 | 0.0561 | 0.2734 | 0.36 | 0.36 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1225 | 1591.2 | 831.1 | 140 | 191 | 29.2 | 1318.1 | 9033.4 | 33.4 | 45.6 | 106.9 | 107.7 | 93.1 | 114.9 | 44.9 | 31.6 | 1207.2 | 1226.3 | 1553.3 | 1334.4 | 1303.2 | 1818.3 | 1.105 | 1.063 | 1.171 | 0.929 | 0.99 | 0.941 | 9.37 | -9.84 | 9.3 | 0.855 | 0.855 | 0.937 | 7.19 | 9.69 | 7.62 | 0.829 | 0.823 | 0.853 | 8.32 | -6.59 | 9.81 | 0.776 | 0.842 | 0.99 | 7.08 | 6.59 | 9.48 | Very Poor_Mixed | 1207.2 | 1303.2 | 1.063 | 0.99 | 9.84 | 0.99 | 9.81 | 0.0966 | 0.6241 | 0.1317 | 0.3368 | 1 | 0.0554 | 0.1768 | 0.3286 | 0.3286 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1226 | 1580.5 | 899.7 | 138.9 | 180.5 | 26.8 | 1372.6 | 8927.4 | 36 | 43.9 | 103.7 | 101.2 | 93.9 | 115.5 | 43.9 | 33.2 | 816.5 | 1346.6 | 1875.9 | 1200 | 1424.1 | 1972.5 | 1.47 | 1.058 | 1.051 | 0.927 | 0.958 | 0.945 | 8.27 | 9.28 | 8.7 | 0.84 | 0.923 | 0.751 | 8.66 | 6.14 | 5.8 | 0.896 | 0.787 | 0.809 | 6.97 | 8.24 | 8.17 | 0.885 | 0.798 | 0.797 | 7.34 | 6.22 | 8.26 | Very Poor_Mixed | 816.5 | 1200 | 1.051 | 0.958 | 9.28 | 0.923 | 8.66 | 0.1065 | 0.6406 | 0.1857 | 0.2748 | 1 | 0.0999 | 0.2277 | 0.3508 | 0.3508 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1227 | 246.3 | 120 | 70.8 | 61 | 1.2 | 408.3 | 2601.8 | 57.5 | 20.2 | 82.6 | 76.6 | 73.6 | 87.1 | 36.5 | 12.6 | 3972 | 4754.2 | 4516.8 | 5467.4 | 6971.5 | 6637.5 | 1.376 | 1.466 | 1.47 | 0.66 | 0.633 | 0.669 | -3.9 | -3.97 | 3.75 | 0.506 | 0.527 | 0.517 | -2 | 2.04 | -2.05 | 0.542 | 0.547 | 0.539 | 2.75 | 2.75 | -2 | 0.561 | 0.536 | 0.5 | 2.28 | 2.5 | 2.11 | Poor_IR_PI | 3972 | 5467.4 | 1.376 | 0.669 | 3.97 | 0.561 | 2.75 | 0.9115 | 0.984 | 0.8173 | 0.953 | 1 | 0.6009 | 0.8444 | 0.8714 | 0.8714 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1228 | 100 | 166.8 | 67.7 | 50 | 1 | 350 | 2507.7 | 60 | 20.2 | 75.4 | 75.9 | 71.8 | 81.3 | 35 | 13.4 | 8949.1 | 10000 | 10000 | 17371.3 | 20000 | 19483 | 1.941 | 2 | 1.948 | 0.526 | 0.5 | 0.522 | 2.21 | -2.44 | 2.17 | 0.53 | 0.516 | 0.525 | 2 | -2.34 | 2.51 | 0.558 | 0.537 | 0.524 | 2.52 | 2.22 | -2.52 | 0.519 | 0.542 | 0.504 | 2.73 | 2.53 | 2.33 | Good_Mixed | 8949.1 | 17371.3 | 1.941 | 0.526 | 2.44 | 0.558 | 2.73 | 0.9927 | 0.984 | 0.9476 | 0.9342 | 1 | 0.9163 | 0.8345 | 0.9462 | 0.9462 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_LV_R_TanDelta_pct
1229 | 173.3 | 120 | 65 | 50 | 1.6 | 371.2 | 2984 | 56.4 | 21.8 | 81.4 | 81 | 76.8 | 88 | 37.5 | 13.3 | 2728.9 | 2223.6 | 1177.6 | 3284.1 | 2601.1 | 1369.5 | 1.203 | 1.17 | 1.163 | 0.685 | 0.686 | 0.662 | 5.26 | 4.85 | 5.21 | 0.587 | 2.266 | 0.592 | 3.17 | 4.01 | 3.27 | 0.561 | 0.582 | 0.585 | 2.73 | 3.87 | 3.34 | 0.605 | 0.58 | 0.619 | 2.98 | -2.52 | -4.53 | Critical_IR_PI | 1177.6 | 1369.5 | 1.163 | 0.686 | 5.26 | 2.266 | 4.53 | 0.9302 | 0.9331 | 0.7508 | 0.9367 | 1 | 0.5045 | 0.6102 | 0.8069 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Bushing_HV_Y_TanDelta_pct
1230 | 684 | 412.4 | 90 | 99.8 | 13.5 | 698.6 | 4425.7 | 49.6 | 32 | 86.2 | 83.3 | 74.7 | 93.7 | 38 | 19.8 | 5735.7 | 7877.1 | 7512.5 | 9201.6 | 14159.3 | 12851 | 1.604 | 1.798 | 1.711 | 0.72 | 0.638 | 0.635 | 5.49 | 5.22 | 4.04 | 0.604 | 0.525 | 0.611 | -3.91 | -4.21 | 3.42 | 0.575 | 0.617 | 0.593 | 3.98 | 3.42 | 3.6 | 0.649 | 0.652 | 0.54 | 4.38 | 3.13 | 3.91 | Fair_Mixed | 5735.7 | 9201.6 | 1.604 | 0.72 | 5.49 | 0.652 | 4.38 | 0.5491 | 0.7703 | 0.6803 | 0.753 | 1 | 0.5307 | 0.6357 | 0.6841 | 0.6841 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1231 | 312.1 | 216.7 | 75.6 | 95.3 | 5.5 | 498.1 | 2982.4 | 54.4 | 26.1 | 94.4 | 93.2 | 85.2 | 99.3 | 40.2 | 12.4 | 9512.6 | 9422.9 | 8931.9 | 19025.2 | 17766.5 | 16652.7 | 2 | 1.885 | 1.864 | 0.561 | 0.573 | 0.551 | 2.34 | -3.15 | 2.49 | 0.5 | 0.525 | 0.579 | 2.54 | 2.67 | 2.55 | 0.52 | 0.505 | 0.569 | 2 | 2.55 | 3.48 | 0.582 | 0.551 | 0.555 | 2.35 | -2.74 | -2.49 | Poor_Thermal | 8931.9 | 16652.7 | 1.864 | 0.573 | 3.15 | 0.582 | 3.48 | 0.7332 | 0.852 | 0.4457 | 0.9575 | 1 | 0.793 | 0.801 | 0.7932 | 0.7932 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1232 | 844.6 | 501.3 | 105.2 | 107.8 | 14.9 | 741.3 | 4731.3 | 46.2 | 33.6 | 91 | 91.8 | 82.6 | 95.8 | 39.4 | 25.2 | 7059.7 | 4813.5 | 6297.8 | 11982.8 | 7340.6 | 10067.2 | 1.697 | 1.525 | 1.599 | 0.737 | 0.748 | 0.758 | -6.37 | 5.9 | -6.13 | 0.717 | 0.67 | 0.632 | -4.57 | 5.81 | 4.44 | 0.675 | 0.727 | 0.688 | 5.12 | 5.79 | 5.57 | 0.625 | 0.654 | 0.626 | 4.58 | 4.26 | 5.72 | Poor_Mixed | 4813.5 | 7340.6 | 1.525 | 0.758 | 6.37 | 0.727 | 5.81 | 0.4887 | 0.7509 | 0.515 | 0.5725 | 1 | 0.3838 | 0.4777 | 0.5921 | 0.5921 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1233 | 813.8 | 553.4 | 106.1 | 125.6 | 14.7 | 853.6 | 5450.3 | 45.1 | 34.9 | 92.1 | 93 | 81.2 | 99.7 | 39.9 | 25.9 | 6182.4 | 5170.3 | 5286.6 | 9450.7 | 7665.3 | 7806.7 | 1.529 | 1.483 | 1.477 | 0.747 | 0.74 | 0.753 | 6.15 | 6.38 | 5.96 | 0.667 | 0.695 | 0.61 | 5.56 | 5.14 | -4.24 | 0.631 | 0.678 | 0.797 | -4.5 | 4.84 | 6.15 | 0.686 | 0.725 | 0.722 | 6 | 5.71 | 4.44 | Poor_Mixed | 5170.3 | 7665.3 | 1.477 | 0.753 | 6.38 | 0.797 | 6.15 | 0.4472 | 0.7356 | 0.4865 | 0.5478 | 1 | 0.383 | 0.4498 | 0.5707 | 0.5707 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1234 | 819.7 | 520.1 | 106.1 | 119.4 | 17.9 | 827.8 | 5314.8 | 47.7 | 31.4 | 91 | 92.6 | 82.6 | 96.2 | 39.8 | 25.7 | 5876.1 | 6435 | 6504.9 | 9146.9 | 10805.9 | 10549.2 | 1.557 | 1.679 | 1.622 | 0.721 | 0.701 | 0.695 | 5.69 | 5.37 | 5.2 | 0.736 | 0.655 | 0.649 | 4.67 | 5.17 | -4.02 | 0.612 | 0.611 | 0.677 | -4.14 | 6.21 | 4.35 | 0.665 | 0.744 | 0.671 | -3.6 | 4.77 | 4.46 | Poor_Mixed | 5876.1 | 9146.9 | 1.557 | 0.721 | 5.69 | 0.744 | 6.21 | 0.44 | 0.7778 | 0.5053 | 0.5549 | 1 | 0.4603 | 0.4965 | 0.5954 | 0.5954 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1235 | 411.8 | 266.2 | 77 | 70.1 | 4.1 | 518.9 | 3261.4 | 54 | 25 | 77.6 | 75.4 | 73.2 | 83.8 | 36 | 13 | 8365.5 | 8383.7 | 9363.2 | 14799.1 | 15553.7 | 18479.7 | 1.769 | 1.855 | 1.974 | 0.783 | 0.819 | 0.786 | 6.58 | 6.76 | 7.03 | 0.543 | 0.531 | 0.557 | 2.59 | 2.57 | 2.91 | 0.571 | 0.545 | 0.539 | 2.65 | 3.46 | 2.3 | 0.5 | 0.539 | 0.51 | -3.2 | -3.54 | 3.18 | Poor_Winding_TD_Cap | 8365.5 | 14799.1 | 1.769 | 0.819 | 7.03 | 0.571 | 3.54 | 0.7619 | 0.87 | 0.8994 | 0.9438 | 1 | 0.3088 | 0.792 | 0.7778 | 0.7778 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1236 | 1007.5 | 610.6 | 110.8 | 121.6 | 13.9 | 838.2 | 5322.3 | 45.8 | 34.3 | 91 | 88.8 | 81.8 | 98.6 | 39.4 | 24.5 | 6109.4 | 5037.4 | 6327.1 | 9846.1 | 7580.1 | 10123.4 | 1.612 | 1.505 | 1.6 | 0.763 | 0.741 | 0.724 | 6.43 | 5.74 | 6.01 | 0.629 | 0.605 | 0.671 | 5.21 | 5.99 | 4.7 | 0.724 | 0.68 | 0.759 | 4.36 | 4.94 | -5.65 | 0.595 | 0.726 | 0.671 | 5.66 | -5.75 | 4.04 | Poor_Mixed | 5037.4 | 7580.1 | 1.505 | 0.763 | 6.43 | 0.759 | 5.99 | 0.435 | 0.7426 | 0.5259 | 0.597 | 1 | 0.3922 | 0.4723 | 0.5802 | 0.5802 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1237 | 1766 | 970.6 | 143.5 | 197 | 34.3 | 1379 | 8744 | 51.8 | 27.4 | 75.3 | 79.3 | 73 | 85.3 | 36.2 | 17.3 | 7612.5 | 6763.2 | 6643.7 | 13230.5 | 11595.9 | 11538.2 | 1.738 | 1.715 | 1.737 | 0.597 | 0.656 | 0.576 | -4.46 | 4.72 | -16.63 | 0.545 | 0.571 | 0.578 | -2.64 | 2.49 | 2.71 | 0.609 | 0.527 | 0.515 | -2.6 | 3.52 | 2 | 0.559 | 0.544 | 0.531 | -3.63 | 3.22 | 2.87 | Critical_DGA | 6643.7 | 11538.2 | 1.715 | 0.656 | 16.63 | 0.609 | 3.63 | 0.036 | 0.8323 | 0.8781 | 0.8291 | 1 | 0.5134 | 0.7547 | 0.6058 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1238 | 180.8 | 197.2 | 65 | 52.5 | 1 | 368.8 | 2799.4 | 58.5 | 20.1 | 77.6 | 77.3 | 72 | 82.5 | 36.2 | 12.1 | 9038.7 | 9302.8 | 9514.1 | 18022 | 17484.7 | 18879.8 | 1.994 | 1.88 | 1.984 | 0.541 | 0.53 | 0.558 | 2.21 | 2.82 | 2.59 | 0.561 | 0.52 | 0.529 | 2.43 | -2.49 | 2.61 | 0.519 | 0.563 | 0.57 | 3.17 | 3.07 | 2.94 | 0.5 | 0.672 | 0.55 | -2.02 | 4.58 | 3.21 | Fair_Bushing_TD_Cap | 9038.7 | 17484.7 | 1.88 | 0.558 | 2.82 | 0.672 | 4.58 | 0.9655 | 0.9898 | 0.8917 | 0.964 | 1 | 0.8319 | 0.7648 | 0.9117 | 0.9117 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_TV_Y_TanDelta_pct
1239 | 993 | 535.9 | 101 | 119 | 21.3 | 860 | 5530.6 | 44.2 | 36 | 89.5 | 87.9 | 78.9 | 96.7 | 39.4 | 23.5 | 5906.6 | 6913 | 5927.3 | 9771.9 | 11995.4 | 9165.2 | 1.654 | 1.735 | 1.546 | 0.721 | 0.76 | 0.725 | 5.35 | -6 | 4.99 | 0.605 | 0.64 | 0.682 | 4.29 | 3.87 | -4.4 | 0.694 | 0.625 | 0.672 | 5.19 | 4.41 | 4.25 | 0.741 | 0.658 | 0.536 | 3.75 | -5.3 | 4.01 | Poor_Mixed | 5906.6 | 9165.2 | 1.546 | 0.76 | 6 | 0.741 | 5.3 | 0.4024 | 0.7231 | 0.5705 | 0.6314 | 1 | 0.4326 | 0.5329 | 0.5925 | 0.5925 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1240 | 525.8 | 293.4 | 93 | 153.9 | 4.7 | 690.6 | 4047.7 | 56.2 | 24.8 | 107.3 | 124.5 | 95.6 | 117 | 44.6 | 14.1 | 7093.3 | 7953.1 | 8690.3 | 11864.2 | 14574.5 | 15162.6 | 1.673 | 1.833 | 1.745 | 0.653 | 0.631 | 0.639 | -3.77 | 3.87 | -3.89 | 0.56 | 0.569 | 0.536 | 3.69 | 3.34 | 3.97 | 0.593 | 0.5 | 0.569 | 3.11 | -3.38 | -3.33 | 0.57 | 0.55 | 0.591 | 3.66 | 3.72 | 2.57 | Critical_Thermal | 7093.3 | 11864.2 | 1.673 | 0.653 | 3.89 | 0.593 | 3.97 | 0.6129 | 0.8734 | 0.0949 | 0.9169 | 1 | 0.6161 | 0.7209 | 0.6894 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | C2H4
1241 | 630.3 | 332.7 | 90.9 | 93.5 | 3 | 641.9 | 4866.7 | 53.2 | 26.4 | 87.1 | 86.9 | 79.7 | 93.4 | 38.8 | 15.2 | 9204.9 | 8039.8 | 8822.8 | 17139.1 | 14849.6 | 16724.5 | 1.862 | 1.847 | 1.896 | 0.942 | 0.99 | 0.957 | 9.48 | 9.84 | -8.56 | 0.533 | 0.5 | 0.513 | 2.9 | 2 | -2.89 | 0.575 | 0.535 | 1.034 | 2.81 | 2.95 | 2.15 | 0.544 | 0.521 | 0.542 | 2.19 | 2.95 | 3.52 | Critical_Winding_TD_Cap | 8039.8 | 14849.6 | 1.847 | 0.99 | 9.84 | 1.034 | 3.52 | 0.687 | 0.8474 | 0.6087 | 0.8882 | 1 | 0.0595 | 0.7541 | 0.6828 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_LV_TanDelta_pct
1242 | 866.6 | 514.8 | 103.5 | 123.2 | 18.1 | 900.1 | 5408.2 | 46.4 | 34.4 | 88.5 | 89.1 | 82.4 | 94.8 | 38.8 | 24.5 | 5612.2 | 6434.2 | 6015.7 | 8588.3 | 10157.9 | 9762.6 | 1.53 | 1.579 | 1.623 | 0.765 | 0.708 | 0.708 | 5.54 | 5.53 | 5.46 | 0.639 | 0.657 | 0.653 | -4.38 | 4.44 | -3.58 | 0.695 | 0.633 | 0.674 | 3.94 | 4.4 | -4.07 | 0.646 | 0.69 | 0.643 | 4.01 | -4.09 | -4.06 | Poor_Mixed | 5612.2 | 8588.3 | 1.53 | 0.765 | 5.54 | 0.695 | 4.44 | 0.424 | 0.7414 | 0.5593 | 0.597 | 1 | 0.4365 | 0.5251 | 0.5964 | 0.5964 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1243 | 919.7 | 518.8 | 110.4 | 122.4 | 15.6 | 815.1 | 4536.1 | 44.2 | 35.6 | 90.6 | 89.4 | 83.2 | 99.4 | 39.4 | 25.3 | 4783 | 4691.2 | 5258.3 | 6821.7 | 6432.8 | 7596.2 | 1.426 | 1.371 | 1.445 | 0.738 | 0.767 | 0.725 | 6.12 | 6.41 | -5.81 | 0.636 | 0.722 | 0.741 | -5.51 | 4.75 | 4.9 | 0.691 | 0.702 | 0.687 | 4.38 | 4.17 | -3.37 | 0.698 | 0.678 | 0.649 | 5.18 | 4.04 | 4.51 | Poor_Mixed | 4691.2 | 6432.8 | 1.371 | 0.767 | 6.41 | 0.741 | 5.51 | 0.4502 | 0.7276 | 0.5115 | 0.569 | 1 | 0.3888 | 0.472 | 0.5789 | 0.5789 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1244 | 577.4 | 395 | 88.5 | 91.5 | 68.5 | 520.2 | 4728.5 | 50.7 | 26 | 81.3 | 79.5 | 76.2 | 86.3 | 36.2 | 16.2 | 690 | 690 | 913 | 758.7 | 724.2 | 934.4 | 1.1 | 1.05 | 1.023 | 0.747 | 0.748 | 0.723 | 4.64 | 5.49 | 5.65 | 0.59 | 0.64 | 0.604 | -3.74 | 3.58 | 3.6 | 0.637 | 0.59 | 0.547 | 4.46 | 3 | 4.31 | 0.566 | 0.567 | 0.565 | -3.47 | 4.37 | 4.81 | Critical_IR_PI | 690 | 724.2 | 1.023 | 0.748 | 5.65 | 0.64 | 4.81 | 0.4764 | 0.8536 | 0.7843 | 0.8607 | 0.775 | 0.4396 | 0.6367 | 0.6431 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1245 | 509.7 | 267.6 | 75.7 | 121.7 | 3.8 | 523.2 | 3408.1 | 55.2 | 25.6 | 94.5 | 95.2 | 86.5 | 100.9 | 42.2 | 15.3 | 8512.6 | 9126.1 | 8303.8 | 15786.4 | 16769.6 | 14593.8 | 1.854 | 1.838 | 1.757 | 0.659 | 0.673 | 0.621 | -3.92 | 4.95 | 3.5 | 0.573 | 0.564 | 0.532 | 2.94 | 2.38 | 2.73 | 0.544 | 0.53 | 0.545 | -2.75 | 2.47 | 3.6 | 0.581 | 0.571 | 0.535 | -2 | 2.82 | 2.41 | Poor_Thermal | 8303.8 | 14593.8 | 1.757 | 0.673 | 4.95 | 0.581 | 3.6 | 0.7006 | 0.86 | 0.4033 | 0.8855 | 1 | 0.5899 | 0.7599 | 0.7423 | 0.7423 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1246 | 931.7 | 582.2 | 108.7 | 120.5 | 20.2 | 913.1 | 5512.2 | 58 | 21.8 | 81.8 | 76.7 | 71.3 | 83.3 | 36.5 | 11 | 8215.4 | 8519.5 | 8552.6 | 15616.5 | 15709.9 | 15907.9 | 1.901 | 1.844 | 1.86 | 0.574 | 0.583 | 0.522 | 2.65 | 3.17 | -2.46 | 0.508 | 0.5 | 0.543 | -2.08 | -2.23 | -2.29 | 0.53 | 0.524 | 0.525 | -2.15 | 2.1 | -2.06 | 0.51 | 0.513 | 0.554 | -2 | -2.24 | -2.79 | Poor_DGA | 8215.4 | 15616.5 | 1.844 | 0.583 | 3.17 | 0.554 | 2.79 | 0.3949 | 0.9331 | 0.8619 | 0.9858 | 1 | 0.7929 | 0.8679 | 0.7734 | 0.7734 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1247 | 203.5 | 120 | 75.9 | 88.1 | 1.9 | 350 | 3052.7 | 60 | 20.4 | 91.3 | 94.3 | 85.9 | 100.8 | 40.3 | 11.3 | 9506 | 8704.2 | 9090.8 | 18122.8 | 15577.8 | 16454.5 | 1.906 | 1.79 | 1.81 | 0.549 | 0.506 | 0.538 | -2.51 | 2.71 | 2.66 | 0.5 | 0.534 | 0.551 | 3.25 | 2.12 | 2.89 | 0.546 | 0.544 | 0.53 | 2.77 | 2 | 2.28 | 0.553 | 0.55 | 0.558 | 2.98 | 3.12 | 2.98 | Poor_Thermal | 8704.2 | 15577.8 | 1.79 | 0.549 | 2.71 | 0.558 | 3.25 | 0.8593 | 0.9748 | 0.446 | 0.9802 | 1 | 0.8518 | 0.7926 | 0.8474 | 0.8474 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_LV
1248 | 922.9 | 462.9 | 107.6 | 112.1 | 16.9 | 750.6 | 5099.7 | 47.4 | 34 | 90.4 | 89.6 | 78.5 | 99 | 39.2 | 26.8 | 5355.6 | 3807.7 | 5528.3 | 8125.1 | 5214.2 | 8595.1 | 1.517 | 1.369 | 1.555 | 0.753 | 0.737 | 0.703 | -6.08 | 5.64 | 5.39 | 0.685 | 0.702 | 0.755 | -3.83 | 5.43 | 5.51 | 0.615 | 0.715 | 0.649 | 4.32 | 5.24 | 5.18 | 0.703 | 0.713 | 0.693 | -4.22 | 4.72 | 4.55 | Poor_Mixed | 3807.7 | 5214.2 | 1.369 | 0.753 | 6.08 | 0.755 | 5.51 | 0.4627 | 0.7461 | 0.5455 | 0.5156 | 1 | 0.4221 | 0.4601 | 0.5875 | 0.5875 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1249 | 995.7 | 642.9 | 112.3 | 132.5 | 21.5 | 954.5 | 6015.2 | 60 | 21.6 | 77.6 | 76.8 | 71.8 | 81.7 | 36.3 | 15.4 | 9019.8 | 8922.4 | 9748.2 | 16551.1 | 16401.9 | 19123.9 | 1.835 | 1.838 | 1.962 | 0.548 | 0.55 | 0.544 | 3.22 | -2.5 | -3.64 | 0.564 | 0.569 | 0.501 | 2.77 | 2.84 | 3.03 | 0.5 | 0.52 | 0.511 | 2.74 | -2.82 | 2.63 | 0.514 | 0.511 | 0.538 | 2 | -2.79 | 2.57 | Poor_DGA | 8922.4 | 16401.9 | 1.835 | 0.55 | 3.64 | 0.569 | 3.03 | 0.3514 | 0.938 | 0.9025 | 0.8828 | 1 | 0.7836 | 0.8431 | 0.7563 | 0.7563 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1250 | 725.8 | 518.5 | 102 | 115 | 17.6 | 856.3 | 5522.2 | 54.3 | 25.4 | 81 | 78.9 | 72 | 83.5 | 36.7 | 12.9 | 9303 | 10000 | 8737.2 | 18389.1 | 19868.5 | 16876.6 | 1.977 | 1.987 | 1.932 | 0.568 | 0.543 | 0.635 | 3.04 | 2.17 | -3.86 | 0.501 | 0.5 | 0.545 | -2.79 | -2.62 | 2.74 | 0.584 | 0.529 | 0.529 | -2.63 | 2.45 | 2.43 | 0.506 | 0.514 | 0.5 | 2 | 2.78 | 2.35 | Poor_DGA | 8737.2 | 16876.6 | 1.932 | 0.635 | 3.86 | 0.584 | 2.79 | 0.4512 | 0.8633 | 0.8374 | 0.9461 | 1 | 0.7457 | 0.8641 | 0.7674 | 0.7674 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1251 | 237.1 | 172.9 | 75.6 | 60.7 | 1.2 | 381.1 | 2943.9 | 55.7 | 24.5 | 79.1 | 77.9 | 70.6 | 83.1 | 35.1 | 14.7 | 6135.1 | 5809.7 | 5901.8 | 10063.1 | 8713.5 | 9125.3 | 1.64 | 1.5 | 1.546 | 0.619 | 0.627 | 0.628 | 4.05 | 4.1 | 4.24 | 0.522 | 0.518 | 0.506 | 2.71 | 2 | -2 | 0.52 | 0.514 | 0.517 | -2.57 | 2.44 | 2.58 | 0.5 | 0.526 | 0.5 | 2.15 | 2.22 | -2.38 | Poor_IR_PI | 5809.7 | 8713.5 | 1.5 | 0.628 | 4.24 | 0.526 | 2.71 | 0.9072 | 0.8786 | 0.8868 | 0.9014 | 1 | 0.6165 | 0.8928 | 0.873 | 0.873 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1252 | 896.9 | 607.2 | 112.9 | 131.6 | 18.7 | 813.7 | 5764.5 | 56 | 24.4 | 79.9 | 80.3 | 72.7 | 83.7 | 36.9 | 12.5 | 9527.6 | 9609.1 | 8882 | 18780.4 | 18708.9 | 16014.2 | 1.971 | 1.947 | 1.803 | 0.5 | 0.521 | 0.548 | 2.35 | 2.14 | 3.01 | 0.509 | 0.532 | 0.538 | -2 | 2.21 | 2.45 | 0.525 | 0.515 | 0.5 | 2.49 | -2.01 | 2.82 | 0.5 | 0.5 | 0.5 | 2.77 | -2.2 | 2 | Poor_DGA | 8882 | 16014.2 | 1.803 | 0.548 | 3.01 | 0.538 | 2.82 | 0.3997 | 0.8804 | 0.8261 | 0.9552 | 1 | 0.8871 | 0.9081 | 0.7836 | 0.7836 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1253 | 223.7 | 120 | 65 | 50 | 1.1 | 386.8 | 2500 | 58.9 | 21.8 | 77.4 | 80.9 | 70.8 | 82.7 | 35.5 | 11.5 | 9783.8 | 8681.1 | 10000 | 19401.3 | 16572.5 | 20000 | 1.983 | 1.909 | 2 | 0.538 | 0.529 | 0.525 | 2.6 | 2.63 | 3.34 | 0.537 | 0.522 | 0.501 | -2.23 | 2.12 | -2 | 0.534 | 0.564 | 0.5 | -2.3 | 2 | 3.01 | 0.504 | 0.526 | 0.512 | 2 | 2 | 2.21 | Good_Mixed | 8681.1 | 16572.5 | 1.909 | 0.538 | 3.34 | 0.564 | 3.01 | 0.9521 | 0.9331 | 0.8745 | 0.9764 | 1 | 0.8312 | 0.8776 | 0.9206 | 0.9206 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1254 | 284 | 196.7 | 81.1 | 68.4 | 1 | 516.2 | 3145.6 | 17.9 | 26.6 | 81.9 | 79.2 | 73.9 | 85.9 | 36.2 | 17.8 | 7882.3 | 6982.2 | 7182.1 | 13825.6 | 12162.4 | 13052.6 | 1.754 | 1.742 | 1.817 | 0.63 | 0.615 | 0.598 | 4.59 | 4.12 | 3.87 | 0.624 | 0.502 | 0.647 | 3.57 | 3.53 | 3.61 | 0.968 | 0.566 | 0.503 | -9.07 | -2.47 | -4.11 | 0.592 | 0.53 | 0.577 | 3.25 | 4.85 | 2.73 | Critical_Bushing_TD_Cap | 6982.2 | 12162.4 | 1.742 | 0.63 | 4.59 | 0.968 | 9.07 | 0.892 | 0.2609 | 0.8016 | 0.8143 | 1 | 0.6249 | 0.6409 | 0.7381 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1255 | 278.3 | 203 | 90.6 | 91.6 | 52.3 | 560.9 | 3795.2 | 30.6 | 49.4 | 82.3 | 81.8 | 77 | 89.8 | 37.9 | 18.8 | 5342.9 | 5086.3 | 4948.2 | 7779.9 | 7622.2 | 7435.2 | 1.456 | 1.499 | 1.503 | 0.717 | 0.673 | 0.691 | 5.41 | 4.97 | 4.79 | 0.554 | 0.546 | 0.563 | 2.41 | 3.92 | -2.69 | 0.572 | 0.508 | 0.553 | -2.8 | 3.69 | -3.14 | 0.573 | 0.505 | 0.599 | -2 | 2.28 | -3.03 | Critical_Oil | 4948.2 | 7435.2 | 1.456 | 0.717 | 5.41 | 0.599 | 3.92 | 0.5263 | 0.5888 | 0.7243 | 0.7841 | 1 | 0.4922 | 0.7597 | 0.6795 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1256 | 222.1 | 222.2 | 74.6 | 53.7 | 2.6 | 386.6 | 3107 | 58.5 | 23.9 | 75 | 77.5 | 70.5 | 81.3 | 35.9 | 13.2 | 5987.7 | 6743.3 | 6965.4 | 9894.3 | 11220.9 | 11820.2 | 1.652 | 1.664 | 1.697 | 0.607 | 0.509 | 0.574 | 3.3 | 2.76 | 3.14 | 0.552 | 0.546 | 0.54 | -2.19 | 2.05 | -2 | 0.616 | 0.549 | 0.531 | -2.87 | -2.2 | -2.54 | 0.505 | 0.502 | 0.528 | 2.79 | 3.16 | -2.59 | Fair_IR_PI | 5987.7 | 9894.3 | 1.652 | 0.607 | 3.3 | 0.616 | 3.16 | 0.8642 | 0.8894 | 0.948 | 0.939 | 1 | 0.7729 | 0.8081 | 0.8782 | 0.8782 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1257 | 1084 | 657.4 | 114.4 | 144.3 | 20.1 | 952.2 | 6298.1 | 46.8 | 33.8 | 92.9 | 92.9 | 83.9 | 97.8 | 40.6 | 25.6 | 5243.1 | 6120.4 | 4702.1 | 7632.8 | 9724 | 6797.3 | 1.456 | 1.589 | 1.446 | 0.693 | 0.671 | 0.695 | 5.26 | 4.47 | 5.27 | 0.692 | 0.665 | 0.676 | 4.88 | 5.52 | 4.41 | 0.74 | 0.665 | 0.646 | -5.02 | 5.39 | 5.7 | 0.744 | 0.675 | 0.668 | 5.7 | 4.59 | 3.39 | Poor_Mixed | 4702.1 | 6797.3 | 1.446 | 0.695 | 5.27 | 0.744 | 5.7 | 0.3358 | 0.7485 | 0.4699 | 0.5584 | 1 | 0.5023 | 0.4609 | 0.562 | 0.562 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1258 | 1597.6 | 911.5 | 134.9 | 181.4 | 34.3 | 1334.6 | 8227 | 32.2 | 47.2 | 105.4 | 106.9 | 93.6 | 116.2 | 43.3 | 31.8 | 1945.3 | 1308.4 | 1591.4 | 2104.1 | 1464.6 | 1718.2 | 1.082 | 1.119 | 1.08 | 0.921 | 0.946 | 0.869 | 8.74 | -9.41 | 8.33 | 0.846 | 0.788 | 0.905 | 7.32 | 7.9 | -7.24 | 0.865 | 0.792 | 0.84 | -7.97 | 6.57 | 8.38 | 0.779 | 0.771 | 0.796 | 8.19 | 5.35 | 7.55 | Very Poor_Mixed | 1308.4 | 1464.6 | 1.08 | 0.946 | 9.41 | 0.905 | 8.38 | 0.0855 | 0.609 | 0.1466 | 0.3291 | 1 | 0.1178 | 0.2353 | 0.3444 | 0.3444 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1259 | 463 | 299.3 | 79.6 | 77.2 | 9.6 | 517.3 | 4242.2 | 53.9 | 24.4 | 80.9 | 79.4 | 74.3 | 84.6 | 37.6 | 14.4 | 8300 | 7694.7 | 7433.6 | 15333.7 | 13735.3 | 12943.9 | 1.847 | 1.785 | 1.741 | 0.593 | 0.574 | 0.578 | -3.77 | 3.5 | -3.32 | 0.541 | 0.551 | 0.574 | 2.49 | 2.38 | 2.94 | 0.546 | 0.574 | 0.56 | -3.06 | 3.27 | -3.45 | 0.534 | 0.571 | 0.5 | 3.31 | 3.22 | 2.86 | Fair_Mixed | 7433.6 | 12943.9 | 1.741 | 0.593 | 3.77 | 0.574 | 3.45 | 0.6721 | 0.8804 | 0.804 | 0.9092 | 1 | 0.7059 | 0.7582 | 0.7948 | 0.7948 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1260 | 445 | 338.8 | 86.6 | 88.9 | 10.6 | 616.3 | 3847.2 | 54.1 | 22.3 | 81.3 | 81.8 | 76.9 | 87.6 | 36 | 16 | 8786.6 | 8841.9 | 7914.2 | 16503.9 | 15949.7 | 14685.1 | 1.878 | 1.804 | 1.856 | 0.585 | 0.603 | 0.563 | 3.16 | 3.42 | 3.42 | 0.588 | 0.605 | 0.633 | 3.41 | -3.16 | 3.9 | 0.595 | 0.604 | 0.591 | 4.54 | 3.04 | 3.31 | 0.532 | 0.638 | 0.583 | 3.08 | 3.1 | 3.05 | Fair_Mixed | 7914.2 | 14685.1 | 1.804 | 0.603 | 3.42 | 0.638 | 4.54 | 0.631 | 0.9215 | 0.7542 | 0.8663 | 1 | 0.7164 | 0.6469 | 0.7638 | 0.7638 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1261 | 1567.6 | 880.2 | 134.1 | 172 | 31.6 | 1179.6 | 7239.8 | 32.8 | 45.1 | 104.3 | 107.4 | 93 | 118.3 | 44.5 | 31.9 | 2197.2 | 2596.5 | 2137.8 | 2507.2 | 3288.9 | 2522.2 | 1.141 | 1.267 | 1.18 | 0.883 | 0.928 | 0.981 | 7.98 | 9.32 | -9.8 | 0.812 | 0.748 | 0.809 | -5.42 | 7.34 | -5.3 | 0.863 | 0.816 | 0.899 | 8.86 | 7.6 | -8.4 | 0.753 | 0.904 | 0.853 | -5.66 | 8.36 | -7.65 | Very Poor_Mixed | 2137.8 | 2507.2 | 1.141 | 0.981 | 9.8 | 0.904 | 8.86 | 0.1409 | 0.6289 | 0.1343 | 0.3252 | 1 | 0.0949 | 0.2355 | 0.3561 | 0.3561 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1262 | 257 | 165.2 | 66.7 | 61.8 | 1.6 | 482.3 | 3125.6 | 59.7 | 21.8 | 85.8 | 82.4 | 78.4 | 88.5 | 37.8 | 15.2 | 2385.2 | 2838.5 | 1763.2 | 2791.7 | 3255.6 | 2150.9 | 1.17 | 1.147 | 1.22 | 0.657 | 0.732 | 2.006 | 4.68 | -5.73 | -4.43 | 0.543 | 0.516 | 0.535 | -2.86 | -2.64 | 3.14 | 0.567 | 0.552 | 0.574 | 2.9 | 3.21 | 2.65 | 0.544 | 0.523 | 0.569 | 3.52 | 2.1 | 2.25 | Critical_IR_PI | 1763.2 | 2150.9 | 1.147 | 2.006 | 5.73 | 0.574 | 3.52 | 0.8696 | 0.9331 | 0.6905 | 0.8882 | 1 | 0.4215 | 0.7673 | 0.7999 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_TV_TanDelta_pct
1263 | 305.5 | 120 | 70.7 | 53.9 | 1.4 | 398.8 | 2953.7 | 56.2 | 22.1 | 78.5 | 80.1 | 76.9 | 87.6 | 36.9 | 13 | 7143.5 | 6850.1 | 6304.4 | 12123.7 | 11515.6 | 10409.2 | 1.697 | 1.681 | 1.651 | 0.581 | 0.578 | 0.59 | 3.36 | 3.06 | 2.81 | 0.552 | 0.511 | 0.582 | 2.93 | 2.57 | 2.99 | 0.521 | 0.537 | 0.52 | -2.81 | 2.43 | 2.16 | 0.509 | 0.529 | 0.577 | 2.45 | 3.2 | -3.52 | Poor_IR_PI | 6304.4 | 10409.2 | 1.651 | 0.59 | 3.36 | 0.582 | 3.52 | 0.9065 | 0.926 | 0.7885 | 0.9438 | 1 | 0.7335 | 0.7956 | 0.8697 | 0.8697 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1264 | 355 | 258 | 77.2 | 73 | 2.3 | 502.9 | 3487.1 | 50.2 | 30 | 75 | 75 | 72.1 | 83.6 | 36.5 | 18.5 | 8514 | 9240.4 | 9661.2 | 16036.1 | 5289.9 | 18122.4 | 1.883 | 0.572 | 1.876 | 0.982 | 0.99 | 0.934 | 9.82 | 9.84 | 9.67 | 0.676 | 0.59 | 0.609 | 2.73 | -3.98 | 5.06 | 0.704 | 0.605 | 0.662 | 4.91 | 3.28 | 3.56 | 0.613 | 0.697 | 0.589 | 4.52 | 4.16 | 4.37 | Critical_Winding_TD_Cap | 8514 | 5289.9 | 0.572 | 0.99 | 9.84 | 0.704 | 5.06 | 0.8004 | 0.796 | 0.9519 | 0.7933 | 0.8187 | 0.0316 | 0.5586 | 0.6664 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_LV
1265 | 952.2 | 548.8 | 100.6 | 110.6 | 15.6 | 788.8 | 4753.9 | 48 | 33.8 | 90.6 | 90.7 | 81.8 | 99.2 | 39.9 | 23.8 | 6260.6 | 7023.1 | 6703.3 | 10391.6 | 12006.2 | 11647.1 | 1.66 | 1.71 | 1.738 | 0.731 | 0.716 | 0.702 | -5.48 | -5.51 | 6 | 0.654 | 0.756 | 0.69 | 4.12 | -4.93 | 5.58 | 0.634 | 0.679 | 0.671 | 4.49 | 5.22 | 3.67 | 0.748 | 0.606 | 0.629 | 5.62 | 4.97 | -5.18 | Poor_Mixed | 6260.6 | 10391.6 | 1.66 | 0.731 | 6 | 0.756 | 5.62 | 0.4643 | 0.7485 | 0.5097 | 0.6212 | 1 | 0.4371 | 0.4805 | 0.5956 | 0.5956 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1266 | 421 | 383.2 | 86.3 | 84.9 | 1.3 | 570.9 | 3740.2 | 35.9 | 65.2 | 77.3 | 81.8 | 73.7 | 87.5 | 36.2 | 15.5 | 5760.1 | 5344.9 | 5417.2 | 8554.5 | 8103.5 | 8119.4 | 1.485 | 1.516 | 1.499 | 0.689 | 0.702 | 0.619 | 4.06 | 4.61 | 3.78 | 0.616 | 0.623 | 0.534 | 3.38 | -3.22 | 3.75 | 0.636 | 0.534 | 0.553 | 3.98 | 3.39 | 4.2 | 0.531 | 0.584 | 0.599 | 4.93 | 2.9 | 2.85 | Critical_Oil | 5344.9 | 8103.5 | 1.485 | 0.702 | 4.61 | 0.636 | 4.93 | 0.7831 | 0.5833 | 0.8146 | 0.88 | 1 | 0.5695 | 0.6725 | 0.752 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1267 | 885.6 | 488.6 | 102.9 | 118.8 | 15.6 | 814.5 | 4729.4 | 47.6 | 34.3 | 91.7 | 92.8 | 83.1 | 100.7 | 39.4 | 27 | 5268.1 | 6199.3 | 5671.8 | 7893.1 | 9344.3 | 8131.5 | 1.498 | 1.507 | 1.434 | 0.713 | 0.741 | 0.705 | 5.3 | 5.75 | 5.34 | 0.639 | 0.654 | 0.701 | 4.99 | 4.94 | 5.65 | 0.701 | 0.608 | 0.734 | 3.78 | -5.01 | 4.76 | 0.691 | 0.708 | 0.657 | 4.35 | -3.42 | 4.45 | Poor_Mixed | 5268.1 | 7893.1 | 1.434 | 0.741 | 5.75 | 0.734 | 5.65 | 0.4635 | 0.7426 | 0.4764 | 0.5083 | 1 | 0.4453 | 0.4857 | 0.5878 | 0.5878 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1268 | 872.4 | 600 | 116.9 | 129.7 | 22 | 852.5 | 6062 | 57.7 | 22.9 | 75 | 77.9 | 72 | 83 | 35 | 12.1 | 9505.6 | 9102.1 | 8906.2 | 19011.1 | 17897 | 17483.3 | 2 | 1.966 | 1.963 | 0.565 | 0.623 | 0.588 | 2.94 | -3.49 | 2.95 | 0.582 | 0.526 | 0.526 | 2.43 | 2.69 | 2.26 | 0.524 | 0.547 | 0.574 | 2.93 | 3.61 | 2.63 | 0.529 | 0.535 | 0.589 | 2.25 | 3.21 | 2.63 | Poor_DGA | 8906.2 | 17483.3 | 1.963 | 0.623 | 3.49 | 0.589 | 3.61 | 0.374 | 0.9088 | 0.9235 | 0.964 | 1 | 0.7201 | 0.7698 | 0.7425 | 0.7425 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1269 | 261 | 231.9 | 79.6 | 81.8 | 4.6 | 480.7 | 3162.3 | 54 | 24.4 | 84.1 | 84.1 | 78 | 90.7 | 37.2 | 11.9 | 1032 | 1050.4 | 1008.4 | 1053.2 | 1091.7 | 1066.6 | 1.021 | 1.039 | 1.058 | 2.087 | 0.659 | 0.752 | -4.82 | 5.27 | 5.53 | 0.539 | 0.54 | 0.599 | 2.44 | 2.55 | 2.35 | 0.554 | 0.568 | 0.526 | 2.77 | 3.15 | 3.29 | 0.545 | 0.538 | 0.564 | -2.13 | -3.53 | 2.49 | Critical_IR_PI | 1008.4 | 1053.2 | 1.021 | 2.087 | 5.53 | 0.599 | 3.53 | 0.7632 | 0.8804 | 0.685 | 0.9682 | 1 | 0.3999 | 0.7573 | 0.7656 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
1270 | 486.5 | 323.9 | 87.6 | 83.2 | 2.1 | 586 | 4365.2 | 52 | 24.1 | 81.1 | 77.6 | 75.5 | 87.2 | 35.5 | 11.3 | 1172.5 | 1236.2 | 1162.6 | 1275.4 | 987.1 | 1221 | 1.088 | 0.798 | 1.05 | 0.739 | 0.695 | 0.709 | 6.03 | 5.27 | 4.73 | 0.541 | 0.5 | 0.533 | 2.83 | -2.44 | 3.02 | 0.549 | 0.537 | 0.506 | 3.61 | 2.9 | 3.12 | 0.538 | 0.557 | 0.538 | 2.82 | -2.05 | 2.99 | Critical_IR_PI | 1162.6 | 987.1 | 0.798 | 0.739 | 6.03 | 0.557 | 3.61 | 0.7476 | 0.8857 | 0.8078 | 0.9802 | 0.7437 | 0.4572 | 0.8052 | 0.7509 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_LV
1271 | 219.6 | 198.4 | 66.6 | 111.6 | 2.4 | 415 | 3486.5 | 55 | 23.5 | 93.7 | 96.2 | 85.9 | 104.7 | 40.9 | 11.7 | 7193.5 | 9952.5 | 7912.6 | 13517.7 | 19266.5 | 14353.9 | 1.879 | 1.936 | 1.814 | 0.616 | 0.508 | 0.517 | 4.19 | 2.48 | 2 | 0.576 | 0.534 | 0.536 | 2 | 2.43 | 2 | 0.561 | 0.551 | 0.5 | 2.23 | 2.77 | 2.69 | 0.503 | 0.51 | 0.539 | 3.21 | 2.91 | 3.19 | Poor_Thermal | 7193.5 | 13517.7 | 1.814 | 0.616 | 4.19 | 0.576 | 3.21 | 0.7961 | 0.8969 | 0.3956 | 0.9724 | 1 | 0.8216 | 0.8215 | 0.8177 | 0.8177 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1272 | 951.2 | 605.3 | 108.9 | 109.8 | 20.2 | 846.2 | 5185.2 | 56.7 | 21.8 | 77.6 | 77.1 | 72.8 | 81.3 | 36.8 | 10 | 9530.7 | 9385.7 | 9949.8 | 19061.4 | 18771.3 | 19253.4 | 2 | 2 | 1.935 | 0.542 | 0.57 | 0.537 | 3.34 | 3.16 | 2.38 | 0.547 | 0.596 | 0.542 | 2 | 2 | 2.2 | 0.513 | 0.517 | 0.5 | 2.91 | -2 | 3.05 | 0.552 | 0.552 | 0.503 | 2.23 | -2 | -3 | Fair_DGA | 9385.7 | 18771.3 | 1.935 | 0.57 | 3.34 | 0.596 | 3.05 | 0.4128 | 0.9331 | 0.8898 | 1 | 1 | 0.7918 | 0.8331 | 0.7749 | 0.7749 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1273 | 100 | 184.5 | 72.8 | 58.2 | 2.1 | 399 | 2604.5 | 56.7 | 21.3 | 78.9 | 77.3 | 73.4 | 83.7 | 35.7 | 12 | 5593.2 | 5260.6 | 6315.5 | 9486.4 | 8180.7 | 9928.7 | 1.696 | 1.555 | 1.572 | 0.621 | 0.601 | 0.654 | 4.16 | 3.58 | 4.34 | 0.5 | 0.552 | 0.521 | 2.54 | 2.92 | -2.35 | 0.562 | 0.504 | 0.501 | 2.36 | -3.11 | -2 | 0.564 | 0.524 | 0.538 | -2.82 | 2.65 | 2.14 | Poor_IR_PI | 5260.6 | 8180.7 | 1.555 | 0.654 | 4.34 | 0.564 | 3.11 | 0.8891 | 0.9458 | 0.8633 | 0.9661 | 1 | 0.623 | 0.8394 | 0.8687 | 0.8687 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1274 | 270.9 | 173.8 | 65 | 59.6 | 4.8 | 350 | 3111.4 | 60 | 20 | 76.7 | 76.4 | 71.5 | 82.1 | 35 | 10.9 | 9799 | 9947.3 | 10000 | 19117.4 | 19386.1 | 19966.8 | 1.951 | 1.949 | 1.997 | 0.506 | 0.544 | 0.5 | 2 | 2.64 | 2 | 0.569 | 0.564 | 0.526 | 2.38 | 2.91 | 2.29 | 0.527 | 0.552 | 0.555 | -2.45 | 2.78 | 2.46 | 0.508 | 0.525 | 0.522 | -2 | -2.62 | -2.45 | Good_Mixed | 9799 | 19117.4 | 1.949 | 0.544 | 2.64 | 0.569 | 2.91 | 0.8307 | 1 | 0.9231 | 0.9875 | 1 | 0.9278 | 0.8047 | 0.9041 | 0.9041 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1275 | 580.5 | 258.2 | 82.7 | 90.4 | 10.6 | 589.8 | 3907.1 | 51.1 | 28 | 83.2 | 85.4 | 76.1 | 88.3 | 37.3 | 21.2 | 7527.3 | 7712.9 | 8411.8 | 13284 | 13107.2 | 15829.5 | 1.765 | 1.699 | 1.882 | 0.633 | 0.706 | 0.643 | 3.93 | 4.3 | 3.66 | 0.557 | 0.624 | 0.596 | -4.32 | 2.65 | 3.74 | 0.632 | 0.614 | 0.605 | 4.25 | -3.06 | -3.5 | 0.615 | 0.608 | 0.632 | 3.73 | 3.42 | -3.51 | Fair_Mixed | 7527.3 | 13107.2 | 1.699 | 0.706 | 4.3 | 0.632 | 4.32 | 0.6328 | 0.8235 | 0.7072 | 0.7082 | 1 | 0.5897 | 0.6175 | 0.7169 | 0.7169 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1276 | 139.6 | 120 | 67.2 | 50 | 1.1 | 350 | 2617.8 | 59.8 | 20 | 75 | 75 | 70 | 81.7 | 35.3 | 10.1 | 9773 | 8949.8 | 9632.5 | 19546 | 17666.8 | 19065.4 | 2 | 1.974 | 1.979 | 0.519 | 0.616 | 0.525 | -2.45 | 2.99 | 2.51 | 0.5 | 0.503 | 0.5 | 2.18 | 2 | 2 | 0.532 | 0.524 | 0.5 | -2 | 2.3 | -2.24 | 0.5 | 0.5 | 0.5 | 2 | 2 | 2.09 | Good_Mixed | 8949.8 | 17666.8 | 1.974 | 0.616 | 2.99 | 0.532 | 2.3 | 0.9699 | 1 | 0.9906 | 0.9992 | 1 | 0.8165 | 0.9566 | 0.958 | 0.958 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1277 | 1278 | 737.3 | 125.2 | 152.7 | 65.8 | 1061 | 6557.7 | 39.8 | 40.2 | 100.4 | 98.1 | 87 | 106.4 | 41.4 | 31.3 | 2653 | 2820.2 | 2912.2 | 3430.5 | 3480.4 | 3624.2 | 1.293 | 1.234 | 1.244 | 0.855 | 0.874 | 0.845 | 7.44 | 7.86 | 8.1 | 0.808 | 0.72 | 0.774 | 7.71 | 6.61 | 4.81 | 0.723 | 0.726 | 0.825 | -5.33 | -6.58 | 5.01 | 0.769 | 0.8 | 0.698 | 6.84 | 7.03 | 7.63 | Critical_Mixed | 2653 | 3430.5 | 1.234 | 0.874 | 8.1 | 0.825 | 7.71 | 0.2079 | 0.6778 | 0.3254 | 0.3483 | 1 | 0.2085 | 0.3278 | 0.4315 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1278 | 452.3 | 316.4 | 84.5 | 78.7 | 3.1 | 589.7 | 3689.2 | 57.3 | 20.6 | 77.6 | 75.2 | 72.5 | 82.2 | 35 | 16.4 | 977.6 | 1272.6 | 1659.3 | 1110 | 1392.1 | 1915.5 | 1.135 | 1.094 | 1.154 | 0.721 | 0.745 | 1.312 | 5.5 | 5.57 | 5.02 | 0.564 | 0.608 | 0.594 | -4.21 | -2.94 | 3.02 | 0.594 | 0.562 | 0.598 | 3.04 | -3.16 | -3.09 | 0.632 | 0.577 | 0.567 | 3.42 | 3.31 | -3.15 | Critical_IR_PI | 977.6 | 1110 | 1.094 | 1.312 | 5.57 | 0.632 | 4.21 | 0.7409 | 0.9672 | 0.9208 | 0.855 | 1 | 0.3734 | 0.664 | 0.7679 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_TV_TanDelta_pct
1279 | 242.8 | 142.5 | 69.2 | 55.1 | 3.4 | 350 | 2890.5 | 28.4 | 44.8 | 76 | 79.7 | 73.1 | 86.2 | 35.5 | 10.4 | 5306.1 | 4302.1 | 4792 | 7984.2 | 5917.1 | 7053.4 | 1.505 | 1.375 | 1.472 | 0.671 | 0.632 | 0.7 | 4.31 | 4.34 | 4.5 | 0.508 | 0.58 | 0.558 | 2.3 | 3.27 | 2.67 | 0.5 | 0.554 | 0.519 | 3.06 | -2.86 | -2 | 0.54 | 0.556 | 0.6 | -3.15 | 3.73 | 3.13 | Critical_Oil | 4302.1 | 5917.1 | 1.375 | 0.7 | 4.5 | 0.6 | 3.73 | 0.8668 | 0.0485 | 0.8619 | 0.9955 | 1 | 0.557 | 0.7786 | 0.7366 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1280 | 1679 | 952.5 | 136.6 | 177 | 29.9 | 1243.8 | 8838.1 | 34.6 | 44.5 | 103.1 | 103.4 | 95.2 | 115.8 | 44.4 | 33 | 2059.2 | 1225.3 | 1004.7 | 2352.1 | 1286.6 | 1200 | 1.142 | 1.05 | 1.194 | 0.972 | 0.95 | 0.963 | 8.72 | 8.99 | 9.33 | 0.875 | 0.838 | 0.84 | 6.87 | 8.53 | 7.05 | 0.867 | 0.889 | 0.736 | -9.08 | -8.2 | 8.87 | 0.894 | 0.967 | 0.945 | 6.96 | -7.89 | -7.45 | Very Poor_Mixed | 1004.7 | 1200 | 1.05 | 0.972 | 9.33 | 0.967 | 9.08 | 0.0989 | 0.6347 | 0.1642 | 0.2826 | 1 | 0.0742 | 0.173 | 0.333 | 0.333 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1281 | 533.8 | 364.1 | 94.4 | 89.1 | 2.9 | 685.2 | 3959.7 | 22.8 | 49 | 83.8 | 82.8 | 76.7 | 91.4 | 36.9 | 19.1 | 5333 | 5365.2 | 4608.2 | 7932 | 7697.3 | 6664.1 | 1.487 | 1.435 | 1.446 | 0.686 | 0.688 | 0.661 | 4.79 | 4.64 | 5.03 | 0.518 | 0.581 | 0.57 | -2 | 2.82 | 2.75 | 0.501 | 0.548 | 0.55 | 3.48 | 2.91 | 2.2 | 0.546 | 0.581 | 0.512 | 2 | -2.52 | 3.74 | Critical_Oil | 4608.2 | 6664.1 | 1.435 | 0.688 | 5.03 | 0.581 | 3.74 | 0.6982 | 0.0091 | 0.7045 | 0.7749 | 1 | 0.5202 | 0.7869 | 0.6593 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1282 | 819 | 488.7 | 103 | 120.1 | 17.7 | 757.3 | 5101.7 | 47 | 33.2 | 88.6 | 88.7 | 85.1 | 97.7 | 40.8 | 23.4 | 5874.8 | 6453.9 | 6563.3 | 8921.5 | 10494.8 | 11352.3 | 1.519 | 1.626 | 1.73 | 0.838 | 0.712 | 0.691 | -7.63 | 5.3 | -6.05 | 0.682 | 0.719 | 0.677 | 6.09 | 6.43 | 4.09 | 0.624 | 0.648 | 0.715 | 4.94 | 5.37 | 5.06 | 0.666 | 0.581 | 0.674 | -3.62 | 3.77 | 3.44 | Poor_Mixed | 5874.8 | 8921.5 | 1.519 | 0.838 | 7.63 | 0.719 | 6.43 | 0.4575 | 0.7556 | 0.5173 | 0.6348 | 1 | 0.3774 | 0.4962 | 0.5907 | 0.5907 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1283 | 1589.5 | 907.2 | 143.4 | 192.5 | 33.5 | 1336.5 | 7990.8 | 51.7 | 26.1 | 75.7 | 80.6 | 70.6 | 83 | 36.9 | 16.8 | 8003.7 | 7693.1 | 8401.9 | 14116.4 | 13608.6 | 15955.7 | 1.764 | 1.769 | 1.899 | 0.616 | 0.71 | 1.812 | 4.18 | 4.85 | -3.29 | 0.571 | 0.635 | 0.626 | 4.73 | 3.92 | -3.07 | 0.648 | 0.594 | 0.648 | 4.82 | 3.9 | 3.09 | 0.657 | 0.565 | 0.583 | 4.16 | -3.98 | -3.93 | Critical_DGA | 7693.1 | 13608.6 | 1.764 | 1.812 | 4.85 | 0.657 | 4.82 | 0.077 | 0.852 | 0.8913 | 0.8436 | 1 | 0.4926 | 0.5965 | 0.5892 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
1284 | 509.5 | 329 | 88.4 | 75.3 | 10.7 | 623.6 | 4567.8 | 54 | 27.3 | 85.9 | 84.3 | 75 | 91.6 | 37.6 | 19.9 | 6719.4 | 6575.6 | 7190.5 | 11361.7 | 10756.2 | 12584.4 | 1.691 | 1.636 | 1.75 | 0.639 | 0.724 | 0.685 | 3.94 | 5.31 | 5.13 | 0.605 | 0.582 | 0.612 | 4.18 | 3.13 | -3.22 | 0.567 | 0.655 | 0.626 | 3.89 | 4.78 | 4.68 | 0.639 | 0.635 | 0.559 | 4.63 | 3.92 | -4.39 | Fair_Mixed | 6575.6 | 10756.2 | 1.636 | 0.724 | 5.31 | 0.655 | 4.78 | 0.6332 | 0.8337 | 0.6853 | 0.7499 | 1 | 0.5193 | 0.5989 | 0.7049 | 0.7049 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1285 | 1050.8 | 601.2 | 104 | 117.5 | 16.4 | 807.1 | 4881.3 | 41.5 | 37.2 | 93.8 | 91.5 | 83.6 | 101.2 | 41.3 | 21.9 | 6507.6 | 4608.1 | 4775.4 | 10264 | 6751.6 | 6942.4 | 1.577 | 1.465 | 1.454 | 0.745 | 0.752 | 0.74 | 5.27 | 5.7 | -6.25 | 0.736 | 0.71 | 0.725 | 4.33 | 4 | 5.42 | 0.781 | 0.68 | 0.727 | -3.66 | 4.41 | 4.57 | 0.765 | 0.705 | 0.646 | -4.04 | -4.87 | 6.66 | Poor_Mixed | 4608.1 | 6751.6 | 1.454 | 0.752 | 6.25 | 0.781 | 6.66 | 0.4328 | 0.7098 | 0.4534 | 0.6852 | 1 | 0.4072 | 0.4333 | 0.568 | 0.568 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1286 | 441.5 | 361.8 | 92.6 | 97.5 | 1 | 633.3 | 4116.2 | 56 | 25.2 | 84.4 | 84.2 | 75.7 | 90.1 | 36.7 | 13.9 | 7807.1 | 7392.4 | 7431.3 | 13823.3 | 12607.6 | 12687.5 | 1.771 | 1.705 | 1.707 | 0.99 | 0.954 | 1.369 | 9.78 | 9.26 | -9.05 | 0.548 | 0.552 | 0.586 | -2.78 | 2 | 3.05 | 0.531 | 0.5 | 0.528 | -2.45 | 2 | -2.8 | 0.577 | 0.528 | 0.5 | 3.43 | 2.61 | 2.87 | Critical_Winding_TD_Cap | 7392.4 | 12607.6 | 1.705 | 1.369 | 9.78 | 0.586 | 3.43 | 0.7917 | 0.8666 | 0.7042 | 0.9219 | 1 | 0.0438 | 0.8114 | 0.7306 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_TV_TanDelta_pct
1287 | 560.4 | 423.1 | 87.7 | 145.5 | 5.2 | 746.3 | 4676.6 | 54.6 | 25.3 | 109.3 | 109.1 | 97 | 119.2 | 44.9 | 17.5 | 8914.9 | 9172.7 | 411.1 | 16551.9 | 18345.5 | 664.8 | 1.857 | 2 | 1.617 | 0.588 | 0.565 | 0.603 | 3.52 | 3.36 | 4.09 | 0.597 | 0.619 | 0.56 | 3.58 | -4.23 | -3.28 | 0.645 | 0.601 | 0.586 | 4.16 | -2.78 | -3.55 | 0.606 | 0.561 | 0.612 | -3.11 | -4.94 | 3.34 | Critical_Thermal | 411.1 | 664.8 | 1.617 | 0.603 | 4.09 | 0.645 | 4.94 | 0.5862 | 0.865 | 0.068 | 0.8232 | 0.85 | 0.6938 | 0.6315 | 0.6451 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1288 | 799 | 515.3 | 98.2 | 106.4 | 13.1 | 788.5 | 5394 | 56.5 | 22.8 | 77.6 | 78.4 | 71.1 | 81.5 | 35.6 | 16.8 | 10000 | 9318.5 | 9469.7 | 19743.4 | 17905 | 18060.2 | 1.974 | 1.921 | 1.907 | 0.595 | 0.548 | 0.574 | -2.75 | -2.77 | 2.12 | 0.561 | 0.5 | 0.517 | 2.02 | 2.51 | 2.61 | 0.562 | 0.542 | 0.522 | -2.05 | 2 | 2 | 0.509 | 0.543 | 0.5 | -3.4 | 2.19 | 2 | Poor_DGA | 9318.5 | 17905 | 1.907 | 0.595 | 2.77 | 0.562 | 3.4 | 0.4975 | 0.9108 | 0.8971 | 0.8436 | 1 | 0.7873 | 0.8574 | 0.7901 | 0.7901 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1289 | 1134 | 787.6 | 113.3 | 153.3 | 23.6 | 964.8 | 6905.9 | 56.7 | 21.9 | 81.3 | 80.1 | 72.6 | 86.8 | 36.5 | 11.7 | 9532.7 | 8841.5 | 8945.2 | 18613.1 | 16362.8 | 16614.7 | 1.953 | 1.851 | 1.857 | 0.625 | 0.562 | 0.554 | 3.24 | 2.59 | 3.63 | 0.572 | 0.556 | 0.51 | 2.84 | 3.2 | 2.66 | 0.55 | 0.5 | 0.566 | 2 | -2.67 | -3.01 | 0.547 | 0.531 | 0.566 | 2 | 2.78 | 2.8 | Poor_DGA | 8841.5 | 16362.8 | 1.851 | 0.625 | 3.63 | 0.572 | 3.2 | 0.2825 | 0.9307 | 0.8034 | 0.9724 | 1 | 0.7356 | 0.7911 | 0.7166 | 0.7166 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1290 | 397.4 | 294.1 | 81 | 70.7 | 1.6 | 517.3 | 2984.7 | 54.2 | 65.9 | 76.8 | 80.3 | 74 | 84.8 | 36.1 | 18.6 | 1385.6 | 1568.4 | 1912.7 | 1555.9 | 1904.9 | 2311.3 | 1.123 | 1.215 | 1.208 | 0.702 | 0.73 | 0.68 | 4.88 | 5.11 | 4.72 | 0.593 | 0.574 | 0.69 | 3.8 | 3.12 | 3.56 | 0.563 | 0.559 | 0.601 | -2.96 | 3.61 | -2.99 | 0.557 | 0.666 | 0.629 | 2.76 | -2.58 | -3.76 | Critical_IR_PI | 1385.6 | 1555.9 | 1.123 | 0.73 | 5.11 | 0.69 | 3.8 | 0.8155 | 0.5833 | 0.8441 | 0.7902 | 1 | 0.4914 | 0.6455 | 0.7428 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1291 | 1565.5 | 886.2 | 137.4 | 180 | 31.7 | 1291.7 | 7472.7 | 36 | 45 | 104.2 | 105.8 | 93.2 | 111.8 | 44.7 | 32.5 | 1756.5 | 830.1 | 2525.3 | 2113.6 | 1200 | 3048 | 1.203 | 1.446 | 1.207 | 0.89 | 0.925 | 0.955 | 8.21 | 8.63 | 8.65 | 0.796 | 0.911 | 0.733 | 9.2 | -5.69 | 9.26 | 0.918 | 0.972 | 0.748 | 8.99 | -7.61 | -6.72 | 0.819 | 0.864 | 0.821 | -6.43 | -5.32 | 7.64 | Very Poor_Mixed | 830.1 | 1200 | 1.203 | 0.955 | 8.65 | 0.972 | 9.26 | 0.1154 | 0.6299 | 0.1735 | 0.302 | 1 | 0.1265 | 0.2163 | 0.3535 | 0.3535 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1292 | 1067.8 | 630.1 | 115.1 | 139.7 | 25 | 945.9 | 5955.4 | 53.8 | 25 | 80.9 | 78.6 | 76.1 | 84.5 | 36.5 | 11.9 | 9056.5 | 9840.6 | 9523.5 | 16602.5 | 19103.1 | 17570 | 1.833 | 1.941 | 1.845 | 0.542 | 0.58 | 0.553 | 2.29 | 3.48 | -3.29 | 0.523 | 0.545 | 0.547 | 2.91 | 3.45 | 2.81 | 0.535 | 0.536 | 0.549 | 2.78 | -2.9 | -2.86 | 0.545 | 0.533 | 0.571 | 3.18 | 2.33 | 2.03 | Poor_DGA | 9056.5 | 16602.5 | 1.833 | 0.58 | 3.48 | 0.571 | 3.45 | 0.3216 | 0.87 | 0.8041 | 0.9682 | 1 | 0.7748 | 0.7747 | 0.7215 | 0.7215 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1293 | 1526.6 | 941.7 | 138.3 | 167.9 | 30.8 | 1259.2 | 8122.7 | 35.5 | 43.1 | 105.7 | 103.2 | 92.3 | 113.5 | 43.4 | 32.3 | 2753.1 | 3377.5 | 2922.6 | 3700.3 | 4416 | 3488.4 | 1.344 | 1.307 | 1.194 | 0.946 | 0.907 | 0.906 | 9.51 | 8.38 | -8.14 | 0.78 | 0.891 | 0.898 | 6.25 | 5.42 | -5.98 | 0.854 | 0.907 | 0.821 | -7.16 | 7.82 | 7.21 | 0.858 | 0.906 | 0.84 | -7.15 | 7.19 | 7.26 | Very Poor_Mixed | 2753.1 | 3488.4 | 1.194 | 0.946 | 9.51 | 0.907 | 7.82 | 0.121 | 0.6484 | 0.1857 | 0.3098 | 1 | 0.1199 | 0.2153 | 0.3577 | 0.3577 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1294 | 981.5 | 608.8 | 109.2 | 136 | 16.6 | 858.8 | 6382.3 | 44.7 | 35.2 | 94 | 96.3 | 85.3 | 99.5 | 40.5 | 26.6 | 5580.9 | 4964.8 | 5891.2 | 8466.1 | 7490.1 | 9700.9 | 1.517 | 1.509 | 1.647 | 0.731 | 0.76 | 0.769 | 5.4 | -5.45 | -6.26 | 0.797 | 0.624 | 0.71 | 6.17 | 5.01 | 5.4 | 0.747 | 0.716 | 0.666 | 6.07 | -6.22 | 7 | 0.694 | 0.703 | 0.645 | -5.4 | 5.35 | 4.32 | Poor_Mixed | 4964.8 | 7490.1 | 1.509 | 0.769 | 6.26 | 0.797 | 7 | 0.3923 | 0.7322 | 0.4254 | 0.5228 | 1 | 0.4028 | 0.4201 | 0.5466 | 0.5466 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1295 | 823.1 | 498.7 | 107.9 | 121 | 15.4 | 721.1 | 5239.8 | 42.9 | 34.1 | 92 | 88.7 | 81 | 102 | 40.2 | 27.4 | 5243.3 | 6491.4 | 6127.8 | 7389.2 | 10311 | 9848 | 1.409 | 1.588 | 1.607 | 0.745 | 0.725 | 0.802 | 6.02 | 6.38 | 6.18 | 0.603 | 0.648 | 0.699 | 5.28 | -4.47 | -5.68 | 0.66 | 0.758 | 0.679 | 4.13 | 4.37 | 4.89 | 0.624 | 0.7 | 0.635 | 5.17 | 5.02 | 5.77 | Poor_Mixed | 5243.3 | 7389.2 | 1.409 | 0.802 | 6.38 | 0.758 | 5.77 | 0.4699 | 0.7449 | 0.5032 | 0.4938 | 1 | 0.373 | 0.4843 | 0.5813 | 0.5813 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1296 | 145.3 | 124.2 | 75.9 | 73.8 | 3 | 412.8 | 2901 | 57.1 | 24.6 | 75.1 | 75 | 71.3 | 82.5 | 35.3 | 15.7 | 8758.8 | 9097.2 | 8791.6 | 16068.1 | 16857.8 | 17064.8 | 1.835 | 1.853 | 1.941 | 0.528 | 0.544 | 0.562 | -2.76 | -2.84 | -2.67 | 0.579 | 0.565 | 0.511 | 2 | -2.5 | 2.11 | 0.568 | 0.569 | 0.5 | 2 | 2 | 3.01 | 0.538 | 0.54 | 0.501 | -2.06 | 2.17 | -2.03 | Good_Mixed | 8758.8 | 16068.1 | 1.835 | 0.562 | 2.84 | 0.579 | 3.01 | 0.8414 | 0.8768 | 0.9673 | 0.8746 | 1 | 0.8132 | 0.8304 | 0.8793 | 0.8793 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1297 | 510.5 | 322.4 | 85.8 | 88.8 | 2.5 | 628 | 4691.9 | 30.6 | 49.4 | 80.5 | 131.2 | 74.3 | 88.5 | 36.9 | 14.5 | 4917.3 | 3773.3 | 4976.3 | 7274 | 5578.8 | 7051.9 | 1.479 | 1.478 | 1.417 | 0.671 | 0.601 | 0.687 | 3.94 | -3.1 | 4.11 | 0.575 | 0.563 | 0.642 | -2.92 | -3.54 | 3.06 | 0.562 | 0.561 | 0.614 | 3.51 | -3.52 | 2.59 | 0.561 | 0.541 | 0.583 | -3.39 | 2.56 | 4.02 | Critical_Oil | 3773.3 | 5578.8 | 1.417 | 0.687 | 4.11 | 0.642 | 4.02 | 0.7214 | 0.5888 | 0.5944 | 0.9067 | 1 | 0.6139 | 0.6856 | 0.7251 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | Moisture_PPM
1298 | 855.7 | 539.5 | 97.2 | 112.1 | 17.5 | 783.9 | 5703.5 | 46.9 | 31.7 | 89.8 | 92.7 | 81.3 | 96.7 | 39.7 | 22.3 | 5648.7 | 5668.7 | 5785.9 | 8576.6 | 8952.8 | 9340.5 | 1.518 | 1.579 | 1.614 | 0.717 | 0.746 | 0.775 | 5.75 | 6.08 | 6.1 | 0.624 | 0.633 | 0.672 | 4.48 | -5.69 | 5.12 | 0.693 | 0.647 | 0.724 | 5.21 | 4.29 | 4.93 | 0.64 | 0.663 | 0.678 | 4.5 | 3.62 | 5.54 | Poor_Mixed | 5648.7 | 8576.6 | 1.518 | 0.775 | 6.1 | 0.724 | 5.69 | 0.4525 | 0.7741 | 0.5191 | 0.6719 | 1 | 0.3941 | 0.4929 | 0.5954 | 0.5954 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1299 | 946.2 | 461.6 | 105.5 | 114.3 | 14.4 | 784.9 | 5553 | 47.1 | 32.4 | 92.6 | 90.8 | 81.8 | 99.3 | 39.9 | 25.7 | 5068.8 | 6989.5 | 5609.1 | 8035.6 | 12232.1 | 8612.2 | 1.585 | 1.75 | 1.535 | 0.704 | 0.72 | 0.648 | 5.67 | 4.98 | 4.37 | 0.738 | 0.647 | 0.695 | 6.49 | 5.5 | -5.23 | 0.64 | 0.605 | 0.725 | -5.21 | 5.05 | 4.69 | 0.658 | 0.776 | 0.726 | 5 | 4.91 | -3.73 | Poor_Mixed | 5068.8 | 8035.6 | 1.535 | 0.72 | 5.67 | 0.776 | 6.49 | 0.4682 | 0.7654 | 0.4956 | 0.5549 | 1 | 0.4989 | 0.4534 | 0.5976 | 0.5976 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1300 | 1441.8 | 778.8 | 128.1 | 159.5 | 27 | 1142.4 | 7259.8 | 36.4 | 44.8 | 100.2 | 103.6 | 90.8 | 109.1 | 42.2 | 29.4 | 2711.2 | 1666.6 | 2535.2 | 3102 | 1920.5 | 3061.9 | 1.144 | 1.152 | 1.208 | 0.924 | 0.939 | 0.888 | 8.34 | 9.2 | -9.14 | 0.766 | 0.783 | 0.74 | -4.95 | 7.83 | -5.71 | 0.809 | 0.877 | 0.783 | -6.47 | -5.29 | 7.52 | 0.913 | 0.757 | 0.764 | -7.52 | 8.3 | -6.05 | Very Poor_Mixed | 1666.6 | 1920.5 | 1.144 | 0.939 | 9.2 | 0.913 | 8.3 | 0.2019 | 0.6318 | 0.2536 | 0.4201 | 1 | 0.1107 | 0.2817 | 0.3989 | 0.3989 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1301 | 133.6 | 162.8 | 70.9 | 62.2 | 2.8 | 350 | 3108.9 | 55.4 | 24 | 75.1 | 75 | 70 | 80.5 | 35 | 12.6 | 9972.8 | 9547.4 | 10000 | 19617.1 | 19094.8 | 19642.9 | 1.967 | 2 | 1.964 | 0.552 | 0.5 | 0.572 | 3.15 | 2.04 | -2.63 | 0.552 | 0.583 | 0.532 | 2.2 | 2 | 2.44 | 0.566 | 0.5 | 0.5 | 2.82 | 2.46 | 2.44 | 0.615 | 0.531 | 0.518 | 3.29 | 2.36 | 2 | Fair_Bushing_TD_Cap | 9547.4 | 19094.8 | 1.964 | 0.572 | 3.15 | 0.615 | 3.29 | 0.8742 | 0.8875 | 0.9944 | 0.953 | 1 | 0.8489 | 0.8143 | 0.8976 | 0.8976 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1302 | 169.8 | 128.3 | 70.4 | 52.9 | 3.6 | 350 | 2892.6 | 58.2 | 20.9 | 75 | 76.5 | 70 | 80 | 35 | 13.8 | 8791.6 | 9243.5 | 9719.6 | 16481.9 | 17771.9 | 18796.5 | 1.875 | 1.923 | 1.934 | 0.523 | 0.5 | 0.555 | 2.54 | 2 | 3.18 | 0.505 | 0.5 | 0.5 | 2.31 | 2.27 | 2.53 | 0.523 | 0.53 | 0.5 | 2 | -2.13 | 2.59 | 0.568 | 0.558 | 0.523 | 2.45 | -3.27 | 2.9 | Good_Mixed | 8791.6 | 16481.9 | 1.875 | 0.555 | 3.18 | 0.568 | 3.27 | 0.8766 | 0.9574 | 0.9765 | 0.9244 | 1 | 0.8783 | 0.8683 | 0.9171 | 0.9171 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1303 | 344.7 | 227.8 | 75.6 | 72.7 | 70.9 | 485.5 | 3239.7 | 57.9 | 20.4 | 81.3 | 85.6 | 76.7 | 87.4 | 37.1 | 15 | 2789 | 2304.4 | 2942.1 | 3324.2 | 2732.1 | 3579.4 | 1.192 | 1.186 | 1.217 | 0.664 | 0.668 | 0.682 | -4.79 | 5.11 | -4.9 | 0.588 | 0.515 | 0.588 | 2.84 | 3.01 | -2.01 | 0.513 | 0.546 | 0.522 | 2 | -2.55 | -3 | 0.517 | 0.5 | 0.552 | -2.85 | -2.64 | 2.11 | Critical_IR_PI | 2304.4 | 2732.1 | 1.186 | 0.682 | 5.11 | 0.588 | 3.01 | 0.5644 | 0.9748 | 0.7221 | 0.8935 | 1 | 0.5205 | 0.8157 | 0.7547 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1304 | 935.7 | 548.3 | 99.3 | 122.2 | 19.7 | 838 | 5689.2 | 43.8 | 35.7 | 89.7 | 95.3 | 81.6 | 98.4 | 40.8 | 25.4 | 5749 | 5543.4 | 6830.5 | 8822.6 | 8765.8 | 11154.5 | 1.535 | 1.581 | 1.633 | 0.746 | 0.747 | 0.704 | 6.1 | -5.48 | 5.01 | 0.693 | 0.704 | 0.685 | 3.98 | -4.27 | 4.68 | 0.758 | 0.667 | 0.671 | 5.45 | -5.65 | 4.99 | 0.672 | 0.643 | 0.65 | 4.99 | 5.08 | -4.55 | Poor_Mixed | 5543.4 | 8765.8 | 1.535 | 0.747 | 6.1 | 0.758 | 5.65 | 0.4138 | 0.7265 | 0.4859 | 0.5655 | 1 | 0.4307 | 0.4683 | 0.5721 | 0.5721 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1305 | 827.4 | 496 | 103.1 | 133.7 | 19.8 | 846.3 | 5679.5 | 46.1 | 33.1 | 93.3 | 94.7 | 84.2 | 101.7 | 40 | 24.5 | 6346.2 | 4799.4 | 5054 | 9697.6 | 7180.9 | 7052.9 | 1.528 | 1.496 | 1.396 | 0.713 | 0.745 | 0.778 | 5.49 | 6.56 | 5.46 | 0.747 | 0.583 | 0.676 | 5.19 | 5.79 | 4.51 | 0.647 | 0.727 | 0.748 | 4.62 | 6.07 | 4.61 | 0.741 | 0.686 | 0.664 | 4.18 | -5.45 | 5.78 | Poor_Mixed | 4799.4 | 7052.9 | 1.396 | 0.778 | 6.56 | 0.748 | 6.07 | 0.4131 | 0.7568 | 0.4386 | 0.597 | 1 | 0.4027 | 0.4509 | 0.5654 | 0.5654 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1306 | 207.5 | 185.1 | 76.2 | 70.9 | 3.4 | 450 | 2892.3 | 58.1 | 21.7 | 75.2 | 77.3 | 70.9 | 80.8 | 35 | 10 | 8906.8 | 9048.6 | 10000 | 16498.4 | 17913.3 | 19763.8 | 1.852 | 1.98 | 1.976 | 0.636 | 0.686 | 0.655 | 4.31 | 5.17 | -4.01 | 0.545 | 0.522 | 0.516 | -2.38 | 2.03 | 3.16 | 0.537 | 0.5 | 0.523 | 2.78 | -3.14 | 2.07 | 0.508 | 0.5 | 0.566 | 2 | 2 | 2.47 | Fair_Winding_TD_Cap | 8906.8 | 16498.4 | 1.852 | 0.686 | 5.17 | 0.566 | 3.16 | 0.816 | 0.9355 | 0.9463 | 1 | 1 | 0.559 | 0.8604 | 0.854 | 0.854 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1307 | 943.5 | 451 | 100.4 | 117.2 | 17.6 | 835.7 | 5147.2 | 49.1 | 30.7 | 92.7 | 89.3 | 84.9 | 97.6 | 39.4 | 24.4 | 5636.3 | 4717.1 | 6344.6 | 8896.7 | 7442.6 | 9637.9 | 1.578 | 1.578 | 1.519 | 0.718 | 0.771 | 0.738 | 5.29 | 5.78 | 5.55 | 0.736 | 0.657 | 0.703 | 3.45 | 3.7 | 4.75 | 0.596 | 0.681 | 0.679 | -5.23 | 4.58 | 3.74 | 0.641 | 0.624 | 0.605 | 3.84 | 4.9 | -5.27 | Poor_Mixed | 4717.1 | 7442.6 | 1.519 | 0.771 | 5.78 | 0.736 | 5.27 | 0.4469 | 0.7868 | 0.4971 | 0.6005 | 1 | 0.4213 | 0.5189 | 0.5983 | 0.5983 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1308 | 381.6 | 268.7 | 87.5 | 86.6 | 3.9 | 587.8 | 4420.6 | 57.9 | 24.5 | 83 | 82.4 | 75.4 | 90.4 | 37.8 | 14.7 | 323.4 | 7663.3 | 7873.5 | 549.4 | 13495.7 | 13582.3 | 1.699 | 1.761 | 1.725 | 0.956 | 0.979 | 0.99 | -9.53 | 9.82 | -9.62 | 0.592 | 0.5 | 0.533 | 2.61 | -3.23 | -2 | 0.522 | 0.608 | 0.566 | -2.37 | 2.83 | 2 | 0.563 | 0.5 | 0.559 | 2.72 | 2.51 | 2.29 | Critical_Winding_TD_Cap | 323.4 | 549.4 | 1.699 | 0.99 | 9.82 | 0.608 | 3.23 | 0.7215 | 0.8786 | 0.7233 | 0.9014 | 0.85 | 0.0333 | 0.7991 | 0.6877 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1309 | 1649.9 | 970.1 | 141.4 | 176.3 | 30.4 | 1286.3 | 8160.9 | 33.1 | 44.2 | 103.4 | 102.6 | 92.8 | 112.1 | 44.3 | 31.6 | 2496.3 | 2194.3 | 2818.7 | 3189.7 | 2726.2 | 3633.2 | 1.278 | 1.242 | 1.289 | 0.9 | 0.944 | 0.875 | -8.64 | -8.88 | 8.11 | 0.813 | 0.779 | 0.795 | -7.73 | 5.56 | 7.14 | 0.731 | 0.795 | 0.785 | 6.9 | -4.82 | 5.56 | 0.819 | 0.761 | 0.8 | 4.37 | 8.24 | -6.9 | Very Poor_Mixed | 2194.3 | 2726.2 | 1.242 | 0.944 | 8.88 | 0.819 | 8.24 | 0.0979 | 0.6376 | 0.1996 | 0.3368 | 1 | 0.1359 | 0.302 | 0.3712 | 0.3712 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1310 | 147 | 185.9 | 72.5 | 61.6 | 1.3 | 397.1 | 2714.7 | 55.4 | 23.6 | 77.7 | 76.1 | 71.5 | 84.5 | 36 | 10 | 4378.4 | 4713.1 | 4018.1 | 6066 | 6085.2 | 5776.6 | 1.385 | 1.291 | 1.438 | 0.608 | 0.628 | 0.614 | -3.7 | 3.96 | 4.36 | 0.538 | 0.538 | 0.529 | 2.18 | -2.09 | -2 | 0.537 | 0.538 | 0.5 | 2.03 | 2 | -2.3 | 0.526 | 0.5 | 0.527 | -2 | -2.69 | 2.61 | Poor_IR_PI | 4018.1 | 5776.6 | 1.291 | 0.628 | 4.36 | 0.538 | 2.69 | 0.9073 | 0.895 | 0.9002 | 1 | 1 | 0.6333 | 0.8635 | 0.8783 | 0.8783 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1311 | 100 | 133.4 | 68.7 | 58 | 1 | 1625.5 | 22248.7 | 60 | 20.2 | 76.4 | 76.8 | 71.1 | 81.5 | 36 | 15.3 | 8207.6 | 7832.6 | 9143 | 14461.8 | 13937.7 | 17838.5 | 1.762 | 1.779 | 1.951 | 0.541 | 0.59 | 0.559 | -2.61 | -2.57 | 3.54 | 0.541 | 0.654 | 0.572 | 3.21 | 2 | 3.01 | 0.525 | 0.626 | 0.955 | 3.48 | 4.48 | -9.16 | 0.576 | 0.594 | 0.533 | 3.67 | 2.93 | 2.19 | Critical_Bushing_TD_Cap | 7832.6 | 13937.7 | 1.762 | 0.59 | 3.54 | 0.955 | 9.16 | 0.7587 | 0.984 | 0.9251 | 0.8855 | 1 | 0.7749 | 0.6285 | 0.8261 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
1312 | 853.8 | 497.4 | 103.7 | 115.2 | 20 | 836.1 | 5304.6 | 45.2 | 35.8 | 91.9 | 91.2 | 80.5 | 94.9 | 40.3 | 23.2 | 6021.6 | 5879.6 | 5367.4 | 9729.3 | 8982 | 8030.3 | 1.616 | 1.528 | 1.496 | 0.688 | 0.719 | 0.725 | 5.72 | 5.97 | 5.59 | 0.652 | 0.693 | 0.676 | 3.61 | -4.02 | -4.39 | 0.626 | 0.657 | 0.616 | 4.01 | 4.55 | 4.7 | 0.675 | 0.678 | 0.6 | -4.19 | 4.75 | 4.56 | Poor_Mixed | 5367.4 | 8030.3 | 1.496 | 0.725 | 5.97 | 0.693 | 4.75 | 0.4321 | 0.7253 | 0.5253 | 0.6416 | 1 | 0.4369 | 0.5267 | 0.5957 | 0.5957 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1313 | 353 | 257.6 | 80.6 | 79.1 | 8.5 | 645 | 3854.3 | 56.9 | 24.3 | 80.2 | 79 | 76.1 | 87 | 35.9 | 17.7 | 7652.1 | 9109.6 | 8382 | 13794.1 | 17110.4 | 15234.4 | 1.803 | 1.878 | 1.818 | 0.608 | 0.594 | 0.639 | 3 | 3.8 | 3.88 | 0.613 | 0.585 | 0.612 | -3.24 | 2.52 | 2.9 | 0.537 | 0.635 | 0.583 | 3.93 | -3.41 | -3.11 | 0.597 | 0.566 | 0.594 | 3.62 | 4.2 | -3.72 | Fair_Mixed | 7652.1 | 13794.1 | 1.803 | 0.639 | 3.88 | 0.635 | 4.2 | 0.6791 | 0.8821 | 0.7967 | 0.8173 | 1 | 0.6653 | 0.6548 | 0.7672 | 0.7672 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1314 | 262.8 | 189.5 | 76.5 | 66 | 1.3 | 458.5 | 3383.6 | 57.2 | 23.2 | 79.1 | 79 | 73.6 | 83.2 | 35.7 | 12.4 | 9695 | 9855.4 | 9531.7 | 19390 | 18649.4 | 17440.5 | 2 | 1.892 | 1.83 | 0.824 | 0.761 | 0.778 | 7.39 | 6.21 | 5.94 | 0.533 | 0.535 | 0.609 | 2.81 | 3.21 | 3.14 | 0.532 | 0.553 | 0.569 | 2.68 | 2.63 | -2.27 | 0.543 | 0.542 | 0.537 | -4.1 | 3.46 | 3.14 | Poor_Winding_TD_Cap | 9531.7 | 17440.5 | 1.83 | 0.824 | 7.39 | 0.609 | 4.1 | 0.8708 | 0.9027 | 0.8456 | 0.9575 | 1 | 0.3308 | 0.7484 | 0.7995 | 0.7995 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
1315 | 1611.4 | 814.5 | 136.1 | 174.2 | 28.2 | 1304.6 | 7812.8 | 32.9 | 45.6 | 101.6 | 105 | 93.2 | 114.7 | 44.2 | 29.6 | 2714.5 | 2580.5 | 3585.2 | 3146.8 | 2959.1 | 4538.1 | 1.159 | 1.147 | 1.266 | 0.92 | 0.864 | 0.91 | -8.34 | 8.16 | 8.27 | 0.746 | 0.914 | 0.855 | 7.84 | -8.21 | -7.83 | 0.724 | 0.803 | 0.858 | 6.11 | -5.35 | 6.3 | 0.941 | 0.722 | 0.771 | 6.74 | 8.67 | 8.29 | Very Poor_Mixed | 2580.5 | 2959.1 | 1.147 | 0.92 | 8.34 | 0.941 | 8.67 | 0.1363 | 0.6241 | 0.1819 | 0.4126 | 1 | 0.1563 | 0.2474 | 0.3742 | 0.3742 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1316 | 754.8 | 504.4 | 100.8 | 122.4 | 19.5 | 766.3 | 5898.7 | 45.7 | 33.1 | 93.4 | 92.4 | 81.6 | 99.3 | 39.2 | 24.9 | 6316.3 | 4613.9 | 5246.8 | 10800.6 | 7040.9 | 8424.1 | 1.71 | 1.526 | 1.606 | 0.747 | 0.642 | 0.76 | -6.24 | 4.54 | 5.5 | 0.722 | 0.719 | 0.678 | 3.78 | 3.55 | -4.61 | 0.587 | 0.678 | 0.72 | -4.73 | 5.82 | -3.29 | 0.599 | 0.704 | 0.593 | -4.39 | -4.48 | 5.76 | Poor_Mixed | 4613.9 | 7040.9 | 1.526 | 0.76 | 6.24 | 0.722 | 5.82 | 0.4398 | 0.7568 | 0.4859 | 0.5831 | 1 | 0.4533 | 0.5063 | 0.5931 | 0.5931 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1317 | 756.1 | 534.2 | 103 | 118.4 | 18.6 | 821.3 | 4637 | 46.7 | 31.5 | 88.8 | 85.6 | 79.9 | 93.4 | 38.9 | 25.3 | 5957.8 | 5818.2 | 6303.4 | 9255.2 | 9216.9 | 10413.9 | 1.553 | 1.584 | 1.652 | 0.775 | 0.767 | 0.746 | 6.16 | -6.28 | 6.29 | 0.668 | 0.744 | 0.793 | -5.38 | 4.36 | -5.36 | 0.77 | 0.681 | 0.703 | -4.26 | 5.69 | 6.59 | 0.672 | 0.664 | 0.693 | 4.59 | 3.35 | 4.97 | Poor_Mixed | 5818.2 | 9216.9 | 1.553 | 0.775 | 6.29 | 0.793 | 6.59 | 0.4499 | 0.7766 | 0.6043 | 0.569 | 1 | 0.3652 | 0.4342 | 0.5838 | 0.5838 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1318 | 990 | 552.5 | 109.1 | 130.5 | 19.6 | 839.2 | 5706.4 | 47.2 | 31.3 | 91.7 | 91.7 | 83.8 | 101.6 | 40.3 | 26.8 | 5096.5 | 4830.9 | 6185.9 | 8003.7 | 7163.8 | 9910 | 1.57 | 1.483 | 1.602 | 0.74 | 0.702 | 0.767 | -5.95 | -5.9 | 6.54 | 0.677 | 0.64 | 0.659 | -3.97 | -3.92 | 5.19 | 0.684 | 0.701 | 0.699 | 5.41 | 5.2 | 4.15 | 0.622 | 0.691 | 0.691 | 4.28 | 5.33 | 4.45 | Poor_Mixed | 4830.9 | 7163.8 | 1.483 | 0.767 | 6.54 | 0.701 | 5.41 | 0.3945 | 0.7791 | 0.4688 | 0.5156 | 1 | 0.3942 | 0.4861 | 0.5674 | 0.5674 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1319 | 1335.2 | 841.2 | 131.4 | 170.9 | 23.1 | 1195.6 | 7622.9 | 56.9 | 23.4 | 80.4 | 77.6 | 75.3 | 84.6 | 37.3 | 14.9 | 10000 | 9694.9 | 8268.5 | 19745.5 | 17540.3 | 14568 | 1.975 | 1.809 | 1.762 | 0.574 | 0.571 | 0.567 | 2.36 | 2.92 | -11.68 | 0.523 | 0.568 | 0.537 | 2 | 2.12 | 2.27 | 0.51 | 0.5 | 0.535 | 2.65 | 2.84 | 2.25 | 0.535 | 0.526 | 0.555 | 3.35 | -3.54 | -2.7 | Critical_DGA | 8268.5 | 14568 | 1.762 | 0.574 | 11.68 | 0.568 | 3.54 | 0.2001 | 0.8988 | 0.8194 | 0.8962 | 1 | 0.644 | 0.8206 | 0.6825 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1320 | 154.4 | 120 | 68.9 | 58.5 | 1 | 354.1 | 2808.2 | 58 | 23.5 | 77.4 | 75 | 71.2 | 81.5 | 35.3 | 15.2 | 9745.2 | 9756 | 9014.1 | 18870.9 | 19461.5 | 18028.1 | 1.936 | 1.995 | 2 | 0.562 | 0.567 | 0.578 | 3.06 | 2.31 | 3.06 | 0.553 | 0.513 | 0.572 | 2.04 | -2.6 | 3.15 | 0.506 | 0.531 | 0.5 | 2.15 | 2.59 | 2 | 0.536 | 0.515 | 0.532 | -2.18 | 2.6 | 2.77 | Good_Mixed | 9014.1 | 18028.1 | 1.936 | 0.578 | 3.06 | 0.572 | 3.15 | 0.9694 | 0.8969 | 0.9429 | 0.8882 | 1 | 0.7716 | 0.8415 | 0.9082 | 0.9082 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1321 | 823.1 | 580.7 | 102.1 | 117.3 | 15.2 | 855.1 | 5877.3 | 49.4 | 32.6 | 90.6 | 93.5 | 81.9 | 100.7 | 40.2 | 23.4 | 5845.4 | 4643.1 | 5914.2 | 8481.1 | 6726.1 | 9184.4 | 1.451 | 1.449 | 1.553 | 0.775 | 0.73 | 0.711 | -6.32 | 5.25 | 4.61 | 0.632 | 0.736 | 0.576 | 4.27 | 3.54 | -4.49 | 0.651 | 0.645 | 0.727 | 5.66 | -4.25 | 4.14 | 0.635 | 0.691 | 0.638 | 4.68 | 4.17 | 4.7 | Poor_Mixed | 4643.1 | 6726.1 | 1.449 | 0.775 | 6.32 | 0.736 | 5.66 | 0.4462 | 0.7629 | 0.4817 | 0.6348 | 1 | 0.4334 | 0.5162 | 0.5966 | 0.5966 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1322 | 1743.6 | 961.9 | 146.9 | 189.8 | 58.8 | 1379 | 8272 | 56.2 | 24.7 | 83.9 | 82.2 | 76.5 | 91.8 | 38.8 | 15.4 | 6626.2 | 8215 | 6869.7 | 11130.7 | 15128.2 | 11725.5 | 1.68 | 1.842 | 1.707 | 0.591 | 0.616 | 0.683 | -4.18 | 4.28 | 5.07 | 0.556 | 0.519 | 0.52 | -2 | 2.62 | 3.43 | 0.554 | 0.57 | 0.538 | -3.12 | 2.66 | -2.1 | 0.531 | 0.515 | 0.555 | 3.81 | 3.27 | 2.9 | Critical_DGA | 6626.2 | 11130.7 | 1.68 | 0.683 | 5.07 | 0.57 | 3.81 | 0.0449 | 0.8751 | 0.697 | 0.8828 | 1 | 0.5907 | 0.7824 | 0.6136 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1323 | 294.9 | 175 | 72.7 | 54.3 | 1.6 | 462.3 | 2987.8 | 56.1 | 24.5 | 77.7 | 79.2 | 71.3 | 81.7 | 35.2 | 17.8 | 940.6 | 690 | 945 | 993.7 | 703.8 | 1058 | 1.056 | 1.02 | 1.12 | 0.702 | 0.747 | 0.669 | 15.6 | 6.1 | 5.21 | 0.56 | 0.574 | 0.592 | 3.85 | -2.83 | 2.95 | 0.577 | 0.593 | 0.539 | -3.21 | 2.92 | -2.8 | 0.579 | 0.554 | 0.538 | -3.39 | 3.35 | 3.45 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.747 | 15.6 | 0.593 | 3.85 | 0.8782 | 0.8786 | 0.8871 | 0.8143 | 0.85 | 0.3726 | 0.7051 | 0.7695 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_HV_CapChange_pct
1324 | 893.2 | 476.1 | 105.2 | 111 | 16 | 740 | 5528.2 | 45.3 | 34.3 | 90.3 | 89 | 83.7 | 99.2 | 39.8 | 25.2 | 6343.8 | 5271.4 | 6301.4 | 9944.5 | 8153.5 | 9714.2 | 1.568 | 1.547 | 1.542 | 0.806 | 0.755 | 0.742 | 7.06 | 5.71 | -5.68 | 0.657 | 0.73 | 0.693 | 4.26 | 4.68 | 6.54 | 0.664 | 0.715 | 0.729 | -5.43 | 5.38 | 4.38 | 0.732 | 0.663 | 0.735 | -5.53 | 5.91 | 6.09 | Poor_Mixed | 5271.4 | 8153.5 | 1.542 | 0.806 | 7.06 | 0.735 | 6.54 | 0.4693 | 0.7426 | 0.5115 | 0.5725 | 1 | 0.3669 | 0.427 | 0.5744 | 0.5744 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1325 | 860 | 546.1 | 106.5 | 118.3 | 19.8 | 851.3 | 6121.8 | 49.7 | 33.2 | 91.9 | 92.1 | 81.3 | 102.8 | 39.9 | 24.9 | 5901.1 | 5729.4 | 5378.6 | 9505.7 | 9318 | 8911.9 | 1.611 | 1.626 | 1.657 | 0.825 | 0.741 | 0.75 | 6.53 | 6.27 | 5.51 | 0.628 | 0.58 | 0.62 | 3.66 | 5.33 | -5.42 | 0.735 | 0.567 | 0.661 | 5.78 | 5.27 | 4.17 | 0.697 | 0.628 | 0.684 | 3.72 | -4.58 | 3.64 | Poor_Mixed | 5378.6 | 8911.9 | 1.611 | 0.825 | 6.53 | 0.735 | 5.78 | 0.4116 | 0.7556 | 0.4774 | 0.5831 | 1 | 0.366 | 0.5305 | 0.5772 | 0.5772 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1326 | 814.9 | 509 | 100.4 | 108.3 | 16.8 | 827.6 | 5147.9 | 58.2 | 22.5 | 78.5 | 79.2 | 70 | 81.3 | 36.9 | 11.7 | 9452.2 | 7912.4 | 8978.4 | 17993.6 | 14309.1 | 16839.5 | 1.904 | 1.808 | 1.876 | 0.5 | 0.579 | 0.558 | 2 | -2.07 | -3.02 | 0.518 | 0.505 | 0.536 | 3.53 | 2.68 | 3.66 | 0.506 | 0.563 | 0.531 | 2.44 | 2.48 | 2.74 | 0.644 | 0.581 | 0.58 | 3.36 | -2.48 | -2.72 | Poor_DGA | 7912.4 | 14309.1 | 1.808 | 0.579 | 3.02 | 0.644 | 3.66 | 0.4654 | 0.9171 | 0.8897 | 0.9724 | 1 | 0.8623 | 0.7671 | 0.7828 | 0.7828 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1327 | 1537.8 | 868.6 | 134.1 | 172.7 | 28.4 | 1209.1 | 8250.9 | 35.5 | 43.9 | 102.2 | 102.9 | 91.8 | 110.9 | 43.7 | 29.1 | 2634.8 | 2360.4 | 2772.3 | 3286 | 2690.6 | 3387 | 1.247 | 1.14 | 1.222 | 0.861 | 0.94 | 0.923 | 7.85 | 9.35 | -8.67 | 0.737 | 0.825 | 0.888 | 7.17 | 6.89 | 5.74 | 0.862 | 0.766 | 0.787 | 7.21 | -6.14 | -9.2 | 0.824 | 0.752 | 0.757 | 6.57 | 8.66 | -7.08 | Very Poor_Mixed | 2360.4 | 2690.6 | 1.14 | 0.94 | 9.35 | 0.888 | 9.2 | 0.1424 | 0.6406 | 0.2207 | 0.4313 | 1 | 0.131 | 0.2621 | 0.3816 | 0.3816 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1328 | 116.9 | 172 | 70.3 | 54.4 | 1 | 382.1 | 2811.9 | 57.8 | 22.3 | 76.4 | 76.8 | 73 | 83.5 | 35.3 | 10.8 | 9730.5 | 9049.8 | 9801.6 | 19460.9 | 17342.8 | 19251.6 | 2 | 1.916 | 1.964 | 0.531 | 0.534 | 0.502 | 2.9 | 2.37 | -2.38 | 0.5 | 0.5 | 0.559 | -2.8 | 2 | 2.42 | 0.5 | 0.526 | 0.517 | -2 | 2.98 | 2.55 | 0.5 | 0.518 | 0.516 | 2 | 2.12 | 2 | Good_Mixed | 9049.8 | 17342.8 | 1.916 | 0.534 | 2.9 | 0.559 | 2.98 | 0.9669 | 0.9215 | 0.9005 | 0.9892 | 1 | 0.8771 | 0.9046 | 0.9375 | 0.9375 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1329 | 387.3 | 201.8 | 78.6 | 66.2 | 2.8 | 426.5 | 3244.2 | 58.5 | 22.6 | 80.1 | 80.1 | 110 | 85.4 | 36.7 | 13 | 8143.5 | 6849.1 | 8485.4 | 13836.5 | 11723.4 | 16035.3 | 1.699 | 1.712 | 1.89 | 0.959 | 0.943 | 0.917 | 9.6 | 9.25 | 8.77 | 0.542 | 0.587 | 0.639 | 3.49 | 3.05 | 4.06 | 0.572 | 0.608 | 0.583 | 3.59 | 4.43 | -4.14 | 0.608 | 0.609 | 0.6 | 3.56 | 3.71 | 4.95 | Critical_Winding_TD_Cap | 6849.1 | 11723.4 | 1.699 | 0.959 | 9.6 | 0.639 | 4.95 | 0.8152 | 0.915 | 0.6477 | 0.9438 | 1 | 0.0794 | 0.6296 | 0.71 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Winding_HV_TanDelta_pct
1330 | 1745.1 | 913.3 | 148.3 | 186.9 | 34.3 | 1379 | 8519.9 | 51 | 27.6 | 83.6 | 83.1 | 121.7 | 88.5 | 37.7 | 13.8 | 8562.5 | 8466.5 | 7940.8 | 15923.2 | 14792.6 | 14827.2 | 1.86 | 1.747 | 1.867 | 0.626 | 0.666 | 0.642 | 4.04 | 4.35 | 4.4 | 0.561 | 0.545 | 0.541 | 2.04 | -2.93 | -2.7 | 0.599 | 0.568 | 0.586 | -2.1 | -3.27 | 3.84 | 0.55 | 0.522 | 0.523 | 3.34 | 2.96 | 2.16 | Critical_DGA | 7940.8 | 14792.6 | 1.747 | 0.666 | 4.4 | 0.599 | 3.84 | 0.051 | 0.8293 | 0.5741 | 0.9244 | 1 | 0.5871 | 0.7519 | 0.5934 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | C2H2
1331 | 1631.4 | 948.3 | 136.6 | 174.9 | 34.3 | 1128.1 | 8170.5 | 33.7 | 44 | 103.8 | 101.5 | 92.5 | 111.8 | 42.2 | 34 | 690 | 2505.1 | 1231.3 | 1200 | 3153.7 | 1416.3 | 1.739 | 1.259 | 1.15 | 0.956 | 0.905 | 0.979 | 8.42 | 8.29 | 9.37 | 0.775 | 0.874 | 0.915 | 6.27 | 8.1 | 7.8 | 0.877 | 0.867 | 0.923 | 7.57 | 6.18 | 7.55 | 0.755 | 0.787 | 0.75 | 5.92 | -5.99 | -7.46 | Very Poor_Mixed | 690 | 1200 | 1.15 | 0.979 | 9.37 | 0.923 | 8.1 | 0.1067 | 0.6396 | 0.2218 | 0.2434 | 1 | 0.1008 | 0.2353 | 0.3542 | 0.3542 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1332 | 1150.5 | 509.5 | 109.7 | 123.4 | 20.5 | 816 | 5755.8 | 46 | 35.7 | 91.5 | 93.4 | 84.1 | 100.8 | 40.4 | 25.7 | 5942.4 | 4996.4 | 5655.1 | 8818.9 | 7268.7 | 8506.7 | 1.484 | 1.455 | 1.504 | 0.749 | 0.692 | 0.714 | 6.24 | 5.02 | -5.13 | 0.751 | 0.707 | 0.582 | 5.14 | 5.01 | 5.3 | 0.709 | 0.753 | 0.706 | 4.38 | 4.87 | 5.24 | 0.627 | 0.617 | 0.724 | 4.88 | 4.67 | 5.35 | Poor_Mixed | 4996.4 | 7268.7 | 1.455 | 0.749 | 6.24 | 0.753 | 5.35 | 0.3904 | 0.7265 | 0.4607 | 0.5549 | 1 | 0.4471 | 0.463 | 0.5645 | 0.5645 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1333 | 140.3 | 120 | 74.3 | 60.2 | 1 | 431.4 | 2789.5 | 43.8 | 36.6 | 75 | 78.8 | 71.2 | 80 | 36.3 | 13.6 | 6119.8 | 7850.2 | 6814.3 | 10175 | 13808.8 | 12021.4 | 1.663 | 1.759 | 1.764 | 0.653 | 0.548 | 0.534 | -3.5 | 2.53 | -2.7 | 0.558 | 0.512 | 0.533 | 2.93 | -2.81 | 2 | 0.55 | 0.5 | 0.525 | -2 | 2 | -3.32 | 0.562 | 0.554 | 0.582 | -2.44 | 2.81 | 2.37 | Poor_Oil | 6119.8 | 10175 | 1.663 | 0.653 | 3.5 | 0.582 | 3.32 | 0.9491 | 0.7164 | 0.9322 | 0.9294 | 1 | 0.7607 | 0.8049 | 0.8743 | 0.8743 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1334 | 314.7 | 205.1 | 69.5 | 140 | 63.2 | 413.5 | 3189.5 | 56.6 | 23.3 | 109.3 | 107.7 | 97 | 119 | 45.5 | 11.7 | 8589.5 | 8989.9 | 8742 | 16379.2 | 15938.8 | 15424.4 | 1.907 | 1.773 | 1.764 | 0.516 | 0.525 | 0.592 | -2 | 3.56 | -2.94 | 0.578 | 0.572 | 0.523 | 2.79 | -2.84 | 2.66 | 0.617 | 0.53 | 0.562 | 2.69 | 3.09 | 2.43 | 0.617 | 0.532 | 0.564 | 2.87 | 2.63 | 2.31 | Critical_Thermal | 8589.5 | 15424.4 | 1.764 | 0.592 | 3.56 | 0.617 | 3.09 | 0.5159 | 0.9008 | 0.0722 | 0.9724 | 1 | 0.8195 | 0.735 | 0.6999 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1335 | 182.1 | 132.2 | 69 | 66.9 | 1.3 | 477.1 | 2958.9 | 59.2 | 22 | 80.7 | 79.4 | 73.7 | 87.1 | 36.2 | 14.6 | 2183.1 | 3927.2 | 4742.8 | 2746.1 | 5306.8 | 6487.4 | 1.258 | 1.351 | 1.368 | 0.649 | 0.582 | 0.652 | 4.55 | 3.31 | 4.65 | 0.527 | 0.537 | 0.565 | -3.24 | 3.56 | -2.23 | 0.525 | 0.578 | 0.525 | -2.66 | 3.53 | 2.58 | 0.544 | 0.526 | 0.587 | 2.05 | 2.64 | -2.56 | Poor_IR_PI | 2183.1 | 2746.1 | 1.258 | 0.652 | 4.65 | 0.587 | 3.56 | 0.889 | 0.9283 | 0.8053 | 0.904 | 1 | 0.6136 | 0.7722 | 0.8443 | 0.8443 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1336 | 275.9 | 229.9 | 69.7 | 65.3 | 49.1 | 394.4 | 2832.8 | 31.8 | 48.4 | 81.3 | 81.7 | 74.7 | 89 | 37.1 | 16 | 5697.8 | 5006.2 | 5025.9 | 8082.3 | 7198.8 | 7208.5 | 1.418 | 1.438 | 1.434 | 0.678 | 0.648 | 0.659 | 4.82 | 4.57 | -4.98 | 0.522 | 0.507 | 0.527 | 2 | 2.91 | 2.56 | 0.529 | 0.5 | 0.537 | 2.01 | 2.29 | 2.08 | 0.562 | 0.564 | 0.517 | 2 | 2 | -2 | Critical_Oil | 5006.2 | 7198.8 | 1.418 | 0.678 | 4.98 | 0.564 | 2.91 | 0.6024 | 0.5979 | 0.7587 | 0.8663 | 1 | 0.5385 | 0.8531 | 0.7305 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1337 | 318 | 203.1 | 69.1 | 150.9 | 1.6 | 409.6 | 2935.5 | 52.7 | 68.4 | 108.9 | 106.9 | 98.1 | 116.5 | 45.3 | 15.9 | 8910.7 | 7575.7 | 8471.4 | 16748.2 | 13384 | 15671.2 | 1.88 | 1.767 | 1.85 | 0.567 | 0.598 | 0.518 | 3.17 | 2.91 | -2.29 | 0.54 | 0.638 | 0.566 | 3.18 | 4.21 | 3.71 | 0.556 | 0.616 | 0.552 | 2.52 | 2.98 | 2.87 | 0.621 | 0.542 | 0.557 | -3.36 | 3.28 | 3.11 | Critical_Thermal | 7575.7 | 13384 | 1.767 | 0.598 | 3.17 | 0.638 | 4.21 | 0.7764 | 0.5833 | 0.0867 | 0.869 | 1 | 0.7912 | 0.69 | 0.7112 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1338 | 183.8 | 201.7 | 70.6 | 73.8 | 2.4 | 451 | 2644 | 20.9 | 25.2 | 86 | 79.5 | 74.7 | 89.7 | 36.4 | 16.3 | 9450.5 | 8982.4 | 8918.5 | 18087.9 | 15998.1 | 16428.2 | 1.914 | 1.781 | 1.842 | 0.959 | 0.924 | 0.972 | 8.74 | 8.42 | 9.32 | 0.595 | 0.583 | 0.559 | 2.72 | -2.6 | -3.28 | 0.617 | 0.56 | 0.561 | 2.41 | 3.2 | 3.72 | 0.52 | 0.608 | 0.567 | 3.63 | 2.69 | 2.59 | Critical_Winding_TD_Cap | 8918.5 | 15998.1 | 1.781 | 0.972 | 9.32 | 0.617 | 3.72 | 0.8378 | 0.2833 | 0.7417 | 0.8578 | 1 | 0.0905 | 0.7046 | 0.66 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1339 | 197 | 146.3 | 67.7 | 104.1 | 1.8 | 414.3 | 3280.4 | 57.4 | 21.8 | 91.3 | 88.5 | 81.3 | 95.5 | 39.6 | 11.4 | 8958.6 | 9525.9 | 8950.6 | 16569.3 | 18877.4 | 16567.9 | 1.85 | 1.982 | 1.851 | 0.563 | 0.527 | 0.503 | 2.22 | 2.33 | 2.34 | 0.523 | 0.5 | 0.5 | 2 | 2.12 | -2.63 | 0.539 | 0.528 | 0.502 | 2.2 | -2.01 | 2.78 | 0.505 | 0.5 | 0.5 | -2.11 | -2 | 2.7 | Fair_Thermal | 8950.6 | 16567.9 | 1.85 | 0.563 | 2.34 | 0.539 | 2.78 | 0.8306 | 0.9331 | 0.5434 | 0.9783 | 1 | 0.881 | 0.9223 | 0.8722 | 0.8722 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1340 | 614.4 | 448.7 | 98.1 | 101.5 | 15.7 | 638.5 | 5618.2 | 57.5 | 20.7 | 75.2 | 79.3 | 70.5 | 82.3 | 35 | 12.6 | 8329.1 | 9041.5 | 8217.2 | 15656.3 | 16836 | 14527.8 | 1.88 | 1.862 | 1.768 | 0.538 | 0.55 | 0.528 | -2.42 | 2.08 | 2.32 | 0.551 | 0.545 | 0.548 | 2.72 | -2 | -3.48 | 0.531 | 0.518 | 0.591 | 2.63 | 3.35 | 2.82 | 0.511 | 0.52 | 0.5 | 3.03 | 2.72 | 2 | Fair_DGA | 8217.2 | 14527.8 | 1.768 | 0.55 | 2.42 | 0.591 | 3.48 | 0.5243 | 0.9638 | 0.9239 | 0.953 | 1 | 0.8597 | 0.8105 | 0.813 | 0.813 | Good | 1 | 1 | DGA | 0 |  | C2H2
1341 | 1586.5 | 877 | 139.1 | 174.5 | 29.4 | 1175.4 | 7236.4 | 37.7 | 44.5 | 103.9 | 106.2 | 93.7 | 114.8 | 43.5 | 32.1 | 2947.6 | 1157.8 | 2308.4 | 3774.8 | 1396.3 | 2659.8 | 1.281 | 1.206 | 1.152 | 0.917 | 0.963 | 0.938 | 8.88 | 8.79 | 9.33 | 0.773 | 0.894 | 0.742 | 8.42 | -8.59 | 9.05 | 0.82 | 0.901 | 0.857 | 7.95 | -7.49 | 7.16 | 0.751 | 0.857 | 0.948 | -8.79 | 9.23 | 6.05 | Very Poor_Mixed | 1157.8 | 1396.3 | 1.152 | 0.963 | 9.33 | 0.948 | 9.23 | 0.1444 | 0.6347 | 0.1639 | 0.3175 | 1 | 0.09 | 0.198 | 0.3528 | 0.3528 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1342 | 727.1 | 550.8 | 97.9 | 122.3 | 18.5 | 763.4 | 5684.7 | 57 | 24.2 | 79.1 | 79.4 | 71.8 | 83.5 | 36.2 | 12 | 8880.1 | 9370.9 | 8737.6 | 17208.4 | 17965.8 | 15407.9 | 1.938 | 1.917 | 1.763 | 0.52 | 0.546 | 0.529 | 2 | 2.45 | 2.32 | 0.529 | 0.505 | 0.56 | 2.05 | 2.99 | -2.38 | 0.52 | 0.585 | 0.542 | 2.41 | 2.79 | -2.31 | 0.522 | 0.509 | 0.537 | -2.5 | 2 | 2 | Poor_DGA | 8737.6 | 15407.9 | 1.763 | 0.546 | 2.45 | 0.585 | 2.99 | 0.4477 | 0.8839 | 0.8538 | 0.9661 | 1 | 0.8757 | 0.8256 | 0.7829 | 0.7829 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1343 | 100 | 120 | 65 | 50 | 1.1 | 350 | 2584.7 | 60 | 21.5 | 77.1 | 75.4 | 70.1 | 82.7 | 35.6 | 13.2 | 8767.2 | 9250.8 | 9803.1 | 16317 | 18219.9 | 19310.6 | 1.861 | 1.97 | 1.97 | 0.511 | 0.526 | 0.504 | -2.99 | 3.09 | 2.04 | 0.561 | 0.5 | 0.566 | 2.88 | 2.55 | 2.79 | 0.5 | 0.505 | 0.5 | 3.04 | 2.71 | 2.95 | 0.529 | 0.5 | 0.501 | -3.16 | -2 | 2.78 | Good_Mixed | 8767.2 | 16317 | 1.861 | 0.526 | 3.09 | 0.566 | 3.16 | 0.9766 | 0.9406 | 0.9433 | 0.939 | 1 | 0.8854 | 0.8805 | 0.9407 | 0.9407 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1344 | 174.4 | 175.1 | 72.3 | 55.6 | 3.5 | 386.3 | 2942.9 | 55.2 | 25.1 | 79.6 | 79.5 | 71.6 | 87.9 | 36.9 | 15.6 | 9949.9 | 9139.8 | 10000 | 18986.3 | 17130.3 | 20000 | 1.908 | 1.874 | 2 | 0.741 | 0.735 | 0.704 | 5.38 | 5.68 | 5.87 | 0.517 | 0.559 | 0.611 | 2.89 | 3.19 | 2.81 | 0.502 | 0.537 | 0.519 | -2.7 | 2.77 | -3.6 | 0.546 | 0.554 | 0.51 | -2 | -3.4 | 2.81 | Poor_Winding_TD_Cap | 9139.8 | 17130.3 | 1.874 | 0.741 | 5.87 | 0.611 | 3.6 | 0.8557 | 0.8683 | 0.8247 | 0.8773 | 1 | 0.4291 | 0.7908 | 0.8069 | 0.8069 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1345 | 849.5 | 544.4 | 103.8 | 107.5 | 15.2 | 795.1 | 4751.5 | 45.8 | 34.4 | 90.8 | 91.3 | 81.9 | 98.2 | 40 | 24.8 | 5848.3 | 6109.8 | 4777 | 8818.8 | 10104.5 | 7173.8 | 1.508 | 1.654 | 1.502 | 0.694 | 0.71 | 0.687 | 5.67 | 5.79 | 4.95 | 0.649 | 0.663 | 0.678 | 4.65 | 4.53 | 4.91 | 0.684 | 0.708 | 0.64 | -4.45 | 6.29 | 4.43 | 0.603 | 0.67 | 0.616 | 5.26 | 5.5 | -3.76 | Poor_Mixed | 4777 | 7173.8 | 1.502 | 0.71 | 5.79 | 0.708 | 6.29 | 0.4756 | 0.7414 | 0.5082 | 0.5865 | 1 | 0.4656 | 0.5007 | 0.6033 | 0.6033 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1346 | 221.8 | 149.4 | 73.6 | 71.9 | 1 | 578.5 | 3921.1 | 19.8 | 31.2 | 83.3 | 85 | 76 | 88.8 | 37.7 | 16.1 | 690 | 1179.3 | 690 | 703.8 | 1289.1 | 759.3 | 1.02 | 1.093 | 1.1 | 0.657 | 0.793 | 0.7 | -5.17 | 6.72 | 4.83 | 0.602 | 0.583 | 0.634 | 3.24 | 3.08 | 3.62 | 0.636 | 0.594 | 0.6 | 4 | -2.92 | 2.72 | 0.575 | 0.592 | 0.601 | 3.37 | -3.43 | -3.39 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.793 | 6.72 | 0.636 | 4 | 0.8892 | 0.1971 | 0.7054 | 0.8635 | 0.85 | 0.445 | 0.6394 | 0.6731 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
1347 | 976.7 | 518 | 112.6 | 109.1 | 17.1 | 873.7 | 5858.6 | 48.2 | 36.5 | 90.1 | 92.2 | 82.6 | 98.4 | 39.7 | 25 | 4123.8 | 6068.4 | 4640 | 6059.9 | 8889.3 | 7266.2 | 1.469 | 1.465 | 1.566 | 0.734 | 0.704 | 0.743 | -5.66 | -5.93 | 5.86 | 0.651 | 0.677 | 0.723 | 5.44 | 4.83 | 4.69 | 0.7 | 0.727 | 0.651 | 5.61 | 5.68 | 4.11 | 0.652 | 0.773 | 0.622 | 5.59 | 5.46 | 5.27 | Poor_Mixed | 4123.8 | 6059.9 | 1.465 | 0.743 | 5.93 | 0.773 | 5.68 | 0.427 | 0.7175 | 0.5034 | 0.5796 | 1 | 0.4192 | 0.453 | 0.5724 | 0.5724 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1348 | 1300.1 | 751 | 130.2 | 163.9 | 28 | 1093.7 | 7495.3 | 36.4 | 44.2 | 103.2 | 100.4 | 90 | 111.6 | 43.9 | 32.8 | 3583.9 | 3048.9 | 3034.4 | 4243.9 | 1822.2 | 3616.3 | 1.184 | 0.598 | 1.192 | 0.886 | 0.899 | 0.886 | -7.82 | 8.17 | 8.65 | 0.825 | 0.811 | 0.771 | 6.01 | 5.59 | 7.17 | 0.79 | 0.865 | 0.766 | 6.36 | 7.78 | 8.19 | 0.734 | 0.869 | 0.716 | 8.16 | 6.78 | 8.04 | Critical_Mixed | 3034.4 | 1822.2 | 0.598 | 0.899 | 8.65 | 0.869 | 8.19 | 0.2077 | 0.6376 | 0.2348 | 0.2904 | 0.8187 | 0.1638 | 0.2698 | 0.3689 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1349 | 427.6 | 243.6 | 76.5 | 59.3 | 2.5 | 435.6 | 2923.2 | 56.2 | 22.6 | 81.6 | 82.2 | 76.9 | 87.5 | 35.8 | 13.2 | 4441.3 | 4015 | 4648.2 | 6002.1 | 5475.8 | 6662.4 | 1.351 | 1.364 | 1.433 | 0.709 | 0.61 | 0.624 | 5.21 | 3.26 | 4.36 | 0.543 | 0.503 | 0.502 | 2 | 2.43 | 2.06 | 0.507 | 0.5 | 0.521 | 2 | -2.2 | 2.35 | 0.51 | 0.556 | 0.524 | 2 | 2.13 | 2.62 | Poor_IR_PI | 4015 | 5475.8 | 1.351 | 0.709 | 5.21 | 0.556 | 2.62 | 0.825 | 0.915 | 0.7499 | 0.939 | 1 | 0.5866 | 0.8895 | 0.8402 | 0.8402 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1350 | 1662 | 973.1 | 146.9 | 197 | 34.3 | 1379 | 9028.4 | 55.5 | 25.2 | 80.7 | 78.5 | 74.8 | 85.7 | 37.2 | 11.7 | 9283.9 | 7964.4 | 8637.7 | 18567.9 | 13801.6 | 6853.6 | 2 | 1.733 | 0.793 | 0.626 | 0.581 | 0.596 | 4.39 | -3.49 | 3.56 | 0.585 | 0.571 | 0.511 | 2.4 | 3.98 | 3.43 | 0.596 | 0.583 | 0.595 | 3.91 | 3.11 | -2.5 | 0.565 | 0.574 | 0.54 | -3.02 | 2.79 | 3.03 | Critical_DGA | 7964.4 | 6853.6 | 0.793 | 0.626 | 4.39 | 0.596 | 3.98 | 0.0364 | 0.8666 | 0.8068 | 0.9724 | 0.8125 | 0.6646 | 0.7095 | 0.5932 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1351 | 444.6 | 322.6 | 79 | 85.6 | 4.8 | 520 | 3803.6 | 54.8 | 24.3 | 81 | 83.5 | 77.2 | 88.7 | 38.4 | 10 | 8441.1 | 8100.7 | 9994.1 | 15473.9 | 14815.1 | 19452.5 | 1.833 | 1.829 | 1.946 | 0.578 | 0.601 | 0.6 | 3.9 | 15.06 | -3.49 | 0.596 | 0.614 | 0.968 | 2.84 | -3.62 | -9.07 | 0.645 | 0.538 | 0.607 | 3.83 | 2.84 | 4.03 | 0.585 | 0.631 | 0.564 | 2.73 | 4.37 | 3.06 | Critical_Bushing_TD_Cap | 8100.7 | 14815.1 | 1.829 | 0.601 | 15.06 | 0.968 | 9.07 | 0.7177 | 0.8821 | 0.7227 | 1 | 1 | 0.5676 | 0.5799 | 0.7514 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1352 | 1680.6 | 968.5 | 147.4 | 197 | 34.2 | 1338.4 | 8792.2 | 30.6 | 48.1 | 107.8 | 108.3 | 95.1 | 118.2 | 44.6 | 33.6 | 1007.6 | 1012.1 | 1753.1 | 1200 | 1200 | 2250.9 | 1.191 | 1.186 | 1.284 | 0.935 | 0.93 | 0.982 | 9.55 | 8.3 | 9.63 | 0.894 | 0.774 | 0.912 | 5.39 | 5.8 | 6.56 | 0.883 | 0.852 | 0.835 | 6.23 | -7.77 | -7.31 | 0.733 | 0.886 | 0.868 | 8.52 | 5.84 | 7.54 | Very Poor_Mixed | 1007.6 | 1200 | 1.186 | 0.982 | 9.63 | 0.912 | 8.52 | 0.0432 | 0.6007 | 0.0981 | 0.2591 | 1 | 0.0756 | 0.2302 | 0.3177 | 0.3177 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1353 | 742.6 | 476.9 | 103.7 | 106.5 | 17.4 | 725.2 | 4755.4 | 54.8 | 23.6 | 75.5 | 77.9 | 73.2 | 83.2 | 36.1 | 11.4 | 9689.9 | 10000 | 10000 | 18337.2 | 19232.8 | 20000 | 1.892 | 1.923 | 2 | 0.535 | 0.557 | 0.558 | 3 | -3.31 | -2.4 | 0.501 | 0.502 | 0.553 | -2 | 3.12 | 2 | 0.558 | 0.557 | 0.572 | 2.43 | 2.17 | 3.72 | 0.558 | 0.504 | 0.5 | 2.6 | 2.38 | 2.42 | Poor_DGA | 9689.9 | 18337.2 | 1.892 | 0.558 | 3.31 | 0.572 | 3.72 | 0.4874 | 0.895 | 0.8973 | 0.9783 | 1 | 0.7944 | 0.836 | 0.7896 | 0.7896 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1354 | 690.2 | 373.4 | 90.9 | 100.8 | 14.9 | 703.2 | 5082.3 | 47.8 | 30.9 | 88.2 | 87.5 | 79.8 | 94.2 | 37.9 | 21.3 | 6221.7 | 7216.4 | 6803.1 | 10295 | 12487.3 | 10759 | 1.655 | 1.73 | 1.581 | 0.616 | 0.67 | 0.64 | 4.21 | 4.39 | -4.44 | 0.637 | 0.677 | 0.633 | 3.38 | 4.36 | 3.86 | 0.604 | 0.584 | 0.655 | 3.52 | -3.2 | 3.67 | 0.651 | 0.559 | 0.596 | 5.17 | -4.61 | 4.14 | Fair_Mixed | 6221.7 | 10295 | 1.581 | 0.67 | 4.44 | 0.677 | 5.17 | 0.5346 | 0.7842 | 0.5976 | 0.7049 | 1 | 0.5853 | 0.5841 | 0.6698 | 0.6698 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1355 | 1389.3 | 789.3 | 133.6 | 172 | 33.3 | 1146.8 | 7269.9 | 38.3 | 41.2 | 106.6 | 106.6 | 93.4 | 116 | 44.5 | 31.5 | 949.5 | 2467.2 | 1891 | 1200 | 2709.2 | 2178.5 | 1.264 | 1.098 | 1.152 | 0.883 | 0.863 | 0.919 | 7.43 | 7.28 | 8.3 | 0.88 | 0.672 | 0.767 | 5.29 | 6.34 | 6.94 | 0.702 | 0.839 | 0.772 | 7.56 | 7.01 | 6.34 | 0.805 | 0.8 | 0.763 | 7.89 | -5.51 | 6.03 | Very Poor_Mixed | 949.5 | 1200 | 1.098 | 0.919 | 8.3 | 0.88 | 7.89 | 0.1599 | 0.6675 | 0.1351 | 0.3406 | 1 | 0.1935 | 0.3061 | 0.3928 | 0.3928 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1356 | 275 | 257.9 | 79 | 92.3 | 2.4 | 526.9 | 3598.4 | 57.3 | 22.6 | 97 | 99.6 | 91.5 | 107.2 | 42.7 | 12.4 | 9415.5 | 8936.4 | 9472.1 | 18664.9 | 17345.6 | 18944.3 | 1.982 | 1.941 | 2 | 0.603 | 0.548 | 0.604 | 2.75 | 3.3 | 4.23 | 0.531 | 0.587 | 0.5 | -2.86 | 2 | 2.38 | 0.5 | 0.516 | 0.536 | 2.46 | 2 | -2.74 | 0.583 | 0.5 | 0.5 | 2 | 2 | 2.24 | Poor_Thermal | 8936.4 | 17345.6 | 1.941 | 0.604 | 4.23 | 0.587 | 2.86 | 0.7773 | 0.915 | 0.2975 | 0.9575 | 1 | 0.7114 | 0.8756 | 0.7989 | 0.7989 | Fair | 1 | 0 | No_Anomaly | 0 |  | WTI_LV
1357 | 207.9 | 250.2 | 78.2 | 66.9 | 3.5 | 504.8 | 2736.2 | 39.2 | 39.6 | 81.3 | 83.9 | 72.9 | 84.8 | 37.4 | 14.6 | 7600.4 | 6055.7 | 7141.1 | 13065.3 | 9934.8 | 12045.5 | 1.719 | 1.641 | 1.687 | 0.595 | 0.648 | 0.655 | -3.38 | 3.97 | 3.99 | 0.561 | 0.576 | 0.533 | 3.69 | 2.91 | 2.29 | 0.536 | 0.5 | 0.575 | 2.66 | -2 | 2.53 | 0.525 | 0.535 | 0.521 | 2.66 | 2 | 2.19 | Poor_Oil | 6055.7 | 9934.8 | 1.641 | 0.655 | 3.99 | 0.576 | 3.69 | 0.8022 | 0.684 | 0.7755 | 0.904 | 1 | 0.6304 | 0.8059 | 0.7987 | 0.7987 | Fair | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1358 | 1616.9 | 873.3 | 133.6 | 177.3 | 33.6 | 1273.8 | 8083 | 36.2 | 45.3 | 103.6 | 105 | 94.7 | 113.5 | 43.8 | 31.2 | 2068 | 1206.9 | 1514.4 | 2371.3 | 1309.2 | 1630.5 | 1.147 | 1.085 | 1.077 | 0.959 | 0.928 | 0.99 | 9.38 | 8.68 | -9.68 | 0.768 | 0.778 | 0.889 | 6.75 | -7.64 | 7.01 | 0.742 | 0.785 | 0.86 | 8.08 | -6.67 | 7.17 | 0.768 | 0.937 | 0.847 | 8.43 | -6.85 | 4.84 | Very Poor_Mixed | 1206.9 | 1309.2 | 1.077 | 0.99 | 9.68 | 0.937 | 8.43 | 0.1042 | 0.627 | 0.171 | 0.3521 | 1 | 0.0645 | 0.2486 | 0.3498 | 0.3498 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1359 | 249.5 | 162.7 | 77.4 | 71.8 | 2.2 | 501.2 | 3120.4 | 54.8 | 23.2 | 80.3 | 75.1 | 71.5 | 81.8 | 36.2 | 14.7 | 9470.9 | 8994.2 | 9184.8 | 18773.1 | 17836.5 | 17869.1 | 1.982 | 1.983 | 1.946 | 0.819 | 0.842 | 0.828 | 6.84 | 7.14 | 6.88 | 0.608 | 0.574 | 0.527 | 2.97 | 2.97 | 2.96 | 0.542 | 0.626 | 0.609 | -3.22 | 2.99 | 4.26 | 0.552 | 0.608 | 0.572 | 2.99 | 2.46 | 3.23 | Poor_Winding_TD_Cap | 8994.2 | 17836.5 | 1.946 | 0.842 | 7.14 | 0.626 | 4.26 | 0.8289 | 0.9027 | 0.9042 | 0.9014 | 1 | 0.2739 | 0.6897 | 0.7735 | 0.7735 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
1360 | 315 | 262.9 | 73.6 | 57.8 | 1 | 410.1 | 3041.2 | 58.8 | 20.7 | 80.5 | 80.7 | 72.7 | 84.6 | 36 | 11.7 | 8723.6 | 7795.4 | 9348 | 16775.7 | 13485.7 | 17048.1 | 1.923 | 1.73 | 1.824 | 0.558 | 0.551 | 0.545 | -2.65 | 2.76 | 2.94 | 0.744 | 0.566 | 0.57 | 5.39 | 2.38 | -2.87 | 0.526 | 0.58 | 0.566 | 2.27 | -2.22 | 2.28 | 0.613 | 0.549 | 0.504 | 2.33 | 2.9 | 2.67 | Poor_Bushing_TD_Cap | 7795.4 | 13485.7 | 1.73 | 0.558 | 2.94 | 0.744 | 5.39 | 0.9198 | 0.9638 | 0.8175 | 0.9724 | 1 | 0.7991 | 0.7203 | 0.8775 | 0.8775 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_HV_R_TanDelta_pct
1361 | 139 | 188.7 | 66.9 | 53.7 | 2.5 | 350 | 2579.9 | 54.9 | 20.2 | 75 | 75.6 | 70 | 80 | 35 | 12.5 | 9918.3 | 10000 | 10000 | 19477.1 | 20000 | 20000 | 1.964 | 2 | 2 | 0.534 | 0.554 | 0.5 | 2.32 | 3.01 | -2.59 | 0.515 | 0.5 | 0.529 | -2.08 | 2 | -2 | 0.535 | 0.507 | 0.501 | 2.48 | 2.16 | 2.35 | 0.5 | 0.5 | 0.55 | 2 | 2 | 2.14 | Good_Mixed | 9918.3 | 19477.1 | 1.964 | 0.554 | 3.01 | 0.55 | 2.48 | 0.896 | 0.984 | 0.9882 | 0.9552 | 1 | 0.8639 | 0.9127 | 0.9339 | 0.9339 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1362 | 829 | 456.5 | 105.3 | 117.7 | 17.2 | 828 | 4935.1 | 47 | 30.2 | 92.5 | 91.2 | 83.2 | 97.9 | 40 | 24.3 | 5209.1 | 6458.1 | 5154.5 | 7741.3 | 10624.8 | 8065.9 | 1.486 | 1.645 | 1.565 | 0.717 | 0.768 | 0.747 | 5.04 | -6.49 | 5.87 | 0.653 | 0.556 | 0.723 | 4.12 | 3.76 | 4.41 | 0.692 | 0.685 | 0.682 | 5.2 | 4.5 | 5.61 | 0.712 | 0.713 | 0.644 | 3.65 | 4.83 | 4.6 | Poor_Mixed | 5154.5 | 7741.3 | 1.486 | 0.768 | 6.49 | 0.723 | 5.61 | 0.4568 | 0.7933 | 0.4911 | 0.6039 | 1 | 0.4058 | 0.4958 | 0.5948 | 0.5948 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1363 | 230.9 | 146.5 | 70.7 | 58.5 | 2.5 | 481.1 | 2699.4 | 60 | 22.7 | 76.8 | 80.4 | 71.4 | 80.8 | 36.6 | 14.3 | 8455.9 | 9318.7 | 10000 | 15955 | 18262.4 | 19492.2 | 1.887 | 1.96 | 1.949 | 0.549 | 0.5 | 0.5 | 2 | -2 | 2 | 0.527 | 0.5 | 0.524 | 2.72 | 2.08 | -2.88 | 0.536 | 0.521 | 0.535 | 3.09 | 2 | 2 | 0.578 | 0.522 | 0.517 | -2.69 | 2.84 | 2.46 | Good_Mixed | 8455.9 | 15955 | 1.887 | 0.549 | 2 | 0.578 | 3.09 | 0.8536 | 0.9129 | 0.8834 | 0.9118 | 1 | 0.9557 | 0.834 | 0.9008 | 0.9008 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1364 | 1766 | 982.4 | 146.5 | 193.7 | 33.4 | 1350.9 | 8415.8 | 54.6 | 24.7 | 85.2 | 82.3 | 76.6 | 90.7 | 39.1 | 16.2 | 7962.3 | 8168.6 | 9151.6 | 14723.5 | 14741.9 | 16950.9 | 1.849 | 1.805 | 1.852 | 0.527 | 0.575 | 0.525 | 2.68 | -10.98 | 2.46 | 0.566 | 0.553 | 0.528 | 3.38 | 2.64 | -2 | 0.526 | 0.5 | 0.584 | -3.48 | 3.31 | 2.65 | 0.508 | 0.528 | 0.531 | 2.92 | -3.1 | -2.34 | Critical_DGA | 7962.3 | 14723.5 | 1.805 | 0.575 | 10.98 | 0.584 | 3.48 | 0.0462 | 0.8751 | 0.6895 | 0.8607 | 1 | 0.6947 | 0.8017 | 0.6301 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1365 | 1710.9 | 960.9 | 146.7 | 180.8 | 32.1 | 1307.7 | 8381.6 | 35 | 46.4 | 104.5 | 104.5 | 91.9 | 109.4 | 43.7 | 32.6 | 2057.7 | 1349.4 | 998 | 2291.3 | 1495 | 1200 | 1.114 | 1.108 | 1.202 | 0.968 | 0.986 | 0.953 | 9.84 | 9.46 | -8.89 | 0.899 | 0.864 | 0.91 | -6.69 | 7.46 | 6.82 | 0.888 | 0.85 | 0.838 | 7.83 | 9.16 | 6.43 | 0.713 | 0.879 | 0.892 | 6.7 | 5.9 | 7.08 | Very Poor_Mixed | 998 | 1200 | 1.108 | 0.986 | 9.84 | 0.91 | 9.16 | 0.0737 | 0.6166 | 0.2057 | 0.2982 | 1 | 0.0502 | 0.2091 | 0.3326 | 0.3326 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1366 | 917.1 | 549 | 110.5 | 136.5 | 19.7 | 884 | 5178.4 | 46.4 | 32.4 | 91.7 | 90.8 | 83.1 | 100.2 | 39.7 | 23.9 | 5381.2 | 5237.1 | 5551.7 | 7963 | 8286.9 | 8470.8 | 1.48 | 1.582 | 1.526 | 0.743 | 0.74 | 0.789 | 5.58 | -6.09 | 6.52 | 0.626 | 0.646 | 0.755 | 4.11 | 4.46 | 5.53 | 0.644 | 0.69 | 0.737 | 4.46 | -4.48 | 5.08 | 0.678 | 0.685 | 0.634 | 5.56 | -5.86 | 4.93 | Poor_Mixed | 5237.1 | 7963 | 1.48 | 0.789 | 6.52 | 0.755 | 5.86 | 0.3933 | 0.7654 | 0.4899 | 0.6177 | 1 | 0.3798 | 0.4727 | 0.5683 | 0.5683 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1367 | 788.8 | 559.2 | 102.8 | 107.3 | 15.4 | 762.9 | 4757.8 | 47.7 | 31.6 | 91.1 | 91.8 | 83.9 | 98.7 | 39.3 | 23.1 | 6255 | 5989.7 | 5820.1 | 9752.5 | 9556.9 | 9014.8 | 1.559 | 1.596 | 1.549 | 0.692 | 0.629 | 0.747 | 4.81 | -4.38 | -5.48 | 0.672 | 0.592 | 0.603 | 4.68 | 3.75 | 3.02 | 0.582 | 0.649 | 0.646 | -3.86 | 3.45 | 5.43 | 0.616 | 0.546 | 0.652 | 3.83 | 4.53 | -3.93 | Poor_Mixed | 5820.1 | 9014.8 | 1.549 | 0.747 | 5.48 | 0.672 | 5.43 | 0.4824 | 0.7753 | 0.4923 | 0.645 | 1 | 0.5082 | 0.5888 | 0.6323 | 0.6323 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1368 | 1650.6 | 843.4 | 137.8 | 189 | 30.3 | 1268.1 | 8123.3 | 34.5 | 46 | 104.2 | 105.3 | 92.6 | 113.7 | 43.8 | 32.2 | 2256.8 | 1127.9 | 1818.9 | 2665.8 | 1200 | 1912.2 | 1.181 | 1.064 | 1.051 | 0.913 | 0.939 | 0.884 | 9.15 | 9.19 | 8.81 | 0.762 | 0.813 | 0.884 | 6.61 | -5.76 | 6.04 | 0.841 | 0.882 | 0.861 | 8.74 | 8.49 | -6.8 | 0.711 | 0.874 | 0.792 | -6.29 | -8.3 | 4.82 | Very Poor_Mixed | 1127.9 | 1200 | 1.051 | 0.939 | 9.19 | 0.884 | 8.74 | 0.1069 | 0.6203 | 0.1767 | 0.3137 | 1 | 0.1062 | 0.2498 | 0.3544 | 0.3544 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1369 | 282.1 | 272.8 | 81 | 68.9 | 4.8 | 480.8 | 3511.7 | 54.4 | 26.9 | 79.6 | 79.7 | 73.3 | 85.9 | 35.9 | 15.3 | 8508.3 | 7936.4 | 8598.2 | 16445.1 | 14711.7 | 15000.7 | 1.933 | 1.854 | 1.745 | 0.608 | 0.619 | 0.6 | -3.86 | 3.56 | 3.43 | 0.643 | 0.621 | 0.638 | 3.72 | 3.56 | 4.45 | 0.598 | 0.619 | 0.578 | 4.74 | 3.57 | -3.65 | 0.514 | 0.622 | 0.547 | -3.39 | -3.22 | -3.22 | Fair_Mixed | 7936.4 | 14711.7 | 1.745 | 0.619 | 3.86 | 0.643 | 4.74 | 0.7663 | 0.8397 | 0.8228 | 0.8855 | 1 | 0.6662 | 0.6367 | 0.7868 | 0.7868 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1370 | 1464.1 | 836.8 | 128.9 | 169.8 | 29 | 1163.9 | 7821.5 | 12.9 | 43.2 | 104.6 | 99 | 89.9 | 110.5 | 42.6 | 36.9 | 3158.9 | 3568.3 | 2243 | 3944.7 | 4632.4 | 2673.8 | 1.249 | 1.298 | 1.192 | 0.85 | 0.898 | 0.865 | 7.74 | -9.22 | -8.37 | 0.808 | 0.811 | 0.748 | 7.87 | 7.09 | 7.78 | 0.712 | 0.844 | 0.747 | 5.87 | 7.24 | 7 | 0.658 | 0.858 | 0.791 | 8.62 | 9.25 | 6.97 | Critical_Mixed | 2243 | 2673.8 | 1.192 | 0.898 | 9.22 | 0.858 | 9.25 | 0.1654 | 0.0641 | 0.2504 | 0.1275 | 1 | 0.1662 | 0.2768 | 0.3136 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
1371 | 777.6 | 557.4 | 95.9 | 110.2 | 20 | 762.7 | 4675.7 | 56.8 | 21.7 | 79.3 | 78.6 | 73.9 | 85.3 | 35.8 | 10 | 8027.4 | 8240 | 8656.8 | 14818.2 | 15348.8 | 15876.5 | 1.846 | 1.863 | 1.834 | 0.647 | 0.571 | 0.59 | -3.94 | 2.9 | 2.89 | 0.56 | 0.5 | 0.521 | 2.37 | -2.28 | 2 | 0.5 | 0.545 | 0.503 | 2.85 | 2.58 | 2 | 0.507 | 0.545 | 0.55 | 2.13 | -3.27 | 2.62 | Poor_DGA | 8027.4 | 14818.2 | 1.834 | 0.647 | 3.94 | 0.56 | 3.27 | 0.4574 | 0.9355 | 0.8341 | 1 | 1 | 0.7006 | 0.8588 | 0.7727 | 0.7727 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1372 | 1021.9 | 550.9 | 119.1 | 129.3 | 20.3 | 973.4 | 5860.5 | 43.7 | 34.5 | 92.3 | 92.1 | 85.8 | 98.7 | 41 | 27.4 | 6849 | 5863 | 6682.3 | 11504.1 | 9424.6 | 10520.1 | 1.68 | 1.607 | 1.574 | 0.79 | 0.792 | 0.752 | 6.22 | 6.55 | 5.76 | 0.664 | 0.665 | 0.633 | -6.35 | 5.48 | 4.96 | 0.719 | 0.709 | 0.674 | 4.99 | -4.72 | -5.44 | 0.64 | 0.604 | 0.73 | 5.47 | 6.12 | 5.96 | Poor_Mixed | 5863 | 9424.6 | 1.574 | 0.792 | 6.55 | 0.73 | 6.35 | 0.3638 | 0.7403 | 0.46 | 0.4938 | 1 | 0.3564 | 0.4603 | 0.5432 | 0.5432 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1373 | 365 | 302.5 | 79 | 75.6 | 67.7 | 514.7 | 3254.9 | 35.8 | 46.2 | 78.9 | 82.3 | 74.8 | 89 | 36.6 | 13.8 | 6025.5 | 6241.6 | 6100.2 | 9231.7 | 10312.4 | 9640 | 1.532 | 1.652 | 1.58 | 0.564 | 0.58 | 0.675 | 4.11 | -3.02 | 4.94 | 0.598 | 0.542 | 0.56 | 4.19 | 4.21 | 3.41 | 0.558 | 0.626 | 0.644 | 2.8 | -4.17 | 4.02 | 0.602 | 0.683 | 0.584 | 3.6 | 4 | 3.83 | Critical_Oil | 6025.5 | 9231.7 | 1.532 | 0.675 | 4.94 | 0.683 | 4.21 | 0.5433 | 0.6184 | 0.7766 | 0.9244 | 1 | 0.6506 | 0.6277 | 0.698 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1374 | 290.2 | 274.2 | 77.3 | 58.2 | 2.4 | 455.9 | 3450.3 | 46.5 | 33.7 | 81 | 82.8 | 74.5 | 87.8 | 36.5 | 15.6 | 7354.1 | 7367.3 | 7531 | 13215.7 | 12945.8 | 13117.1 | 1.797 | 1.757 | 1.742 | 0.563 | 0.584 | 0.581 | -3.02 | -3.27 | 4.02 | 0.5 | 0.514 | 0.546 | -2 | 2 | -2 | 0.529 | 0.518 | 0.51 | 3.05 | 2 | 2.14 | 0.5 | 0.515 | 0.525 | -2.39 | 2 | 2.52 | Poor_Oil | 7354.1 | 12945.8 | 1.742 | 0.584 | 4.02 | 0.546 | 3.05 | 0.8311 | 0.7497 | 0.7632 | 0.8773 | 1 | 0.72 | 0.8895 | 0.8388 | 0.8388 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1375 | 1460.3 | 835.5 | 139.1 | 181.9 | 34.3 | 1277.7 | 7642.8 | 33.5 | 45.7 | 102.3 | 103.1 | 90.3 | 109.6 | 43.2 | 31.4 | 1659.4 | 2112.3 | 3170.8 | 1791.7 | 2564.7 | 3891 | 1.08 | 1.214 | 1.227 | 0.849 | 0.866 | 0.838 | 8.23 | 8.05 | -8.06 | 0.758 | 0.771 | 0.78 | 7.06 | 6.62 | 6.94 | 0.714 | 0.863 | 0.837 | 5.87 | -5.71 | 6.07 | 0.713 | 0.928 | 0.806 | 7.02 | 5.9 | 7.28 | Very Poor_Mixed | 1659.4 | 1791.7 | 1.08 | 0.866 | 8.23 | 0.928 | 7.28 | 0.1136 | 0.6232 | 0.2377 | 0.3444 | 1 | 0.1974 | 0.2889 | 0.3838 | 0.3838 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1376 | 1726 | 897.1 | 144.4 | 183 | 34.3 | 1312.7 | 7946.6 | 33.7 | 49.4 | 106 | 106.9 | 92.5 | 113.4 | 44.4 | 33.8 | 690 | 690 | 1891.6 | 1200 | 1200 | 1986.1 | 1.739 | 1.739 | 1.05 | 0.962 | 0.952 | 0.99 | 9.5 | 9.39 | 9.19 | 0.847 | 0.849 | 0.761 | -5.84 | 6.57 | 5.84 | 0.924 | 0.761 | 0.96 | -6.42 | -9.04 | 9.11 | 0.767 | 0.897 | 0.809 | -9.34 | 6.43 | 7.32 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.99 | 9.5 | 0.96 | 9.34 | 0.0751 | 0.5888 | 0.1556 | 0.2513 | 1 | 0.0527 | 0.2197 | 0.3245 | 0.3245 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1377 | 100 | 120 | 66.5 | 52.8 | 1 | 350 | 2500 | 58.3 | 22.6 | 76.7 | 78.4 | 71.1 | 81.7 | 35 | 14.1 | 9827.8 | 10000 | 10000 | 18683.2 | 20000 | 19916.3 | 1.901 | 2 | 1.992 | 0.526 | 0.547 | 0.518 | 2 | 2.51 | -2.5 | 0.5 | 0.5 | 0.566 | 2 | -2.96 | 2.71 | 0.561 | 0.512 | 0.565 | 3.02 | 3.11 | -2.07 | 0.548 | 0.716 | 0.548 | 3.17 | 5.04 | 2.42 | Fair_Bushing_TD_Cap | 9827.8 | 18683.2 | 1.901 | 0.547 | 2.51 | 0.716 | 5.04 | 0.9913 | 0.915 | 0.9079 | 0.9169 | 1 | 0.8726 | 0.7722 | 0.9154 | 0.9154 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1378 | 679.6 | 368.6 | 87.7 | 86.2 | 13.8 | 628.1 | 5129.2 | 58.2 | 23.1 | 75 | 80.3 | 70.4 | 82 | 35.5 | 11 | 9079.1 | 9610.5 | 8952.9 | 17167.8 | 18766.9 | 16577.5 | 1.891 | 1.953 | 1.852 | 0.556 | 0.578 | 0.58 | 2.06 | 2.61 | -3.24 | 0.5 | 0.526 | 0.534 | 2 | 2.38 | 2.72 | 0.557 | 0.508 | 0.518 | 2.36 | -3.04 | 2.04 | 0.512 | 0.518 | 0.505 | 2.94 | 2 | -2.88 | Fair_DGA | 8952.9 | 16577.5 | 1.852 | 0.58 | 3.24 | 0.557 | 3.04 | 0.5716 | 0.9047 | 0.9213 | 0.9858 | 1 | 0.7824 | 0.865 | 0.8181 | 0.8181 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1379 | 100 | 134.7 | 72.7 | 65.6 | 1 | 416.2 | 2790.1 | 56.8 | 23.5 | 78.4 | 78.9 | 73.6 | 86.4 | 37.3 | 15 | 9014.7 | 9416.9 | 7302.8 | 16945.2 | 17108.1 | 13061.3 | 1.88 | 1.817 | 1.789 | 0.587 | 0.611 | 0.575 | 3.65 | -3.65 | 3.64 | 0.546 | 0.558 | 0.55 | 2.82 | -2.57 | 2.37 | 0.728 | 0.557 | 0.516 | 4.95 | -2 | -3.14 | 0.571 | 0.618 | 0.514 | 3.12 | 3.21 | 2.49 | Poor_Bushing_TD_Cap | 7302.8 | 13061.3 | 1.789 | 0.611 | 3.65 | 0.728 | 4.95 | 0.9485 | 0.8969 | 0.8291 | 0.8935 | 1 | 0.6867 | 0.7228 | 0.8586 | 0.8586 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1380 | 1638.6 | 982.4 | 143.5 | 190.5 | 34 | 1364.2 | 8719.1 | 55.8 | 52.9 | 79.9 | 81.4 | 76.7 | 86.6 | 35.8 | 14.7 | 8747.1 | 7709.8 | 8533.4 | 16009.8 | 14186.6 | 15953.5 | 1.83 | 1.84 | 1.87 | 0.585 | 0.649 | 0.55 | -3.09 | 4.25 | 3.47 | 0.571 | 0.567 | 0.574 | 2.9 | 2.01 | 2.74 | 0.631 | 0.578 | 0.577 | -2.59 | 3.71 | 2.66 | 0.577 | 0.622 | 0.62 | 2.89 | 3.05 | 3.18 | Critical_DGA | 7709.8 | 14186.6 | 1.83 | 0.649 | 4.25 | 0.631 | 3.71 | 0.0522 | 0.5833 | 0.7766 | 0.9014 | 1 | 0.6894 | 0.6795 | 0.5846 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
1381 | 100 | 149.4 | 65 | 51.7 | 1 | 407.4 | 2696.6 | 58.2 | 20.7 | 77.7 | 80.2 | 76.9 | 81.8 | 37 | 11.7 | 9128.2 | 9387.5 | 8953.5 | 16471.7 | 17458.4 | 16569.6 | 1.804 | 1.86 | 1.851 | 0.519 | 0.584 | 0.518 | 2.08 | 3.23 | 2.52 | 0.554 | 0.5 | 0.531 | 2 | 2.7 | 2.32 | 0.512 | 0.598 | 0.504 | 3.01 | 2.31 | 2.86 | 0.502 | 0.522 | 0.695 | -2.43 | 3.07 | 5.63 | Poor_Bushing_TD_Cap | 8953.5 | 16471.7 | 1.804 | 0.584 | 3.23 | 0.695 | 5.63 | 0.9762 | 0.9638 | 0.824 | 0.9724 | 1 | 0.8396 | 0.7997 | 0.9122 | 0.9122 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1382 | 298.2 | 217.8 | 72.4 | 102.6 | 1 | 350 | 2817 | 56 | 21.8 | 91.1 | 88.9 | 80.3 | 94.9 | 39.4 | 11.5 | 9183.9 | 8516.2 | 9019.8 | 17741.7 | 15316.4 | 16726 | 1.932 | 1.799 | 1.854 | 0.531 | 0.571 | 0.593 | 3.52 | 3.85 | 3.3 | 0.599 | 0.553 | 0.528 | 2.19 | 2.94 | 3.31 | 0.573 | 0.557 | 0.548 | 3.56 | 2.38 | 2.37 | 0.539 | 0.563 | 0.535 | -3.15 | 2.06 | 2.82 | Poor_Thermal | 8516.2 | 15316.4 | 1.799 | 0.593 | 3.85 | 0.599 | 3.56 | 0.8874 | 0.9331 | 0.5528 | 0.9764 | 1 | 0.7305 | 0.7521 | 0.8356 | 0.8356 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1383 | 378.6 | 251.4 | 80.6 | 84.4 | 2.5 | 545.3 | 3633.7 | 55.3 | 22 | 83.5 | 81.3 | 76.1 | 89.3 | 37 | 16.8 | 897.8 | 1446.8 | 690 | 979.2 | 1607 | 703.8 | 1.091 | 1.111 | 1.02 | 1.927 | 0.745 | 0.734 | 5.75 | 5.99 | -6.46 | 0.518 | 0.555 | 0.58 | 3.57 | -3.39 | 2.9 | 0.59 | 0.588 | 0.583 | 3.31 | 3.71 | 2.9 | 0.529 | 0.606 | 0.64 | 3.4 | 3.23 | 3.78 | Critical_IR_PI | 690 | 703.8 | 1.02 | 1.927 | 6.46 | 0.64 | 3.78 | 0.7707 | 0.9283 | 0.7331 | 0.8436 | 0.85 | 0.3307 | 0.6867 | 0.7255 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_HV_TanDelta_pct
1384 | 1014.4 | 604.9 | 114.4 | 127.7 | 20.4 | 833.8 | 5796.2 | 47.3 | 33.9 | 88.1 | 92 | 79.2 | 96 | 39.2 | 25.2 | 6029.5 | 5315 | 5167.7 | 8967.4 | 8122.2 | 8050.5 | 1.487 | 1.528 | 1.558 | 0.688 | 0.688 | 0.686 | -4.98 | 4.82 | -5.18 | 0.58 | 0.666 | 0.678 | 5.64 | 4.8 | 3.33 | 0.678 | 0.639 | 0.615 | 4.34 | 4.79 | -5.12 | 0.625 | 0.553 | 0.604 | 4.26 | 4.03 | 3.94 | Poor_Mixed | 5167.7 | 8050.5 | 1.487 | 0.688 | 5.18 | 0.678 | 5.64 | 0.3805 | 0.7473 | 0.5555 | 0.5725 | 1 | 0.5015 | 0.5596 | 0.5999 | 0.5999 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1385 | 480.8 | 324.7 | 82.3 | 90.1 | 12.1 | 619.8 | 4653.8 | 50.2 | 28.3 | 85.9 | 81.6 | 76.1 | 91 | 38.4 | 19.9 | 5682.5 | 7430.4 | 6300.6 | 8782.8 | 12168.6 | 10359.1 | 1.546 | 1.638 | 1.644 | 0.655 | 0.582 | 0.721 | 4.29 | -3.5 | 4.89 | 0.579 | 0.633 | 0.647 | -4 | 4.7 | 2.34 | 0.602 | 0.623 | 0.587 | 4.07 | 3.98 | 4.03 | 0.576 | 0.633 | 0.579 | 3.34 | 4.07 | 4.4 | Fair_Mixed | 5682.5 | 8782.8 | 1.546 | 0.721 | 4.89 | 0.647 | 4.7 | 0.6112 | 0.8193 | 0.6965 | 0.7499 | 1 | 0.5859 | 0.6101 | 0.7101 | 0.7101 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1386 | 1677.4 | 917.1 | 144.1 | 180 | 34.3 | 1321.1 | 8330.1 | 36.1 | 43.4 | 106.9 | 106.5 | 93.9 | 115.1 | 43.6 | 35.2 | 1790.7 | 1888.5 | 2172.1 | 2045.5 | 2162.9 | 2648.1 | 1.142 | 1.145 | 1.219 | 0.987 | 0.957 | 0.966 | 9.49 | 9.73 | 9.71 | 0.802 | 0.738 | 0.899 | 7.48 | 5.56 | 9.84 | 0.808 | 0.885 | 0.733 | 8.76 | 8.69 | -8.55 | 0.844 | 0.76 | 0.862 | -7.23 | 9.13 | 7.29 | Very Poor_Mixed | 1790.7 | 2045.5 | 1.142 | 0.987 | 9.73 | 0.899 | 9.84 | 0.0732 | 0.6455 | 0.1423 | 0.1958 | 1 | 0.0372 | 0.2205 | 0.3247 | 0.3247 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1387 | 1706.4 | 966.2 | 144.6 | 197 | 33.3 | 1376.6 | 8886.1 | 32 | 47.9 | 108.3 | 107.2 | 91.7 | 117.5 | 43.9 | 35.1 | 2813.4 | 1146.7 | 2295.5 | 3282.2 | 1204.1 | 2410.3 | 1.167 | 1.05 | 1.05 | 0.99 | 0.952 | 0.933 | 9.69 | 8.76 | 8.78 | 0.729 | 0.784 | 0.71 | -6.85 | 7.77 | 8.62 | 0.99 | 0.834 | 0.853 | 6.72 | 6.06 | -7.75 | 0.791 | 0.71 | 0.786 | 9.26 | 9.05 | 8.54 | Very Poor_Mixed | 1146.7 | 1204.1 | 1.05 | 0.99 | 9.69 | 0.99 | 9.26 | 0.0424 | 0.6025 | 0.129 | 0.1998 | 1 | 0.0735 | 0.2447 | 0.3201 | 0.3201 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1388 | 920.7 | 527.2 | 101.6 | 128.7 | 15.9 | 840.5 | 5604.8 | 45.7 | 33.2 | 88.4 | 90.8 | 80.9 | 95 | 39.3 | 25.3 | 5737.8 | 5859.6 | 5049.5 | 8876.8 | 8887.2 | 7626.6 | 1.547 | 1.517 | 1.51 | 0.666 | 0.784 | 0.676 | 5.72 | 5.5 | -4.58 | 0.709 | 0.723 | 0.636 | 4.89 | 6.5 | 4.74 | 0.654 | 0.696 | 0.728 | 4.72 | -5.31 | 4.54 | 0.706 | 0.66 | 0.627 | 5.86 | 4.34 | -5.7 | Poor_Mixed | 5049.5 | 7626.6 | 1.51 | 0.784 | 5.72 | 0.728 | 6.5 | 0.4339 | 0.7556 | 0.5543 | 0.569 | 1 | 0.4687 | 0.4575 | 0.591 | 0.591 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1389 | 768.8 | 434.9 | 103 | 118.4 | 13.3 | 823.8 | 5880.4 | 47.1 | 32.8 | 90.5 | 86.9 | 81.7 | 97.8 | 39.4 | 24.2 | 5748.5 | 6910.3 | 4898 | 9282.1 | 11892 | 7138.2 | 1.615 | 1.721 | 1.457 | 0.771 | 0.764 | 0.74 | 5.69 | 7.18 | 6.11 | 0.704 | 0.646 | 0.679 | 5.26 | 4.3 | -5.06 | 0.666 | 0.654 | 0.625 | -3.6 | -4.24 | 5.46 | 0.693 | 0.607 | 0.673 | 5.67 | 5.4 | 5.11 | Poor_Mixed | 4898 | 7138.2 | 1.457 | 0.771 | 7.18 | 0.704 | 5.67 | 0.4826 | 0.7605 | 0.5469 | 0.6074 | 1 | 0.3647 | 0.494 | 0.5969 | 0.5969 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1390 | 884.3 | 477 | 101.1 | 111.4 | 16.8 | 748.7 | 5221.4 | 48.5 | 32.6 | 92.9 | 93.6 | 82.5 | 101.3 | 38.7 | 24.8 | 6637.9 | 6546.3 | 6385 | 10236.3 | 10994.9 | 10401 | 1.542 | 1.68 | 1.629 | 0.807 | 0.751 | 0.711 | 6.03 | -6.35 | 5.14 | 0.664 | 0.733 | 0.698 | 4.04 | 4.69 | 5.69 | 0.664 | 0.65 | 0.651 | -5.37 | 5.69 | 4.48 | 0.674 | 0.607 | 0.637 | -5.19 | 4.42 | 3.89 | Poor_Mixed | 6385 | 10236.3 | 1.542 | 0.807 | 6.35 | 0.733 | 5.69 | 0.4692 | 0.7629 | 0.4688 | 0.5865 | 1 | 0.3937 | 0.4925 | 0.5888 | 0.5888 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1391 | 223 | 197.7 | 67.5 | 59.6 | 3.4 | 458.7 | 3385.9 | 59.4 | 21.9 | 76.8 | 75 | 72.9 | 83.1 | 35.3 | 15.2 | 8798.5 | 9796.4 | 9611 | 17447.3 | 19268.8 | 18542.4 | 1.983 | 1.967 | 1.929 | 0.612 | 0.606 | 0.517 | 3.48 | -2.74 | 2.41 | 0.5 | 0.512 | 0.5 | 3.24 | 3.13 | 2.51 | 0.501 | 0.522 | 0.538 | 2.33 | -2.55 | 2 | 0.573 | 0.547 | 0.55 | -2.47 | 2.93 | -2.48 | Good_Mixed | 8798.5 | 17447.3 | 1.929 | 0.612 | 3.48 | 0.573 | 3.24 | 0.8293 | 0.9307 | 0.9257 | 0.8882 | 1 | 0.7636 | 0.847 | 0.8753 | 0.8753 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1392 | 203.8 | 168.9 | 73.6 | 58.4 | 3.6 | 392.5 | 2748.9 | 56.6 | 23.3 | 79.2 | 81.1 | 72.5 | 85.8 | 35 | 24.4 | 9367 | 9146.5 | 9936.6 | 17708.7 | 17050.6 | 19257.9 | 1.891 | 1.864 | 1.938 | 0.606 | 0.508 | 0.538 | -3.11 | 2.31 | 2.31 | 0.521 | 0.575 | 0.532 | -2 | 2 | 2.7 | 0.541 | 0.556 | 0.514 | 2.61 | 2.97 | 3.05 | 0.57 | 0.524 | 0.5 | -2.42 | -3.38 | 2.89 | Poor_Age | 9146.5 | 17050.6 | 1.864 | 0.606 | 3.11 | 0.575 | 3.38 | 0.8457 | 0.9008 | 0.8252 | 0.6005 | 1 | 0.8282 | 0.8082 | 0.8535 | 0.8535 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1393 | 435.9 | 218.5 | 77 | 79.8 | 8.5 | 450.5 | 3763.9 | 57.7 | 21.4 | 75.3 | 75 | 70 | 81.2 | 35 | 12.1 | 9517.8 | 9711.5 | 10000 | 18368.3 | 19422.9 | 19413.7 | 1.93 | 2 | 1.941 | 0.573 | 0.5 | 0.521 | 2.7 | 2.48 | 2 | 0.512 | 0.548 | 0.551 | 2.49 | 2.38 | 2 | 0.5 | 0.508 | 0.511 | 2.35 | 2.04 | 2 | 0.5 | 0.5 | 0.521 | -2.47 | 2.46 | 2.66 | Fair_DGA | 9517.8 | 18368.3 | 1.93 | 0.573 | 2.7 | 0.551 | 2.66 | 0.7076 | 0.9432 | 0.987 | 0.964 | 1 | 0.8834 | 0.8942 | 0.8816 | 0.8816 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1394 | 1000.9 | 518.6 | 108 | 132.2 | 19.1 | 832.1 | 5553.3 | 46.9 | 33.6 | 90 | 88.2 | 81.9 | 96.2 | 39 | 23.4 | 6146 | 5140.6 | 5405.7 | 9332 | 7672 | 8402.2 | 1.518 | 1.492 | 1.554 | 0.715 | 0.755 | 0.764 | 5.79 | 6.77 | 5.94 | 0.666 | 0.618 | 0.618 | 4.17 | 4.88 | 5.21 | 0.66 | 0.676 | 0.708 | 5.02 | 3.91 | 4.66 | 0.644 | 0.659 | 0.7 | 5.15 | 5.66 | 5.19 | Poor_Mixed | 5140.6 | 7672 | 1.492 | 0.764 | 6.77 | 0.708 | 5.66 | 0.4021 | 0.7509 | 0.5503 | 0.6348 | 1 | 0.3849 | 0.4944 | 0.5803 | 0.5803 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1395 | 1618.4 | 862 | 131.9 | 170.7 | 28.4 | 1272.9 | 7961.5 | 34.4 | 44.2 | 103.1 | 106.2 | 92.4 | 114.2 | 44.3 | 30.5 | 1085.1 | 1481.3 | 1602.8 | 1200 | 1669.5 | 1683 | 1.106 | 1.127 | 1.05 | 0.942 | 0.911 | 0.954 | 9.1 | 9.05 | -8.91 | 0.918 | 0.74 | 0.81 | 6.64 | 6.75 | 8.64 | 0.765 | 0.809 | 0.734 | 8.2 | 7.23 | 7.54 | 0.862 | 0.908 | 0.901 | 7.87 | -8.34 | -7.31 | Very Poor_Mixed | 1085.1 | 1200 | 1.05 | 0.954 | 9.1 | 0.918 | 8.64 | 0.1375 | 0.6376 | 0.1729 | 0.3787 | 1 | 0.0914 | 0.2227 | 0.36 | 0.36 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1396 | 328.6 | 299.8 | 85.3 | 76.1 | 8.4 | 532.9 | 3478.5 | 53.2 | 27 | 77.9 | 83.5 | 76.4 | 88.3 | 36.2 | 16.8 | 9629.9 | 9129.8 | 8231.9 | 19161.2 | 16336.5 | 15133.9 | 1.99 | 1.789 | 1.838 | 0.607 | 0.598 | 0.573 | 3.77 | 3.82 | 3.55 | 0.613 | 0.561 | 0.573 | 4.28 | 2.75 | 3.19 | 0.559 | 0.565 | 0.55 | 3.14 | 3.51 | -3.14 | 0.561 | 0.576 | 0.585 | -2.91 | 3.14 | 3.39 | Fair_Mixed | 8231.9 | 15133.9 | 1.789 | 0.607 | 3.82 | 0.613 | 4.28 | 0.697 | 0.8382 | 0.7705 | 0.8436 | 1 | 0.6805 | 0.6932 | 0.7741 | 0.7741 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1397 | 1700.9 | 934.3 | 137.7 | 173.5 | 34.3 | 1257.5 | 8001.7 | 34.3 | 44.6 | 103.2 | 106.6 | 91.7 | 112.2 | 44.7 | 32.3 | 1320 | 1387.8 | 1340.3 | 1425.7 | 1564.2 | 1549.9 | 1.08 | 1.127 | 1.156 | 0.93 | 0.944 | 0.919 | 7.87 | -8.01 | 8.86 | 0.866 | 0.776 | 0.787 | 6.33 | 5.71 | 5.47 | 0.819 | 0.945 | 0.812 | 7.96 | 9.18 | 7.35 | 0.82 | 0.721 | 0.908 | 9.2 | 5.91 | 7.74 | Very Poor_Mixed | 1320 | 1425.7 | 1.08 | 0.944 | 8.86 | 0.945 | 9.2 | 0.0914 | 0.6338 | 0.1812 | 0.3098 | 1 | 0.1339 | 0.2358 | 0.3537 | 0.3537 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1398 | 237.1 | 165.1 | 74.5 | 57 | 1.4 | 399.4 | 3216.8 | 57 | 22.3 | 82.1 | 78.9 | 73.2 | 84.4 | 35.8 | 10 | 5085.6 | 4596.1 | 5393.6 | 8115.3 | 6678.9 | 7792 | 1.596 | 1.453 | 1.445 | 0.574 | 0.595 | 0.662 | 3.66 | -3.43 | 4.08 | 0.518 | 0.608 | 0.556 | -2.65 | -3.04 | 3.09 | 0.535 | 0.52 | 0.573 | 3.15 | 2.07 | 2.87 | 0.532 | 0.532 | 0.532 | -3.36 | 2.97 | -2.74 | Poor_IR_PI | 4596.1 | 6678.9 | 1.445 | 0.662 | 4.08 | 0.608 | 3.36 | 0.8978 | 0.9215 | 0.8179 | 1 | 1 | 0.6608 | 0.7706 | 0.858 | 0.858 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1399 | 170.9 | 220 | 67.7 | 65.1 | 1 | 461.5 | 3140.5 | 57.1 | 23.8 | 75 | 75 | 70.1 | 80.9 | 36.2 | 14.4 | 6670.2 | 6192.1 | 5235.5 | 10866 | 9828.1 | 8283.4 | 1.629 | 1.587 | 1.582 | 0.598 | 0.599 | 0.607 | 3.98 | -3.16 | 3.75 | 0.509 | 0.515 | 0.55 | 3.8 | 2.72 | -2.66 | 0.578 | 0.55 | 0.566 | -2.95 | 3.23 | -2.07 | 0.571 | 0.506 | 0.575 | -2.27 | -2.8 | -2.89 | Poor_IR_PI | 5235.5 | 8283.4 | 1.582 | 0.607 | 3.98 | 0.578 | 3.8 | 0.922 | 0.8912 | 0.9886 | 0.9092 | 1 | 0.6747 | 0.775 | 0.8757 | 0.8757 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1400 | 1538.8 | 810.6 | 137.9 | 181.2 | 34.3 | 1172 | 7552.3 | 36.2 | 42.7 | 104.5 | 107.2 | 90.9 | 112.3 | 44.1 | 30.4 | 2098.1 | 2489.9 | 2392.1 | 2417 | 2961.4 | 2973.6 | 1.152 | 1.189 | 1.243 | 0.934 | 0.99 | 0.905 | 8.95 | 9.84 | 8.46 | 0.714 | 0.889 | 0.862 | 8.71 | 6.34 | 6.63 | 0.929 | 0.779 | 0.751 | 5.78 | 8.6 | -8.08 | 0.776 | 0.827 | 0.802 | 8.93 | 5.57 | 7.25 | Very Poor_Mixed | 2098.1 | 2417 | 1.152 | 0.99 | 9.84 | 0.929 | 8.93 | 0.125 | 0.6524 | 0.1791 | 0.3825 | 1 | 0.0837 | 0.245 | 0.3624 | 0.3624 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1401 | 225.2 | 178.8 | 69.7 | 54.4 | 4.1 | 358.2 | 2500 | 57 | 21.6 | 75.2 | 76.3 | 73.1 | 81 | 35.7 | 11.8 | 9636.2 | 9308.1 | 8911.9 | 18536.1 | 17981 | 16569.8 | 1.924 | 1.932 | 1.859 | 0.509 | 0.531 | 0.539 | -2 | -2 | 2.18 | 0.508 | 0.562 | 0.524 | -2.15 | 2 | 2.2 | 0.518 | 0.508 | 0.529 | -2 | 2.44 | 2 | 0.504 | 0.528 | 0.524 | 2.05 | 2 | 2.86 | Good_Mixed | 8911.9 | 16569.8 | 1.859 | 0.539 | 2.18 | 0.562 | 2.86 | 0.8518 | 0.938 | 0.9336 | 0.9703 | 1 | 0.9055 | 0.8673 | 0.9103 | 0.9103 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1402 | 467 | 379.9 | 82.5 | 80 | 9.2 | 579.9 | 3961.9 | 54.7 | 25.5 | 87.8 | 90.8 | 79.5 | 93.9 | 37.7 | 17.9 | 8318.5 | 8901.8 | 6537.8 | 15462.1 | 15785.8 | 10840 | 1.859 | 1.773 | 1.658 | 0.701 | 0.652 | 0.667 | 4.95 | 5.11 | -4.62 | 0.616 | 0.588 | 0.635 | 3.44 | -3.87 | 4.15 | 0.564 | 0.648 | 0.608 | 4.71 | 3.13 | 3.58 | 0.587 | 0.554 | 0.578 | 3.69 | 3.73 | -3.33 | Fair_Mixed | 6537.8 | 10840 | 1.658 | 0.701 | 5.11 | 0.648 | 4.71 | 0.6539 | 0.8617 | 0.5828 | 0.8114 | 1 | 0.5212 | 0.6305 | 0.7122 | 0.7122 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1403 | 974.4 | 560.1 | 103.2 | 126.4 | 14.7 | 751.5 | 5276 | 46.2 | 35.1 | 94.9 | 92.8 | 82.7 | 101 | 40.5 | 26.7 | 5579.1 | 4584.4 | 5450.9 | 8668.4 | 6725.5 | 8635.2 | 1.554 | 1.467 | 1.584 | 0.753 | 0.723 | 0.76 | 5.43 | 5.57 | 5.59 | 0.634 | 0.645 | 0.667 | -5.06 | 4.04 | 4.58 | 0.625 | 0.673 | 0.624 | 5.8 | 4.47 | 4.49 | 0.729 | 0.711 | 0.728 | 5.07 | -4.4 | 4.95 | Poor_Mixed | 4584.4 | 6725.5 | 1.467 | 0.76 | 5.59 | 0.729 | 5.8 | 0.4499 | 0.7333 | 0.4502 | 0.5192 | 1 | 0.4191 | 0.4872 | 0.5778 | 0.5778 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1404 | 100 | 269.4 | 74.5 | 58.6 | 3.2 | 430.1 | 3424 | 54.7 | 25.3 | 76 | 75 | 70.6 | 83 | 35.1 | 13.6 | 7357.6 | 9067.7 | 8792.1 | 12781.8 | 16941.3 | 16218.7 | 1.737 | 1.868 | 1.845 | 0.737 | 0.761 | 0.799 | -6.31 | 6.74 | 7.04 | 0.529 | 0.547 | 0.541 | 3.74 | 2.39 | 3.41 | 0.573 | 0.565 | 0.502 | -3.25 | 3 | 3.05 | 0.55 | 0.582 | 0.552 | 3.5 | 3.41 | 2.35 | Poor_Winding_TD_Cap | 7357.6 | 12781.8 | 1.737 | 0.799 | 7.04 | 0.582 | 3.74 | 0.8419 | 0.865 | 0.9586 | 0.9294 | 1 | 0.3387 | 0.7524 | 0.7995 | 0.7995 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1405 | 249.5 | 120 | 71.9 | 50 | 1.7 | 380.8 | 2522.6 | 57.2 | 22.2 | 75.2 | 75 | 72.1 | 80 | 35.1 | 11.8 | 9743.5 | 9429.4 | 9743.3 | 18849.5 | 17827.8 | 19069.6 | 1.935 | 1.891 | 1.957 | 0.537 | 0.579 | 0.5 | 3.19 | 2.72 | -2.57 | 0.5 | 0.5 | 0.513 | 2.45 | -3.03 | 2 | 0.51 | 0.505 | 0.5 | 2.03 | 2.02 | 2.08 | 0.553 | 0.5 | 0.537 | 2.3 | 2.11 | 2 | Good_Mixed | 9429.4 | 17827.8 | 1.891 | 0.579 | 3.19 | 0.553 | 3.03 | 0.9148 | 0.9238 | 0.9707 | 0.9703 | 1 | 0.8365 | 0.9183 | 0.9276 | 0.9276 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1406 | 545.4 | 383.1 | 85.9 | 101.5 | 4.4 | 639.3 | 4465.3 | 57.6 | 22.9 | 81.7 | 82 | 75.4 | 88.1 | 37.2 | 11.9 | 6379 | 7006.7 | 393 | 10125.2 | 11278.9 | 606.4 | 1.587 | 1.61 | 1.543 | 0.655 | 0.667 | 0.623 | 4.55 | 4.26 | 3.45 | 0.535 | 0.584 | 0.53 | -3.06 | 4.22 | 2.68 | 0.556 | 0.565 | 0.609 | 4.01 | 3.62 | 3.83 | 0.552 | 0.887 | 0.532 | 3.56 | 8.83 | -2.02 | Critical_Bushing_TD_Cap | 393 | 606.4 | 1.543 | 0.667 | 4.55 | 0.887 | 8.83 | 0.6631 | 0.9088 | 0.7517 | 0.9682 | 0.85 | 0.5945 | 0.6544 | 0.7354 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1407 | 1057.6 | 576.8 | 104.8 | 127.5 | 22.5 | 855 | 5894.6 | 44.3 | 34.3 | 91.5 | 90.5 | 84.4 | 99.4 | 38.8 | 25.2 | 5710.1 | 6002.3 | 5880.8 | 8942.9 | 8597.8 | 9782.6 | 1.566 | 1.432 | 1.663 | 0.762 | 0.721 | 0.723 | 5.95 | 5.47 | 5.8 | 0.701 | 0.661 | 0.693 | 4.04 | 5.17 | -4.7 | 0.644 | 0.644 | 0.693 | -4.81 | 4.42 | 4.37 | 0.71 | 0.714 | 0.673 | -4.65 | -5.52 | 3.27 | Poor_Mixed | 5710.1 | 8597.8 | 1.432 | 0.762 | 5.95 | 0.714 | 5.52 | 0.3721 | 0.7426 | 0.4946 | 0.5725 | 1 | 0.4162 | 0.4806 | 0.565 | 0.565 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1408 | 929.1 | 592.5 | 110.7 | 123.8 | 17.3 | 837.9 | 5261.9 | 45.8 | 38.4 | 93.8 | 95 | 84.7 | 101.5 | 41 | 24 | 4778.4 | 5890.4 | 5423.9 | 7131.7 | 8767.7 | 8459.5 | 1.492 | 1.488 | 1.56 | 0.732 | 0.719 | 0.721 | 5.6 | -6.02 | -5.97 | 0.674 | 0.669 | 0.723 | 4.75 | 4.91 | -6.11 | 0.727 | 0.705 | 0.598 | 5.71 | 4.48 | 5.49 | 0.698 | 0.698 | 0.687 | -6.58 | 4.28 | -5.38 | Poor_Mixed | 4778.4 | 7131.7 | 1.488 | 0.732 | 6.02 | 0.727 | 6.58 | 0.4187 | 0.6968 | 0.425 | 0.6143 | 1 | 0.4191 | 0.4481 | 0.5608 | 0.5608 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1409 | 982.7 | 506.7 | 106.6 | 119.8 | 16.8 | 879.8 | 5578.8 | 44.7 | 34.9 | 91.6 | 93.8 | 83.3 | 101.9 | 40.1 | 26.6 | 6389 | 6072.7 | 6908.3 | 9844.7 | 8883.3 | 11680.9 | 1.541 | 1.463 | 1.691 | 0.66 | 0.718 | 0.686 | 5.01 | 4.84 | 4.29 | 0.602 | 0.696 | 0.73 | -4.42 | 4.21 | 4.64 | 0.639 | 0.688 | 0.648 | 4.7 | 5.21 | 4.21 | 0.61 | 0.72 | 0.626 | 4.46 | -3.48 | 4.13 | Poor_Mixed | 6072.7 | 8883.3 | 1.463 | 0.718 | 5.01 | 0.73 | 5.21 | 0.4258 | 0.7356 | 0.459 | 0.5228 | 1 | 0.5176 | 0.5133 | 0.5916 | 0.5916 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1410 | 1377.7 | 824.5 | 132.7 | 166.8 | 30.1 | 1199.3 | 7848.7 | 36.3 | 41.3 | 100.4 | 101.2 | 89.4 | 109.4 | 42.7 | 29.5 | 2798.1 | 2554.6 | 3188 | 3340.3 | 3190.4 | 3851.9 | 1.194 | 1.249 | 1.208 | 0.875 | 0.895 | 0.857 | -7.5 | 8.65 | 8.17 | 0.839 | 0.837 | 0.913 | 6.32 | 5.09 | 5.35 | 0.822 | 0.753 | 0.787 | 5.56 | -5.91 | 7.45 | 0.762 | 0.806 | 0.809 | -7.18 | 8.48 | 7.48 | Very Poor_Mixed | 2554.6 | 3190.4 | 1.194 | 0.895 | 8.65 | 0.913 | 8.48 | 0.1632 | 0.6665 | 0.2692 | 0.4164 | 1 | 0.1799 | 0.2695 | 0.4022 | 0.4022 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1411 | 1468.9 | 878.8 | 141.7 | 179.6 | 34.3 | 1269.4 | 7353.7 | 35.1 | 45.9 | 107.5 | 107 | 93.9 | 116.4 | 42.8 | 32.3 | 1529.3 | 1506.7 | 1899.5 | 1643.9 | 1596.3 | 2050.9 | 1.075 | 1.059 | 1.08 | 0.911 | 0.979 | 0.921 | 8.39 | 9.78 | 8.36 | 0.785 | 0.884 | 0.742 | 6.23 | 7.77 | -7.09 | 0.751 | 0.82 | 0.826 | 7.23 | 5.53 | 7.34 | 0.688 | 0.83 | 0.937 | 7.89 | 6.05 | 6.15 | Very Poor_Mixed | 1506.7 | 1596.3 | 1.059 | 0.979 | 9.78 | 0.937 | 7.89 | 0.1126 | 0.6213 | 0.1354 | 0.3098 | 1 | 0.0998 | 0.2691 | 0.3542 | 0.3542 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1412 | 813.9 | 514.3 | 100.5 | 118.8 | 14.6 | 825.7 | 4806.7 | 45.4 | 31.8 | 93.2 | 91.4 | 81.9 | 100.4 | 40 | 23.6 | 6233.1 | 6316.6 | 5859.3 | 10068.2 | 10480.3 | 9041.6 | 1.615 | 1.659 | 1.543 | 0.697 | 0.75 | 0.703 | 4.23 | -5.87 | 5.28 | 0.677 | 0.665 | 0.637 | 4.74 | -4.65 | 4.81 | 0.71 | 0.659 | 0.686 | 5.21 | 5.95 | 4.47 | 0.761 | 0.651 | 0.705 | 4.02 | 5.32 | 5.56 | Poor_Mixed | 5859.3 | 9041.6 | 1.543 | 0.75 | 5.87 | 0.761 | 5.95 | 0.4728 | 0.7728 | 0.4811 | 0.628 | 1 | 0.4678 | 0.4631 | 0.5993 | 0.5993 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1413 | 1654.4 | 932.6 | 142.6 | 186 | 34.3 | 1301.5 | 8193.4 | 33.9 | 45.1 | 108.6 | 105.4 | 94.3 | 117.8 | 45.3 | 33.1 | 1365.3 | 1768.8 | 1283 | 1542.7 | 2031.3 | 1358.7 | 1.13 | 1.148 | 1.059 | 0.976 | 0.957 | 0.986 | 9.84 | 9.84 | 9.71 | 0.885 | 0.869 | 0.781 | -6.78 | 8.14 | 8.7 | 0.808 | 0.74 | 0.818 | 8.11 | 9.55 | 6.15 | 0.73 | 0.759 | 0.776 | 7.7 | 7.92 | 6.51 | Very Poor_Mixed | 1283 | 1358.7 | 1.059 | 0.986 | 9.84 | 0.885 | 9.55 | 0.0733 | 0.6289 | 0.1109 | 0.2787 | 1 | 0.0276 | 0.2479 | 0.3273 | 0.3273 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1414 | 721.2 | 485.4 | 96.9 | 112.2 | 17.3 | 793.1 | 5413.8 | 58.4 | 22.7 | 75.6 | 76.1 | 72.4 | 81.6 | 35.3 | 10 | 7832.6 | 9089.1 | 10000 | 14136.8 | 16703.4 | 20000 | 1.805 | 1.838 | 2 | 0.53 | 0.635 | 0.521 | 2.9 | 3.82 | 3.03 | 0.536 | 0.576 | 0.568 | 2.02 | -2.71 | -2.52 | 0.547 | 0.514 | 0.5 | 2.43 | -2.75 | 2.35 | 0.537 | 0.538 | 0.576 | 2.6 | 3.34 | 2.87 | Poor_DGA | 7832.6 | 14136.8 | 1.805 | 0.635 | 3.82 | 0.576 | 3.34 | 0.4726 | 0.9129 | 0.9341 | 1 | 1 | 0.7637 | 0.7934 | 0.7808 | 0.7808 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1415 | 100 | 230.5 | 75.2 | 67 | 3.7 | 432.8 | 3347.6 | 56.1 | 23.8 | 75.1 | 77 | 70 | 82.8 | 35 | 14.1 | 9257.2 | 9741.7 | 9811.6 | 17872.5 | 19432.2 | 19623.3 | 1.931 | 1.995 | 2 | 0.558 | 0.535 | 0.5 | -2.38 | 3.01 | -2 | 0.532 | 0.543 | 0.5 | 2.49 | 2.46 | 2.53 | 0.561 | 0.523 | 0.5 | 2.4 | 2.73 | -3.39 | 0.51 | 0.521 | 0.5 | 2 | -2.78 | -2.43 | Good_Mixed | 9257.2 | 17872.5 | 1.931 | 0.558 | 3.01 | 0.561 | 3.39 | 0.8247 | 0.8912 | 0.9537 | 0.9169 | 1 | 0.8765 | 0.866 | 0.8929 | 0.8929 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1416 | 215.9 | 192.2 | 74.5 | 66.7 | 5 | 450.7 | 2764.9 | 58.8 | 21.9 | 78 | 81.9 | 70.8 | 84.9 | 36.1 | 14.8 | 10000 | 9062.3 | 10000 | 20000 | 17391 | 20000 | 2 | 1.919 | 2 | 0.584 | 0.548 | 0.57 | 2.18 | 3.42 | 3 | 0.51 | 0.534 | 0.5 | 2 | 2.41 | 2.98 | 0.5 | 0.556 | 0.523 | 2 | -2.55 | 2.71 | 0.579 | 0.506 | 0.505 | -2.55 | 2.12 | 2.23 | Good_Mixed | 9062.3 | 17391 | 1.919 | 0.584 | 3.42 | 0.579 | 2.98 | 0.7963 | 0.9307 | 0.8466 | 0.8988 | 1 | 0.7719 | 0.8693 | 0.8649 | 0.8649 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1417 | 155.7 | 150.2 | 65 | 50 | 1 | 378.3 | 3029.6 | 57.9 | 20.9 | 78.7 | 78.2 | 71.9 | 82.1 | 35.9 | 13.1 | 10000 | 9813.9 | 9814.1 | 19824.7 | 19003.6 | 19566.3 | 1.982 | 1.936 | 1.994 | 0.5 | 0.541 | 0.56 | -2.35 | -2.85 | 2.38 | 0.572 | 0.509 | 0.525 | 3.19 | 3.04 | 2 | 0.574 | 0.551 | 0.549 | 3.15 | -2.59 | 2.08 | 0.571 | 0.525 | 0.578 | 2 | 3.02 | 2.88 | Good_Mixed | 9813.9 | 19003.6 | 1.936 | 0.56 | 2.85 | 0.578 | 3.19 | 0.9783 | 0.9574 | 0.8762 | 0.9414 | 1 | 0.8647 | 0.7712 | 0.914 | 0.914 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1418 | 1758.7 | 901.7 | 147.4 | 187.4 | 34.3 | 1313.1 | 8520.8 | 14 | 23.9 | 81.4 | 80.4 | 71.7 | 84.9 | 37.1 | 13.7 | 9242.1 | 10000 | 9477.9 | 17638.4 | 19701 | 18955.8 | 1.908 | 1.97 | 2 | 0.585 | 0.517 | 0.576 | 2.96 | 2.25 | 3.22 | 0.52 | 0.512 | 0.522 | 3.04 | -2.97 | 2.99 | 0.54 | 0.555 | 0.534 | -2.97 | 3.17 | -2.58 | 0.583 | 0.522 | 0.547 | 3.77 | 3.73 | 2.43 | Critical_DGA | 9242.1 | 17638.4 | 1.908 | 0.585 | 3.22 | 0.583 | 3.77 | 0.0587 | 0.306 | 0.8145 | 0.9269 | 1 | 0.7922 | 0.7791 | 0.5903 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
1419 | 1766 | 930.5 | 148.3 | 193.9 | 32.8 | 1379 | 8648 | 30.6 | 49.4 | 105.1 | 109.3 | 94.9 | 115.8 | 44.3 | 34.5 | 1430.9 | 690 | 1531.6 | 1593.5 | 1200 | 1712.2 | 1.114 | 1.739 | 1.118 | 0.99 | 0.951 | 0.962 | 9.75 | 9.7 | -9.83 | 0.759 | 0.9 | 0.825 | -5.53 | 6.62 | -6.11 | 0.839 | 0.9 | 0.82 | -7.59 | 8.07 | 7.11 | 0.836 | 0.986 | 0.81 | -7.68 | 7.08 | 6.6 | Very Poor_Mixed | 690 | 1200 | 1.114 | 0.99 | 9.83 | 0.986 | 8.07 | 0.0467 | 0.5888 | 0.1228 | 0.2237 | 1 | 0.033 | 0.221 | 0.3102 | 0.3102 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1420 | 1574.4 | 919.7 | 137.5 | 178.8 | 29.4 | 1229.6 | 8718.8 | 36.4 | 43.3 | 104 | 104 | 92.9 | 113.2 | 43.5 | 30.9 | 2123.1 | 2933.2 | 2052.4 | 2541.7 | 3749.7 | 2301.3 | 1.197 | 1.278 | 1.121 | 0.904 | 0.958 | 0.878 | 8.51 | 9.19 | 7.63 | 0.706 | 0.74 | 0.75 | 5.87 | 6.38 | 6.61 | 0.726 | 0.742 | 0.864 | 5.61 | 8.24 | 5.19 | 0.841 | 0.813 | 0.813 | 6.11 | 7.09 | 6.14 | Very Poor_Mixed | 2052.4 | 2301.3 | 1.121 | 0.958 | 9.19 | 0.864 | 8.24 | 0.1132 | 0.6465 | 0.1881 | 0.3635 | 1 | 0.1364 | 0.3121 | 0.3781 | 0.3781 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1421 | 300.7 | 120 | 71.2 | 63.8 | 6.2 | 502.3 | 2756.8 | 60 | 20.9 | 76.1 | 75.8 | 70.3 | 83.1 | 35 | 12.6 | 9930.3 | 9479.9 | 9903.6 | 19860.5 | 18049.3 | 19517 | 2 | 1.904 | 1.971 | 0.5 | 0.529 | 0.516 | -2 | 2.44 | 2.58 | 0.548 | 0.5 | 0.5 | 2.31 | 2.12 | 2.6 | 0.503 | 0.508 | 0.542 | 2 | 2.06 | 2 | 0.543 | 0.526 | 0.509 | -2 | 2 | 3.2 | Good_Mixed | 9479.9 | 18049.3 | 1.904 | 0.529 | 2.58 | 0.548 | 3.2 | 0.7794 | 0.9574 | 0.9461 | 0.953 | 1 | 0.9152 | 0.8862 | 0.8996 | 0.8996 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1422 | 896.9 | 470.2 | 97.5 | 107.1 | 19.3 | 740.8 | 5912.2 | 47 | 31.8 | 91.9 | 91.9 | 80.3 | 97.8 | 39.5 | 23.6 | 5178.8 | 6582.6 | 6588.5 | 7918.5 | 10881.6 | 10676 | 1.529 | 1.653 | 1.62 | 0.711 | 0.714 | 0.69 | 5.2 | 5.58 | 6.33 | 0.749 | 0.71 | 0.624 | 4.26 | 4.91 | 4.69 | 0.607 | 0.712 | 0.733 | 4.14 | 3.91 | 4.86 | 0.634 | 0.679 | 0.707 | 5 | 5.9 | 5.95 | Poor_Mixed | 5178.8 | 7918.5 | 1.529 | 0.714 | 6.33 | 0.749 | 5.95 | 0.4541 | 0.7728 | 0.5128 | 0.628 | 1 | 0.4453 | 0.4692 | 0.5957 | 0.5957 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1423 | 811.4 | 544.8 | 103.7 | 119.2 | 18.2 | 839.4 | 5294 | 45.8 | 33.3 | 91.6 | 93.2 | 84.2 | 99.5 | 39.1 | 25.6 | 4592 | 4038.5 | 4928.6 | 7057.3 | 5951.9 | 7613.7 | 1.537 | 1.474 | 1.545 | 0.686 | 0.681 | 0.719 | 5.47 | 5.63 | 5.82 | 0.627 | 0.694 | 0.648 | 4.84 | -6.26 | 5.11 | 0.685 | 0.747 | 0.624 | 4.06 | 5.68 | 3.76 | 0.675 | 0.664 | 0.675 | 4.49 | 4.92 | 4.41 | Poor_Mixed | 4038.5 | 5951.9 | 1.474 | 0.719 | 5.82 | 0.747 | 6.26 | 0.4367 | 0.7544 | 0.4755 | 0.5584 | 1 | 0.4578 | 0.4838 | 0.5864 | 0.5864 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1424 | 291 | 292.3 | 78.2 | 72 | 4.3 | 536 | 3421.6 | 55.8 | 24.5 | 76.3 | 75.9 | 70.4 | 80 | 36.3 | 12.3 | 7519.7 | 9183.4 | 9438.2 | 14075.5 | 17198.6 | 17386.4 | 1.872 | 1.873 | 1.842 | 0.768 | 0.792 | 0.78 | -5.74 | 6.6 | 6.32 | 0.528 | 0.557 | 0.529 | 2.4 | -2.57 | -2.65 | 0.53 | 0.558 | 0.539 | 3.56 | 2.95 | 2.14 | 0.564 | 0.545 | 0.5 | 2.8 | -2.78 | 2.89 | Poor_Winding_TD_Cap | 7519.7 | 14075.5 | 1.842 | 0.792 | 6.6 | 0.564 | 3.56 | 0.7602 | 0.8786 | 0.9512 | 0.9597 | 1 | 0.3523 | 0.7949 | 0.791 | 0.791 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1425 | 728.9 | 434.7 | 102.8 | 113.9 | 16.6 | 822.5 | 5081.7 | 56.3 | 23.1 | 77.7 | 75.7 | 72.2 | 80.4 | 35.9 | 13.9 | 9884.3 | 9317.2 | 9187.6 | 19612.9 | 17949.4 | 18135 | 1.984 | 1.926 | 1.974 | 0.574 | 0.589 | 0.55 | 2.65 | 3.12 | 2.45 | 0.556 | 0.517 | 0.543 | 2.92 | -3.65 | 2.69 | 0.556 | 0.513 | 0.554 | 2.57 | 2.78 | -3.1 | 0.573 | 0.571 | 0.5 | -2.52 | 2.65 | 2.91 | Poor_DGA | 9187.6 | 17949.4 | 1.926 | 0.589 | 3.12 | 0.573 | 3.65 | 0.476 | 0.9047 | 0.92 | 0.9219 | 1 | 0.7742 | 0.784 | 0.7752 | 0.7752 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1426 | 100 | 208.1 | 72 | 61.5 | 1 | 423.9 | 2994 | 26.3 | 49.4 | 79 | 80.8 | 71.1 | 85.1 | 35.9 | 13.3 | 5537.9 | 4792.1 | 5061.6 | 8508.5 | 7074.1 | 7582.5 | 1.536 | 1.476 | 1.498 | 0.704 | 0.676 | 0.663 | -4.73 | -5.08 | 4.39 | 0.535 | 0.593 | 0.526 | 2.85 | 2.48 | 2.32 | 0.585 | 0.5 | 0.548 | 2.41 | 2.3 | 3.57 | 0.533 | 0.5 | 0.539 | 2.68 | -2.37 | 3.11 | Critical_Oil | 4792.1 | 7074.1 | 1.476 | 0.704 | 5.08 | 0.593 | 3.57 | 0.9433 | 0.0054 | 0.8428 | 0.9367 | 1 | 0.5229 | 0.808 | 0.7462 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1427 | 883.1 | 537.1 | 105.1 | 120.2 | 15.9 | 843.2 | 5362.6 | 48.2 | 31 | 92 | 89.7 | 81 | 100.1 | 39.1 | 25.1 | 6212.1 | 5966.1 | 6206.9 | 9555 | 9603.5 | 10101.5 | 1.538 | 1.61 | 1.627 | 0.724 | 0.705 | 0.733 | 5.5 | 4.77 | 5.44 | 0.598 | 0.706 | 0.709 | 4.15 | 3.85 | 4.55 | 0.695 | 0.61 | 0.625 | -5.15 | 6.1 | -5.27 | 0.689 | 0.735 | 0.631 | 5.2 | 4.24 | -4.65 | Poor_Mixed | 5966.1 | 9555 | 1.538 | 0.733 | 5.5 | 0.735 | 6.1 | 0.4435 | 0.7829 | 0.5129 | 0.576 | 1 | 0.4572 | 0.493 | 0.5977 | 0.5977 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1428 | 1402.1 | 868.4 | 128.9 | 169 | 27.1 | 1214.6 | 7523.8 | 38.7 | 42.9 | 102.9 | 103.9 | 90.5 | 112.7 | 43.9 | 37.3 | 2814.4 | 3228 | 2967.5 | 2071.4 | 4097 | 3844.5 | 0.736 | 1.269 | 1.296 | 0.933 | 0.948 | 0.922 | 8.72 | 8.49 | 9.14 | 0.758 | 0.865 | 0.792 | 8.02 | 6.51 | -6.5 | 0.809 | 0.713 | 0.723 | 6.5 | 5.91 | 5.75 | 0.831 | 0.738 | 0.722 | 6.41 | 7.11 | 7.18 | Critical_Mixed | 2814.4 | 2071.4 | 0.736 | 0.948 | 9.14 | 0.865 | 8.02 | 0.1744 | 0.6504 | 0.2081 | 0.1112 | 0.8187 | 0.1042 | 0.3068 | 0.3488 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1429 | 723.3 | 393.7 | 95.1 | 100.2 | 14.9 | 759.2 | 4625.3 | 50.2 | 28 | 81.7 | 82 | 77.3 | 89.8 | 38.2 | 18.8 | 5835.4 | 7425.8 | 6671.7 | 9319.4 | 12501.5 | 10988.5 | 1.597 | 1.684 | 1.647 | 0.677 | 0.591 | 0.63 | 3.96 | 4.22 | 3.33 | 0.659 | 0.602 | 0.575 | -3.72 | 3.59 | 3.32 | 0.613 | 0.61 | 0.699 | -3.97 | 3.44 | -4.3 | 0.653 | 0.586 | 0.733 | 3.18 | 5.28 | -4.42 | Fair_Mixed | 5835.4 | 9319.4 | 1.597 | 0.677 | 4.22 | 0.733 | 5.28 | 0.5244 | 0.8235 | 0.7237 | 0.7841 | 1 | 0.6279 | 0.5678 | 0.6916 | 0.6916 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1430 | 611.4 | 394 | 91.8 | 86.3 | 10.8 | 598.2 | 3578.7 | 60 | 20.2 | 80.1 | 80.9 | 73.6 | 86.5 | 35.9 | 13.4 | 8283.4 | 10000 | 9523.8 | 15368.5 | 20000 | 18061 | 1.855 | 2 | 1.896 | 0.575 | 0.5 | 0.538 | 2.77 | 2.18 | 2 | 0.534 | 0.514 | 0.526 | 2.95 | 2.45 | -2 | 0.505 | 0.551 | 0.515 | 2.34 | 2.29 | 2.09 | 0.5 | 0.5 | 0.54 | -2.26 | -2 | 2.04 | Fair_DGA | 8283.4 | 15368.5 | 1.855 | 0.575 | 2.77 | 0.551 | 2.95 | 0.6126 | 0.984 | 0.8027 | 0.9342 | 1 | 0.8774 | 0.8791 | 0.8393 | 0.8393 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1431 | 893.7 | 517.8 | 104.9 | 123.2 | 19 | 883.5 | 5688.2 | 46.5 | 32.4 | 88.1 | 90.8 | 81.8 | 97.6 | 40.8 | 25.9 | 5597.5 | 5489.8 | 4839.1 | 8205.3 | 8311.3 | 6900.3 | 1.466 | 1.514 | 1.426 | 0.781 | 0.685 | 0.782 | 6.36 | 4.91 | 6.45 | 0.623 | 0.753 | 0.637 | 5.12 | 3.84 | -4.27 | 0.746 | 0.603 | 0.649 | -6.53 | 6.23 | 6.04 | 0.735 | 0.662 | 0.7 | 4.09 | -5.1 | -5.84 | Poor_Mixed | 4839.1 | 6900.3 | 1.426 | 0.782 | 6.45 | 0.753 | 6.53 | 0.4141 | 0.7654 | 0.5279 | 0.5478 | 1 | 0.3967 | 0.4628 | 0.5744 | 0.5744 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1432 | 401.8 | 274.9 | 71.5 | 64.2 | 1.1 | 494.6 | 2805.8 | 28.6 | 29.5 | 81.6 | 77.8 | 75.4 | 88.3 | 37.4 | 15.2 | 7641.6 | 6907.5 | 7078.5 | 13397.5 | 11195.2 | 12110.5 | 1.753 | 1.621 | 1.711 | 0.619 | 0.6 | 0.606 | 2.95 | 2.86 | 3.69 | 0.973 | 0.572 | 0.596 | -9.45 | 2.87 | -4.05 | 0.569 | 0.623 | 0.54 | -4.38 | 3.54 | -3.8 | 0.574 | 0.587 | 0.605 | -3.85 | 2.87 | 4.3 | Critical_Bushing_TD_Cap | 6907.5 | 11195.2 | 1.621 | 0.619 | 3.69 | 0.973 | 9.45 | 0.8652 | 0.2193 | 0.7875 | 0.8882 | 1 | 0.6963 | 0.5867 | 0.7289 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1433 | 409.2 | 151.8 | 79.4 | 76.3 | 3.6 | 517.2 | 3435 | 30.6 | 49.4 | 88.1 | 82.9 | 78.1 | 93.5 | 38 | 15.7 | 4596.2 | 5899 | 5912.4 | 6645.5 | 8731.6 | 9287.5 | 1.446 | 1.48 | 1.571 | 0.691 | 0.629 | 0.66 | 5.29 | -4.11 | 5.38 | 0.536 | 0.5 | 0.523 | -2.33 | 2.16 | 2.14 | 0.529 | 0.529 | 0.52 | 2.69 | 2.67 | 2 | 0.5 | 0.546 | 1.043 | 2.41 | -2.11 | -2.4 | Critical_Oil | 4596.2 | 6645.5 | 1.446 | 0.691 | 5.38 | 1.043 | 2.69 | 0.7741 | 0.5888 | 0.6463 | 0.8746 | 1 | 0.5334 | 0.8011 | 0.7514 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_B_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1434 | 100 | 120 | 65.4 | 51.4 | 1 | 407.8 | 2500 | 57.2 | 21.7 | 77.3 | 75 | 70 | 83.2 | 35 | 13.8 | 9809.4 | 9423.3 | 9356.7 | 19424.6 | 18782.5 | 17782.6 | 1.98 | 1.993 | 1.901 | 0.578 | 0.522 | 0.5 | 2.81 | -2 | 2.31 | 0.529 | 0.5 | 0.559 | 2.4 | 2.26 | 2 | 0.563 | 0.553 | 0.5 | -2.38 | -3.21 | -2.58 | 0.565 | 0.514 | 0.538 | 2.57 | 2.26 | -3.09 | Good_Mixed | 9356.7 | 17782.6 | 1.901 | 0.578 | 2.81 | 0.565 | 3.21 | 0.9813 | 0.9355 | 0.9516 | 0.9244 | 1 | 0.8822 | 0.8247 | 0.9309 | 0.9309 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
1435 | 100 | 175.2 | 70.7 | 51.9 | 1.2 | 398.4 | 2549 | 56.5 | 21.9 | 75.6 | 77.6 | 72.4 | 83.6 | 35.2 | 15.3 | 9984.3 | 9482.2 | 9536.2 | 19968.6 | 18553.2 | 18340.3 | 2 | 1.957 | 1.923 | 0.527 | 0.5 | 0.524 | -2 | 2.16 | 2 | 0.559 | 0.543 | 0.534 | 2 | 2.56 | 2.05 | 0.5 | 0.5 | 0.5 | 2 | 2.4 | 2.29 | 0.511 | 0.5 | 0.529 | 2 | -2.46 | -2.3 | Good_Mixed | 9482.2 | 18340.3 | 1.923 | 0.527 | 2.16 | 0.559 | 2.56 | 0.9403 | 0.9307 | 0.9075 | 0.8855 | 1 | 0.9346 | 0.8966 | 0.934 | 0.934 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1436 | 486.1 | 302.5 | 84.5 | 73.2 | 10.9 | 486.3 | 3393.3 | 56.8 | 25.5 | 79.8 | 81.6 | 78.4 | 88.5 | 37.8 | 16.9 | 7704.2 | 7937.2 | 6633.3 | 13202.6 | 14585.2 | 10897 | 1.714 | 1.838 | 1.643 | 0.618 | 0.579 | 0.594 | 3.85 | 3.33 | 4.26 | 0.561 | 0.561 | 0.573 | 2.58 | 3.32 | -3.81 | 0.636 | 0.581 | 0.557 | 3.4 | 3.8 | 3.18 | 0.616 | 0.556 | 0.585 | 3.38 | -3.75 | -2.81 | Fair_Mixed | 6633.3 | 10897 | 1.643 | 0.618 | 4.26 | 0.636 | 3.81 | 0.6718 | 0.8617 | 0.744 | 0.8407 | 1 | 0.6693 | 0.6754 | 0.7631 | 0.7631 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1437 | 334.6 | 241.3 | 77.6 | 71.4 | 1 | 453.3 | 3289 | 56 | 24.5 | 80 | 82.6 | 76.3 | 89.8 | 37.4 | 14.9 | 346.7 | 7121.4 | 8616.6 | 352.4 | 12833.8 | 15505.1 | 1.016 | 1.802 | 1.799 | 0.901 | 0.952 | 0.99 | 9.24 | 8.64 | 9.31 | 0.592 | 0.561 | 0.584 | 2.81 | 2.78 | 2.9 | 0.582 | 0.506 | 0.543 | 3.52 | 2.81 | 2.5 | 0.523 | 0.58 | 0.554 | 2.71 | 2.6 | 2.5 | Critical_Winding_TD_Cap | 346.7 | 352.4 | 1.016 | 0.99 | 9.31 | 0.592 | 3.52 | 0.8892 | 0.8786 | 0.7449 | 0.8962 | 0.85 | 0.0815 | 0.7477 | 0.729 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_TV_TanDelta_pct
1438 | 920.6 | 474.7 | 101.9 | 118.8 | 15.2 | 845.8 | 5378.1 | 54.4 | 22.1 | 75.7 | 79.5 | 70.7 | 81.6 | 35.2 | 13.5 | 8049.8 | 10000 | 9557.9 | 14286.2 | 19924.6 | 18994.9 | 1.775 | 1.992 | 1.987 | 0.575 | 0.537 | 0.5 | 3.08 | 3.33 | 2 | 0.533 | 0.528 | 0.552 | 2.56 | 2.7 | 2.74 | 0.504 | 0.51 | 0.5 | 2.92 | 2.64 | 2.68 | 0.5 | 0.553 | 0.533 | -2.59 | 2 | 3.01 | Poor_DGA | 8049.8 | 14286.2 | 1.775 | 0.575 | 3.33 | 0.553 | 3.01 | 0.4555 | 0.926 | 0.9146 | 0.9318 | 1 | 0.8435 | 0.8505 | 0.7942 | 0.7942 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1439 | 622.6 | 372.4 | 91.7 | 97.6 | 14.8 | 704.3 | 3962.3 | 50.7 | 30.3 | 83 | 85.1 | 76.9 | 88.6 | 38.6 | 19.1 | 6330.7 | 5955.3 | 6816.2 | 10194.6 | 10190.3 | 11212.7 | 1.61 | 1.711 | 1.645 | 0.667 | 0.662 | 0.666 | 4.09 | 5.07 | 4.51 | 0.655 | 0.556 | 0.581 | -3.47 | 2.99 | 4.02 | 0.629 | 0.58 | 0.593 | 3.88 | 3.47 | 3.68 | 0.579 | 0.657 | 0.63 | 3.51 | -3.96 | -2.64 | Fair_Mixed | 5955.3 | 10190.3 | 1.61 | 0.667 | 5.07 | 0.657 | 4.02 | 0.5538 | 0.792 | 0.6962 | 0.7749 | 1 | 0.5488 | 0.6261 | 0.6914 | 0.6914 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1440 | 279.7 | 248.3 | 72.2 | 119.7 | 1 | 471.6 | 3334.9 | 54.3 | 23.7 | 95.9 | 98.8 | 84.8 | 102.7 | 40.5 | 11.8 | 9026.8 | 10000 | 8963.6 | 18053.7 | 20000 | 16415.4 | 2 | 2 | 1.831 | 0.589 | 0.544 | 0.581 | 2.89 | 2.34 | -3.16 | 0.508 | 0.5 | 0.508 | 3.23 | 2.34 | 2.88 | 0.515 | 0.517 | 0.517 | 2.32 | 2.75 | -2.27 | 0.548 | 0.512 | 0.531 | 2.44 | -2.44 | 2.81 | Poor_Thermal | 8963.6 | 16415.4 | 1.831 | 0.589 | 3.16 | 0.548 | 3.23 | 0.8406 | 0.8931 | 0.3858 | 0.9703 | 1 | 0.7707 | 0.8627 | 0.8276 | 0.8276 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1441 | 786.9 | 534.9 | 100.3 | 116.8 | 16.1 | 782.8 | 5241.5 | 57.9 | 22.3 | 78.3 | 75.4 | 72.3 | 80.9 | 36.3 | 13.6 | 10000 | 10000 | 8591.5 | 19473.8 | 19349.3 | 15952.9 | 1.947 | 1.935 | 1.857 | 0.522 | 0.582 | 0.59 | 2.28 | 2.88 | -3.13 | 0.5 | 0.515 | 0.6 | 2.64 | 2.43 | 2.63 | 0.551 | 0.586 | 0.541 | 2 | -2 | 2 | 0.545 | 0.536 | 0.531 | -2.41 | 2.17 | -2 | Poor_DGA | 8591.5 | 15952.9 | 1.857 | 0.59 | 3.13 | 0.6 | 2.64 | 0.4656 | 0.9215 | 0.9133 | 0.9294 | 1 | 0.7864 | 0.8128 | 0.7812 | 0.7812 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1442 | 360.1 | 225.4 | 77.3 | 59.5 | 1 | 486.8 | 3337.5 | 32.6 | 47.8 | 79.3 | 78.7 | 73.7 | 84 | 36.5 | 13.4 | 6004.3 | 5440.6 | 4718 | 9786.7 | 8070.7 | 6797.2 | 1.63 | 1.483 | 1.441 | 0.644 | 2.358 | 0.67 | 4.68 | 4.94 | 4.47 | 0.525 | 0.593 | 0.637 | 2.97 | 3.41 | -4.93 | 0.625 | 0.57 | 0.558 | 3.65 | -3.66 | 3.59 | 0.605 | 0.61 | 0.609 | -3.49 | -4.64 | 3.6 | Critical_Oil | 4718 | 6797.2 | 1.441 | 2.358 | 4.94 | 0.637 | 4.93 | 0.9 | 0.6035 | 0.838 | 0.9342 | 1 | 0.4592 | 0.6401 | 0.7674 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | Moisture_PPM
1443 | 447.1 | 322.6 | 78.8 | 72.6 | 6.4 | 475.7 | 3581.6 | 55.3 | 24.7 | 83.6 | 85 | 76.1 | 90.6 | 37.2 | 15.3 | 690 | 1651.6 | 1222 | 737.4 | 1684.7 | 1246.4 | 1.069 | 1.02 | 1.02 | 0.766 | 0.719 | 0.722 | -6.61 | 4.79 | -5.34 | 0.597 | 0.561 | 0.63 | 2.93 | -22.35 | 3.27 | 0.624 | 0.588 | 0.614 | 3.44 | -2.68 | -2.9 | 0.509 | 0.5 | 0.561 | 4.06 | -3.13 | 3.68 | Critical_IR_PI | 690 | 737.4 | 1.02 | 0.766 | 6.61 | 0.63 | 22.35 | 0.7215 | 0.8751 | 0.6961 | 0.8855 | 0.925 | 0.4255 | 0.6798 | 0.7292 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_HV_Y_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
1444 | 996.3 | 567.7 | 106.3 | 125.9 | 14.9 | 893.1 | 5286.6 | 45 | 33.2 | 91 | 87.7 | 82.7 | 98.2 | 38.4 | 27.2 | 5710.2 | 5590.8 | 6698.3 | 8094.4 | 8784.1 | 10138.3 | 1.418 | 1.571 | 1.514 | 0.756 | 0.736 | 0.707 | 6.55 | 5.46 | 6.47 | 0.647 | 0.585 | 0.589 | 4.5 | 3.77 | 4.69 | 0.665 | 0.601 | 0.701 | 4.82 | 3.93 | -5.06 | 0.721 | 0.658 | 0.682 | 5.16 | 4.7 | 4.52 | Poor_Mixed | 5590.8 | 8094.4 | 1.418 | 0.756 | 6.55 | 0.721 | 5.16 | 0.4264 | 0.7556 | 0.5357 | 0.5011 | 1 | 0.3954 | 0.523 | 0.5854 | 0.5854 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1445 | 1665.2 | 956.2 | 148.3 | 197 | 59.3 | 1379 | 8820.4 | 53.5 | 26.3 | 83.2 | 85.5 | 75.3 | 89.6 | 37.8 | 10.6 | 8569.6 | 8554 | 9489.4 | 15861.7 | 15810.7 | 18211.7 | 1.851 | 1.848 | 1.919 | 0.533 | 0.526 | 0.586 | 2.75 | 2.57 | 4.4 | 0.519 | 0.529 | 0.509 | -2 | 3.01 | 2.16 | 0.547 | 0.539 | 0.552 | 2.52 | 2.47 | 2.69 | 0.563 | 0.568 | 0.562 | 2 | 2.73 | 2.01 | Critical_DGA | 8554 | 15810.7 | 1.848 | 0.586 | 4.4 | 0.568 | 3.01 | 0.0368 | 0.8489 | 0.7032 | 0.9925 | 1 | 0.7799 | 0.7993 | 0.6441 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1446 | 433.3 | 276.2 | 85.7 | 75.8 | 7.5 | 505.1 | 3471.7 | 51.2 | 27.9 | 84.5 | 84.2 | 76 | 89.4 | 38.7 | 19 | 7747.6 | 6797 | 7639.8 | 13546.8 | 11583.2 | 13559.6 | 1.749 | 1.704 | 1.775 | 0.597 | 0.645 | 0.644 | 3.66 | 3.9 | 4.96 | 0.601 | 0.594 | 0.589 | 3.18 | 3.28 | 3.1 | 0.573 | 0.584 | 0.547 | 4.15 | 2.87 | -3.29 | 0.54 | 0.569 | 0.556 | 2.32 | 3.41 | 3.12 | Fair_Mixed | 6797 | 11583.2 | 1.704 | 0.645 | 4.96 | 0.601 | 4.15 | 0.7037 | 0.825 | 0.6934 | 0.778 | 1 | 0.6109 | 0.6959 | 0.7539 | 0.7539 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1447 | 1760 | 883.7 | 138.9 | 186.1 | 33.7 | 1323.2 | 8432.9 | 34.7 | 45.5 | 107.1 | 103.6 | 93 | 114.3 | 44.2 | 35.8 | 2243.8 | 1130.8 | 2491.7 | 2851.3 | 1200 | 2995.4 | 1.271 | 1.061 | 1.202 | 0.927 | 0.932 | 0.918 | 8.31 | 8.52 | 8.39 | 0.869 | 0.776 | 0.712 | 7.49 | 5.21 | 8.17 | 0.88 | 0.724 | 0.836 | 6.21 | 7.56 | 5.82 | 0.756 | 0.758 | 0.773 | -6.61 | -5.87 | 8.1 | Very Poor_Mixed | 1130.8 | 1200 | 1.061 | 0.932 | 8.52 | 0.88 | 8.17 | 0.0711 | 0.6251 | 0.162 | 0.1718 | 1 | 0.1292 | 0.2885 | 0.3476 | 0.3476 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1448 | 965.9 | 584.3 | 112.1 | 121.8 | 19.7 | 872.3 | 5292.9 | 50.5 | 30.5 | 89.5 | 87 | 82.7 | 96 | 38.8 | 24 | 5540.8 | 5612.6 | 5399.6 | 8234.6 | 9006 | 8265.4 | 1.486 | 1.605 | 1.531 | 0.717 | 0.798 | 0.765 | -5.51 | 6.26 | -6.34 | 0.679 | 0.652 | 0.602 | -5.39 | 4.5 | 5.58 | 0.586 | 0.746 | 0.705 | -5.21 | -4.31 | 4.31 | 0.643 | 0.59 | 0.721 | 4.07 | 4.71 | -4.97 | Poor_Mixed | 5399.6 | 8234.6 | 1.486 | 0.798 | 6.34 | 0.746 | 5.58 | 0.3984 | 0.7894 | 0.5591 | 0.6143 | 1 | 0.3794 | 0.5055 | 0.5851 | 0.5851 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1449 | 300.6 | 127.7 | 70.5 | 66.7 | 2.8 | 423.5 | 3128.8 | 59 | 22.8 | 75 | 75.8 | 72.9 | 81.1 | 35.9 | 13.3 | 9761.3 | 10000 | 9449.3 | 19522.6 | 20000 | 18426.1 | 2 | 2 | 1.95 | 0.5 | 0.502 | 0.524 | 2 | 2 | 2 | 0.532 | 0.546 | 0.561 | -2.56 | 2 | 2.16 | 0.562 | 0.5 | 0.543 | -2 | -2.53 | 2.22 | 0.548 | 0.54 | 0.53 | 2.87 | 3 | 2.8 | Good_Mixed | 9449.3 | 18426.1 | 1.95 | 0.524 | 2 | 0.562 | 3 | 0.8379 | 0.9108 | 0.9455 | 0.9367 | 1 | 0.9646 | 0.8069 | 0.9005 | 0.9005 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1450 | 1579.2 | 816.2 | 138.8 | 187.4 | 34.3 | 1379 | 8315.1 | 34.3 | 48.1 | 106.6 | 106.9 | 96.7 | 116.1 | 44.3 | 35.8 | 1398.9 | 1305.6 | 690 | 1473.2 | 1526 | 1200 | 1.053 | 1.169 | 1.739 | 0.948 | 0.967 | 0.954 | 9.52 | 9.79 | -9.36 | 0.964 | 0.748 | 0.847 | -7.49 | 7.67 | 5.38 | 0.703 | 0.686 | 0.689 | -8.84 | -5.8 | 7.59 | 0.766 | 0.798 | 0.86 | -6.59 | 7.5 | 5.4 | Very Poor_Mixed | 690 | 1200 | 1.053 | 0.967 | 9.79 | 0.964 | 8.84 | 0.0832 | 0.6007 | 0.1162 | 0.1718 | 1 | 0.0506 | 0.29 | 0.3324 | 0.3324 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1451 | 1656.5 | 918.7 | 136.6 | 185.8 | 34.3 | 1329.3 | 8244.1 | 36 | 46.1 | 105.5 | 105.6 | 91.7 | 114 | 43.9 | 32.2 | 1617.2 | 824.8 | 1600.6 | 1798.1 | 1200 | 1768.1 | 1.112 | 1.455 | 1.105 | 0.983 | 0.935 | 0.99 | 9.51 | 8.82 | 9.68 | 0.923 | 0.796 | 0.904 | 7.97 | -6.63 | 8.47 | 0.757 | 0.786 | 0.805 | 8.05 | 9 | 5.44 | 0.835 | 0.726 | 0.858 | 7.34 | -7.69 | 8.51 | Very Poor_Mixed | 824.8 | 1200 | 1.105 | 0.99 | 9.68 | 0.923 | 9 | 0.0759 | 0.6194 | 0.1707 | 0.3137 | 1 | 0.0531 | 0.2264 | 0.3343 | 0.3343 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1452 | 168.5 | 203.5 | 69.2 | 50.3 | 5.2 | 438.5 | 2997.1 | 58.3 | 20 | 77 | 75.2 | 70 | 83.8 | 35.8 | 13.8 | 9355.2 | 9981.3 | 8223 | 17971.2 | 18352.4 | 14660.8 | 1.921 | 1.839 | 1.783 | 0.509 | 0.52 | 0.542 | 2.47 | -2.37 | -3.25 | 0.56 | 0.5 | 0.578 | 2.75 | 3.1 | -2.39 | 0.51 | 0.5 | 0.603 | 2.36 | 2.56 | -2.72 | 0.554 | 0.552 | 0.524 | 2.06 | 2 | 2.81 | Good_Mixed | 8223 | 14660.8 | 1.783 | 0.542 | 3.25 | 0.603 | 3.1 | 0.8305 | 1 | 0.9436 | 0.9244 | 1 | 0.8605 | 0.8138 | 0.8952 | 0.8952 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1453 | 173.7 | 195.1 | 66.2 | 66.8 | 1 | 361.1 | 2514.9 | 57.8 | 20 | 76.2 | 79 | 72.5 | 84.9 | 36.2 | 13 | 7211 | 6966.3 | 7694.3 | 12264.1 | 11717.9 | 13350.9 | 1.701 | 1.682 | 1.735 | 0.6 | 0.531 | 0.554 | 3.03 | -2.7 | 2.34 | 0.505 | 0.522 | 0.546 | 2 | -2 | 3.37 | 0.546 | 0.511 | 0.5 | 2.43 | 2.38 | 2.35 | 0.522 | 0.5 | 0.512 | 2.01 | 2.04 | 2.75 | Fair_IR_PI | 6966.3 | 11717.9 | 1.682 | 0.6 | 3.03 | 0.546 | 3.37 | 0.9455 | 1 | 0.8742 | 0.9438 | 1 | 0.7942 | 0.8819 | 0.9209 | 0.9209 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
1454 | 1667 | 905.5 | 139.8 | 188 | 34 | 1256.4 | 7939.3 | 31.4 | 47.7 | 105 | 105.3 | 91.4 | 112.1 | 44.4 | 33.1 | 1585.7 | 2135.1 | 2106.7 | 1878 | 2473.9 | 2411 | 1.184 | 1.159 | 1.144 | 0.981 | 0.976 | 0.905 | 9.12 | 9.51 | 8.75 | 0.811 | 0.701 | 0.977 | -7.79 | -8.36 | 6.18 | 0.767 | 0.987 | 0.791 | 7.58 | 6.33 | -7.14 | 0.746 | 0.93 | 0.94 | -6.93 | 5.94 | 5.67 | Very Poor_Mixed | 1585.7 | 1878 | 1.144 | 0.981 | 9.51 | 0.987 | 8.36 | 0.0855 | 0.6044 | 0.1827 | 0.2787 | 1 | 0.074 | 0.2295 | 0.3378 | 0.3378 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1455 | 125.4 | 187.1 | 65 | 61.2 | 1 | 375.6 | 2843.4 | 58.3 | 20 | 77.3 | 75.1 | 71.9 | 82.9 | 35.8 | 11.1 | 5231.5 | 6871.3 | 6683.8 | 7500 | 10968.7 | 10687.3 | 1.434 | 1.596 | 1.599 | 0.644 | 0.6 | 0.661 | 3.61 | 3.67 | 4 | 0.5 | 0.513 | 0.5 | 2.92 | 2.47 | 2 | 0.504 | 0.502 | 0.519 | 2.59 | -2.59 | 2.17 | 0.555 | 0.538 | 0.55 | -2.35 | 2.69 | -2 | Fair_IR_PI | 5231.5 | 7500 | 1.434 | 0.661 | 4 | 0.555 | 2.92 | 0.9561 | 1 | 0.925 | 0.984 | 1 | 0.6288 | 0.877 | 0.9066 | 0.9066 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1456 | 1200.6 | 577.6 | 112.9 | 129.1 | 22.9 | 968.9 | 6167.7 | 58.8 | 20 | 78.3 | 81.7 | 74 | 83.8 | 35.3 | 15.3 | 8083.9 | 9358.5 | 9346.5 | 14548.9 | 18355.9 | 18312.7 | 1.8 | 1.961 | 1.959 | 0.57 | 0.55 | 0.513 | 3.02 | 3.19 | 2 | 0.578 | 0.507 | 0.545 | 2.79 | 2.35 | 2.87 | 0.5 | 0.557 | 0.537 | 2 | 2.52 | -2.33 | 0.571 | 0.534 | 0.523 | 2.87 | 2.43 | 2.57 | Poor_DGA | 8083.9 | 14548.9 | 1.8 | 0.57 | 3.19 | 0.578 | 2.87 | 0.3348 | 1 | 0.8253 | 0.8855 | 1 | 0.8228 | 0.8103 | 0.7515 | 0.7515 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1457 | 1633.1 | 976.5 | 148.3 | 188.2 | 32.7 | 1303.9 | 8457.4 | 35 | 46.7 | 107.5 | 104.1 | 92.3 | 113.5 | 44.2 | 32.5 | 1826.9 | 2393.7 | 2502.6 | 2162.7 | 2767.1 | 3192.9 | 1.184 | 1.156 | 1.276 | 0.922 | 0.914 | 0.897 | 8.44 | 8.61 | -8.96 | 0.812 | 0.786 | 0.8 | -5.83 | 6.64 | 7.44 | 0.729 | 0.723 | 0.843 | 5 | 6.33 | -4.92 | 0.956 | 0.889 | 0.889 | -7.76 | 8.47 | -5.64 | Very Poor_Mixed | 1826.9 | 2162.7 | 1.156 | 0.922 | 8.96 | 0.956 | 8.47 | 0.0669 | 0.6137 | 0.165 | 0.302 | 1 | 0.126 | 0.2644 | 0.3472 | 0.3472 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1458 | 586.8 | 306.7 | 86 | 69.7 | 2.7 | 430.1 | 3796.9 | 43.5 | 36.7 | 79.3 | 78.1 | 73.4 | 85 | 36.7 | 16.3 | 5662.6 | 8564.8 | 6545.6 | 8894.2 | 14711.7 | 11366.1 | 1.571 | 1.718 | 1.736 | 0.596 | 0.564 | 0.587 | 3.68 | -4.14 | -4.09 | 0.537 | 0.512 | 0.514 | -2 | 2.83 | 2.53 | 0.515 | 0.551 | 0.513 | 2 | 2.44 | 2.21 | 0.5 | 0.5 | 0.506 | 2 | 2.06 | 2 | Poor_Oil | 5662.6 | 8894.2 | 1.571 | 0.596 | 4.14 | 0.551 | 2.83 | 0.7733 | 0.7153 | 0.8402 | 0.8578 | 1 | 0.6781 | 0.8948 | 0.8221 | 0.8221 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1459 | 346.3 | 332 | 82.6 | 147.5 | 6.6 | 636.5 | 3415.5 | 54.5 | 26.6 | 109.2 | 109.3 | 116.1 | 118.6 | 45 | 12 | 7046.6 | 8517.9 | 7933.7 | 11825.9 | 16046.8 | 13959.4 | 1.678 | 1.884 | 1.76 | 0.644 | 0.629 | 0.684 | 4.92 | 4.18 | -4.47 | 0.51 | 0.5 | 0.5 | 2.41 | 3.17 | 2.41 | 0.568 | 0.505 | 0.561 | -3.2 | 3.02 | -2.06 | 0.529 | 0.5 | 0.53 | -2.13 | 2.09 | 2.11 | Critical_Thermal | 7046.6 | 11825.9 | 1.678 | 0.684 | 4.92 | 0.568 | 3.2 | 0.6251 | 0.8443 | 0.0536 | 0.9661 | 1 | 0.5642 | 0.8706 | 0.7069 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | C2H2
1460 | 208.3 | 174.7 | 66.5 | 50.4 | 1.6 | 392.5 | 2667.2 | 58.2 | 22.8 | 75.4 | 76.2 | 70 | 80 | 35.9 | 11.6 | 6724.7 | 6609.6 | 8005.4 | 10815.1 | 11296.4 | 14046.8 | 1.608 | 1.709 | 1.755 | 0.555 | 0.597 | 0.622 | 3.04 | 4.01 | -4.11 | 0.5 | 0.506 | 0.524 | 2.7 | 2.19 | 2 | 0.513 | 0.538 | 0.5 | 2 | 2.83 | 2.08 | 0.5 | 0.534 | 0.5 | 2.57 | 2 | 2.13 | Fair_IR_PI | 6609.6 | 10815.1 | 1.608 | 0.622 | 4.11 | 0.538 | 2.83 | 0.9137 | 0.9108 | 0.9679 | 0.9744 | 1 | 0.6841 | 0.9135 | 0.9034 | 0.9034 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1461 | 100 | 120 | 65 | 74.9 | 1 | 384.2 | 2604.8 | 58.1 | 21.7 | 87.7 | 85.4 | 78.1 | 91.4 | 38.4 | 11.4 | 9595.5 | 10000 | 9003.5 | 18710.4 | 19084.5 | 18007 | 1.95 | 1.908 | 2 | 0.513 | 0.5 | 0.506 | 2 | 2.33 | -2.11 | 0.5 | 0.53 | 0.542 | 2.71 | 2.47 | -2.37 | 0.555 | 0.53 | 0.5 | 2.05 | -2.47 | 2.03 | 0.529 | 0.564 | 0.5 | 2.62 | 2.93 | 2.55 | Fair_Thermal | 9003.5 | 18007 | 1.908 | 0.513 | 2.33 | 0.564 | 2.93 | 0.9491 | 0.9355 | 0.6385 | 0.9783 | 1 | 0.9531 | 0.8528 | 0.9092 | 0.9092 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_HV
1462 | 211.8 | 239 | 76.6 | 55.6 | 1.4 | 474.9 | 3138.3 | 58.9 | 21.5 | 77.4 | 77 | 71.9 | 82.7 | 35 | 15 | 8139.8 | 8883.3 | 8008.2 | 13857.5 | 17060.7 | 14691.1 | 1.702 | 1.921 | 1.835 | 0.738 | 0.766 | 0.76 | 5.52 | -5.5 | -6.23 | 0.562 | 0.525 | 0.602 | 3.28 | -3.01 | -2.61 | 0.567 | 0.58 | 0.547 | 3.42 | 2.31 | 3 | 0.606 | 0.532 | 0.51 | 2.42 | 2.65 | -2.93 | Poor_Winding_TD_Cap | 8008.2 | 13857.5 | 1.702 | 0.766 | 6.23 | 0.606 | 3.42 | 0.8798 | 0.9406 | 0.9018 | 0.8935 | 1 | 0.399 | 0.7442 | 0.8175 | 0.8175 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
1463 | 167.8 | 207 | 73.1 | 51.1 | 1.6 | 374.6 | 2968.3 | 55.9 | 23.8 | 82.9 | 82.6 | 72.8 | 85.3 | 36.6 | 14.2 | 6441.1 | 6945.4 | 7185.2 | 10758.5 | 11232.4 | 11922.3 | 1.67 | 1.617 | 1.659 | 0.584 | 0.612 | 0.544 | 3.76 | 3.35 | 3.12 | 0.516 | 0.5 | 0.542 | 2 | 2 | 2.32 | 0.534 | 0.512 | 0.5 | -2 | -2.05 | -2.32 | 0.523 | 0.5 | 0.549 | 2.23 | 2.86 | 2.23 | Fair_IR_PI | 6441.1 | 10758.5 | 1.617 | 0.612 | 3.76 | 0.549 | 2.86 | 0.911 | 0.8912 | 0.7753 | 0.9144 | 1 | 0.7185 | 0.8895 | 0.8786 | 0.8786 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1464 | 321.9 | 239.4 | 83.2 | 68.2 | 1 | 551.9 | 4035.6 | 54.5 | 24.6 | 77 | 78.2 | 73.7 | 83 | 35.8 | 17 | 1456.2 | 1999.9 | 824.2 | 1485.3 | 2251.1 | 840.7 | 1.02 | 1.126 | 1.02 | 0.758 | 0.703 | 0.71 | 5.54 | 4.83 | 4.87 | 0.615 | 0.566 | 1.626 | 3.58 | 3.98 | 3.26 | 0.591 | 0.551 | 0.597 | 2.59 | 3.87 | -3.35 | 0.565 | 0.548 | 0.542 | 3.47 | 3.46 | 3.54 | Critical_IR_PI | 824.2 | 840.7 | 1.02 | 0.758 | 5.54 | 1.626 | 3.98 | 0.8703 | 0.8768 | 0.8738 | 0.8378 | 0.925 | 0.4637 | 0.6349 | 0.7793 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_HV_B_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_HV_TanDelta_pct
1465 | 875 | 531.4 | 100 | 114.3 | 18.6 | 836.8 | 5518.5 | 46.8 | 32.7 | 90.4 | 90.5 | 82.4 | 96.7 | 39.1 | 25.2 | 5948.1 | 5164.1 | 5149 | 9271.1 | 8220.9 | 7609.4 | 1.559 | 1.592 | 1.478 | 0.764 | 0.787 | 0.684 | 6.15 | 6.06 | -4.93 | 0.692 | 0.626 | 0.662 | 5.21 | 4.6 | -3.88 | 0.693 | 0.632 | 0.655 | -5.25 | 4.09 | 3.77 | 0.611 | 0.699 | 0.716 | 5.53 | 4.99 | 3.66 | Poor_Mixed | 5149 | 7609.4 | 1.478 | 0.787 | 6.15 | 0.716 | 5.53 | 0.4362 | 0.7617 | 0.526 | 0.5725 | 1 | 0.4108 | 0.502 | 0.5895 | 0.5895 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1466 | 677.5 | 442.9 | 92 | 86.3 | 9.9 | 736.4 | 4345.5 | 51.8 | 30.3 | 84.7 | 84.1 | 77.9 | 91.5 | 38.8 | 20.1 | 7152 | 6403.9 | 7561.4 | 11989.8 | 9838.4 | 12764.3 | 1.676 | 1.536 | 1.688 | 0.619 | 0.612 | 0.609 | -4 | 3.59 | -4.09 | 0.621 | 0.581 | 0.68 | 3.11 | 4.25 | 3.72 | 0.609 | 0.549 | 0.597 | 3.85 | -2.68 | 2.73 | 0.612 | 0.582 | 0.613 | 3.16 | 4.08 | 4.74 | Fair_Mixed | 6403.9 | 9838.4 | 1.536 | 0.619 | 4.09 | 0.68 | 4.74 | 0.5842 | 0.792 | 0.668 | 0.7436 | 1 | 0.6439 | 0.6261 | 0.7079 | 0.7079 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1467 | 401.6 | 235.3 | 74.5 | 64.5 | 2.6 | 463.4 | 3418.9 | 59.9 | 20 | 79.1 | 82 | 74.2 | 85.6 | 35.4 | 11.6 | 8930.4 | 10000 | 9857.3 | 17477.4 | 19686.8 | 19390.5 | 1.957 | 1.969 | 1.967 | 0.807 | 0.776 | 0.791 | -6.52 | -6.86 | -6.91 | 0.5 | 0.559 | 0.523 | 2.07 | 2.6 | -3.26 | 0.566 | 0.568 | 0.542 | 3.69 | 3.25 | -2.47 | 0.596 | 0.509 | 0.542 | 2.45 | 2.52 | -3.61 | Poor_Winding_TD_Cap | 8930.4 | 17477.4 | 1.957 | 0.807 | 6.91 | 0.596 | 3.69 | 0.8116 | 1 | 0.8044 | 0.9744 | 1 | 0.3139 | 0.781 | 0.7966 | 0.7966 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1468 | 897.9 | 621.4 | 114.3 | 112.7 | 21.2 | 891.3 | 5433.7 | 46.3 | 34 | 89.8 | 89 | 81 | 98.5 | 39 | 26.1 | 5550.4 | 7217.1 | 4568.9 | 8340.7 | 11388.5 | 6716.9 | 1.503 | 1.578 | 1.47 | 0.748 | 0.704 | 0.74 | 5.6 | 5.61 | 5.72 | 0.736 | 0.659 | 0.664 | 3.57 | 4.13 | -6.19 | 0.666 | 0.7 | 0.642 | 4.27 | 4.76 | 5.58 | 0.627 | 0.677 | 0.686 | 3.48 | 5.84 | 5.58 | Poor_Mixed | 4568.9 | 6716.9 | 1.47 | 0.748 | 5.72 | 0.736 | 6.19 | 0.3945 | 0.7461 | 0.5406 | 0.5407 | 1 | 0.4256 | 0.4819 | 0.5756 | 0.5756 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1469 | 1036.1 | 529.3 | 107.2 | 128.5 | 20.6 | 884.4 | 5137.2 | 46.2 | 34.5 | 92.3 | 89.2 | 81.1 | 97.5 | 38.8 | 25.4 | 6053.4 | 7276 | 5199.9 | 9161.3 | 11452.8 | 8037.3 | 1.513 | 1.574 | 1.546 | 0.705 | 0.771 | 0.76 | 5.14 | 5.85 | 5.75 | 0.676 | 0.593 | 0.644 | -3.59 | -4.49 | -5.11 | 0.68 | 0.645 | 0.683 | 5.22 | 5.37 | 5.16 | 0.657 | 0.637 | 0.664 | -3.93 | 4.55 | 4.11 | Poor_Mixed | 5199.9 | 8037.3 | 1.513 | 0.771 | 5.85 | 0.683 | 5.37 | 0.3913 | 0.7403 | 0.5285 | 0.5655 | 1 | 0.4169 | 0.5142 | 0.5787 | 0.5787 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1470 | 172.9 | 120 | 65 | 63.3 | 2.2 | 396.7 | 3106.6 | 56.5 | 23.1 | 75.7 | 77.1 | 70 | 80 | 35.3 | 12.8 | 9590.3 | 9175.1 | 9447.4 | 19180.6 | 16798.2 | 18447.8 | 2 | 1.831 | 1.953 | 0.52 | 0.5 | 0.525 | 2 | 2.49 | 2.41 | 0.56 | 0.559 | 0.5 | 2.65 | -2.28 | -2 | 0.529 | 0.5 | 0.536 | -2.33 | 2.07 | 2.56 | 0.5 | 0.5 | 0.52 | 2.49 | 2.63 | -2.67 | Good_Mixed | 9175.1 | 16798.2 | 1.831 | 0.525 | 2.49 | 0.56 | 2.67 | 0.879 | 0.9047 | 0.9555 | 0.9484 | 1 | 0.9177 | 0.8774 | 0.9177 | 0.9177 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1471 | 849.8 | 551 | 99.9 | 112.5 | 18.1 | 816.2 | 5350.6 | 47.5 | 33.6 | 91.4 | 92.5 | 82.6 | 97.7 | 41 | 27.1 | 6173.2 | 6386 | 6504.4 | 9725.9 | 9984.7 | 10103.3 | 1.576 | 1.564 | 1.553 | 0.727 | 0.755 | 0.698 | -5.48 | 6.13 | 5.08 | 0.653 | 0.653 | 0.691 | 4.43 | 4.46 | 3.85 | 0.673 | 0.623 | 0.643 | 5.11 | 4.97 | 5.63 | 0.743 | 0.601 | 0.712 | -4.01 | 4.43 | -4.61 | Poor_Mixed | 6173.2 | 9725.9 | 1.553 | 0.755 | 6.13 | 0.743 | 5.63 | 0.4452 | 0.7509 | 0.488 | 0.5047 | 1 | 0.4339 | 0.4995 | 0.5861 | 0.5861 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1472 | 1455.7 | 861.5 | 137.6 | 176.2 | 34.3 | 1223.4 | 8217.8 | 37.4 | 44.6 | 106.7 | 106.2 | 94.3 | 115.1 | 43.3 | 32.5 | 1571.6 | 1679.3 | 1498.4 | 1806.6 | 1813.3 | 1785.1 | 1.15 | 1.08 | 1.191 | 0.957 | 0.957 | 0.945 | 9.28 | -9.78 | 8.88 | 0.876 | 0.785 | 0.798 | 6.44 | 6.91 | -7.8 | 0.797 | 0.799 | 0.779 | -8.21 | 6.9 | 8.52 | 0.92 | 0.795 | 0.749 | 6.7 | 7.54 | -8.9 | Very Poor_Mixed | 1498.4 | 1785.1 | 1.08 | 0.957 | 9.78 | 0.92 | 8.9 | 0.1156 | 0.6338 | 0.1449 | 0.302 | 1 | 0.065 | 0.2392 | 0.3467 | 0.3467 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1473 | 1588.5 | 898 | 139.9 | 169.3 | 34.3 | 1222.6 | 8185.3 | 34.8 | 44.4 | 107.3 | 106.7 | 92.9 | 115.7 | 44.4 | 31.9 | 1817.7 | 1520.7 | 2192.7 | 2082 | 1747.1 | 2657.1 | 1.145 | 1.149 | 1.212 | 0.842 | 0.9 | 0.892 | 8.01 | 8.68 | 8.03 | 0.82 | 0.738 | 0.819 | -5.06 | 6.69 | -5.55 | 0.786 | 0.703 | 0.795 | 7.61 | 6.02 | 6.53 | 0.855 | 0.78 | 0.822 | 7.66 | -7.55 | 8.56 | Very Poor_Mixed | 1520.7 | 1747.1 | 1.145 | 0.9 | 8.68 | 0.855 | 8.56 | 0.1066 | 0.6357 | 0.1358 | 0.3252 | 1 | 0.1715 | 0.2833 | 0.3678 | 0.3678 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1474 | 1556.6 | 917.1 | 143.1 | 187.8 | 32.3 | 1293.6 | 8193.4 | 30.6 | 48.9 | 104.2 | 106.5 | 94.8 | 113.7 | 43.6 | 32.6 | 690 | 1399.5 | 1901 | 1200 | 1495.9 | 2178.4 | 1.739 | 1.069 | 1.146 | 0.938 | 0.976 | 0.974 | 8.53 | -8.85 | 9.72 | 0.739 | 0.822 | 0.901 | -8.54 | 6.96 | 6.9 | 0.909 | 0.813 | 0.924 | 6.66 | 9.06 | 7.32 | 0.898 | 0.884 | 0.884 | 6.86 | 7.7 | 6.89 | Very Poor_Mixed | 690 | 1200 | 1.069 | 0.976 | 9.72 | 0.924 | 9.06 | 0.0897 | 0.5933 | 0.1592 | 0.2982 | 1 | 0.0727 | 0.1945 | 0.3296 | 0.3296 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1475 | 926.8 | 546.6 | 108.5 | 126.7 | 21.1 | 861.7 | 5774.4 | 60 | 23.4 | 78.6 | 82.3 | 72.9 | 83.7 | 36.3 | 10.1 | 9175.2 | 9124.2 | 9841.3 | 17730 | 17328.6 | 19562.3 | 1.932 | 1.899 | 1.988 | 0.515 | 0.552 | 0.572 | -2.35 | 2.64 | -3.16 | 0.511 | 0.5 | 0.525 | 2 | 3.2 | 2.4 | 0.5 | 0.544 | 0.552 | -2 | 2.6 | -2.43 | 0.511 | 0.536 | 0.522 | -2.01 | 2 | -2.44 | Poor_DGA | 9124.2 | 17328.6 | 1.899 | 0.572 | 3.16 | 0.552 | 3.2 | 0.3918 | 0.8988 | 0.8228 | 0.9992 | 1 | 0.8176 | 0.8697 | 0.7691 | 0.7691 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1476 | 100 | 138 | 71.8 | 63.3 | 3.1 | 350 | 2813.7 | 59.4 | 20 | 78.3 | 76.9 | 71.7 | 80 | 35 | 12.9 | 10000 | 9791.1 | 10000 | 19520.3 | 19514.3 | 20000 | 1.952 | 1.993 | 2 | 0.524 | 0.5 | 0.556 | 2.98 | -2.02 | 2.61 | 0.5 | 0.526 | 0.5 | -2 | 2.53 | 2.42 | 0.506 | 0.5 | 0.515 | 2.84 | 2.31 | 2 | 0.5 | 0.518 | 0.5 | 2.46 | 2 | 2.77 | Good_Mixed | 9791.1 | 19514.3 | 1.952 | 0.556 | 2.98 | 0.526 | 2.84 | 0.8757 | 1 | 0.9092 | 0.9461 | 1 | 0.8788 | 0.9306 | 0.9277 | 0.9277 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1477 | 1538.2 | 885.5 | 136.7 | 194.4 | 32.9 | 1300.8 | 7998.2 | 33.3 | 43.6 | 102.3 | 104 | 92.5 | 113.6 | 44.4 | 32.4 | 2188.6 | 1364.7 | 977.8 | 2412.9 | 1432.9 | 1200 | 1.102 | 1.05 | 1.227 | 0.931 | 0.956 | 0.904 | 7.82 | -8.7 | 8.2 | 0.905 | 0.734 | 0.838 | 5.34 | 8.37 | 7.64 | 0.827 | 0.81 | 0.76 | 8.25 | 6.86 | 7.55 | 0.842 | 0.9 | 0.773 | -8.97 | 5.86 | 5.49 | Very Poor_Mixed | 977.8 | 1200 | 1.05 | 0.956 | 8.7 | 0.905 | 8.97 | 0.0932 | 0.6435 | 0.1914 | 0.3059 | 1 | 0.1347 | 0.2437 | 0.3577 | 0.3577 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1478 | 254.4 | 206.2 | 72.7 | 58.5 | 5.1 | 442.7 | 3029.1 | 57.8 | 21.9 | 75.6 | 75 | 70 | 80.4 | 35.5 | 13.8 | 9491.2 | 10000 | 10000 | 18268.3 | 20000 | 19639.9 | 1.925 | 2 | 1.964 | 0.529 | 0.544 | 0.516 | 2.68 | 3 | 2 | 0.5 | 0.529 | 0.5 | 2 | -2.13 | 2 | 0.51 | 0.5 | 0.529 | -2.38 | -2.04 | -2.26 | 0.526 | 0.514 | 0.5 | 2 | 2.34 | 2 | Good_Mixed | 9491.2 | 18268.3 | 1.925 | 0.544 | 3 | 0.529 | 2.38 | 0.8026 | 0.9307 | 0.9845 | 0.9244 | 1 | 0.858 | 0.9228 | 0.9032 | 0.9032 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1479 | 1118 | 636 | 123.6 | 147.2 | 22.1 | 959.7 | 6406.4 | 55.6 | 25.6 | 79.2 | 78.5 | 72.5 | 84.9 | 35 | 15.9 | 9690.4 | 9235 | 8597.9 | 19380.9 | 17699.1 | 16433.8 | 2 | 1.917 | 1.911 | 0.523 | 0.659 | 0.558 | 3.08 | 4.03 | 2.35 | 0.503 | 0.5 | 0.5 | -2.18 | 2.37 | 2 | 0.513 | 0.533 | 0.5 | -2 | 2.25 | -2.29 | 0.5 | 0.51 | 0.55 | 2.93 | 2.2 | -2.69 | Poor_DGA | 8597.9 | 16433.8 | 1.911 | 0.659 | 4.03 | 0.55 | 2.93 | 0.3126 | 0.86 | 0.8527 | 0.869 | 1 | 0.7457 | 0.9152 | 0.7392 | 0.7392 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1480 | 423.8 | 300.2 | 85.1 | 152.7 | 2.5 | 635.1 | 4367.9 | 54.4 | 25.4 | 108.2 | 106.9 | 93.2 | 116.1 | 42.9 | 16 | 8460.1 | 8578.5 | 7322.8 | 14786.4 | 15394.4 | 12888.4 | 1.748 | 1.795 | 1.76 | 0.616 | 0.582 | 0.587 | -2.76 | 3.62 | 2.87 | 0.592 | 0.6 | 0.563 | 2.61 | 3.01 | 3.64 | 0.588 | 0.574 | 1.846 | -3.33 | -3.01 | 3.13 | 0.547 | 0.548 | 0.535 | 2.9 | 3.32 | -2.33 | Critical_Thermal | 7322.8 | 12888.4 | 1.748 | 0.616 | 3.62 | 1.846 | 3.64 | 0.6716 | 0.8633 | 0.1369 | 0.8663 | 1 | 0.7186 | 0.6593 | 0.7078 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H4
1481 | 257.6 | 191.3 | 75.2 | 64.3 | 2.7 | 493.6 | 2839 | 57.5 | 21.7 | 77.1 | 76.1 | 70 | 81.1 | 36.5 | 11.9 | 8226.8 | 8270.2 | 8331.4 | 14762.7 | 15390 | 15179 | 1.794 | 1.861 | 1.822 | 0.745 | 0.711 | 0.804 | -7.08 | 4.7 | 6.87 | 0.5 | 0.503 | 0.525 | 3.23 | 2 | -2.37 | 0.5 | 0.5 | 0.5 | 2.88 | 2.14 | -2 | 0.501 | 0.528 | 0.5 | 2.86 | 2 | -2.71 | Poor_Winding_TD_Cap | 8226.8 | 14762.7 | 1.794 | 0.804 | 7.08 | 0.528 | 3.23 | 0.8267 | 0.9355 | 0.9392 | 0.9682 | 1 | 0.3765 | 0.9342 | 0.8421 | 0.8421 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1482 | 1601.7 | 878.9 | 142.1 | 181.9 | 26.7 | 1349.4 | 8544 | 33.6 | 44.5 | 104.6 | 105.3 | 94.3 | 114.2 | 43.7 | 29.8 | 2340.2 | 1125.7 | 2610.8 | 2711.8 | 1214.8 | 3307.6 | 1.159 | 1.079 | 1.267 | 0.936 | 0.958 | 0.934 | 9.07 | 9.07 | 8.92 | 0.69 | 0.823 | 0.827 | 8.26 | 7.49 | 8.83 | 0.892 | 0.842 | 0.771 | 7.56 | -6.61 | -6.56 | 0.902 | 0.99 | 0.828 | 6.66 | 5.69 | 6.13 | Very Poor_Mixed | 1125.7 | 1214.8 | 1.079 | 0.958 | 9.07 | 0.99 | 8.83 | 0.1117 | 0.6347 | 0.1632 | 0.4051 | 1 | 0.0866 | 0.229 | 0.354 | 0.354 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1483 | 760 | 487.3 | 104.7 | 113.9 | 14.3 | 772.2 | 5380.7 | 47.7 | 33.9 | 91.1 | 95.5 | 81.8 | 99.4 | 40 | 26.9 | 4655.9 | 5127.5 | 5354.2 | 6972.2 | 7495 | 7890.2 | 1.497 | 1.462 | 1.474 | 0.746 | 0.797 | 0.765 | -5.58 | 6.37 | 5.71 | 0.742 | 0.677 | 0.751 | 5.49 | 5.68 | 5.69 | 0.681 | 0.705 | 0.654 | 6.28 | 5.56 | 5.52 | 0.74 | 0.699 | 0.708 | 4.67 | 4.58 | 4.84 | Poor_Mixed | 4655.9 | 6972.2 | 1.462 | 0.797 | 6.37 | 0.751 | 6.28 | 0.4851 | 0.7473 | 0.4744 | 0.512 | 1 | 0.3794 | 0.4212 | 0.5729 | 0.5729 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1484 | 1575.6 | 873.4 | 138.1 | 179.6 | 31.3 | 1261 | 8440.7 | 36.8 | 46.9 | 104.9 | 103.8 | 92.9 | 113.7 | 44.1 | 32.5 | 1464.6 | 1027.7 | 1971.1 | 1608 | 1200 | 2349.8 | 1.098 | 1.168 | 1.192 | 0.878 | 0.928 | 0.915 | 9.2 | -8.26 | 8.92 | 0.77 | 0.908 | 0.834 | -8.87 | -5.49 | 5.85 | 0.864 | 0.928 | 0.726 | -6.32 | -7.47 | -6.54 | 0.916 | 0.871 | 0.854 | 6.05 | 6.27 | 6.66 | Very Poor_Mixed | 1027.7 | 1200 | 1.098 | 0.928 | 9.2 | 0.928 | 8.87 | 0.1086 | 0.6119 | 0.1773 | 0.302 | 1 | 0.1227 | 0.2326 | 0.3524 | 0.3524 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1485 | 1577.5 | 938.1 | 140.7 | 178.3 | 33.1 | 1293.5 | 8262.6 | 31.4 | 47.4 | 105.5 | 105.7 | 94.7 | 116.3 | 44.5 | 34.5 | 1193.8 | 696.1 | 845.2 | 1253.4 | 1200 | 1200 | 1.05 | 1.724 | 1.42 | 0.978 | 0.984 | 0.976 | 8.91 | 9.84 | 8.85 | 0.766 | 0.883 | 0.902 | 9.69 | 6.92 | 6.83 | 0.916 | 0.769 | 0.862 | -9.22 | 8.39 | 7.23 | 0.922 | 0.739 | 0.875 | -6.53 | 9.7 | 6.74 | Very Poor_Mixed | 696.1 | 1200 | 1.05 | 0.984 | 9.84 | 0.922 | 9.7 | 0.0912 | 0.6072 | 0.1374 | 0.2237 | 1 | 0.0533 | 0.1942 | 0.323 | 0.323 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1486 | 370 | 198.8 | 83.5 | 153.4 | 1.2 | 482.8 | 4132.5 | 59.1 | 21.2 | 109.2 | 104.4 | 94.5 | 116.4 | 45 | 14.3 | 8228.2 | 134.6 | 7843.3 | 14241.3 | 225 | 13633.3 | 1.731 | 1.672 | 1.738 | 0.544 | 0.571 | 0.578 | 2.73 | 3.41 | -3.51 | 0.553 | 0.599 | 0.553 | 3.75 | 3.58 | 3.1 | 0.599 | 0.578 | 0.555 | -3.92 | 5.18 | -2.55 | 0.575 | 0.586 | 0.596 | -4.53 | 4.15 | 3.17 | Critical_Thermal | 134.6 | 225 | 1.672 | 0.578 | 3.51 | 0.599 | 5.18 | 0.7604 | 0.9486 | 0.1214 | 0.9118 | 0.85 | 0.7514 | 0.6631 | 0.7222 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H4
1487 | 1652.5 | 910.1 | 142.5 | 181.9 | 34.3 | 1234.2 | 8538.1 | 35 | 45.8 | 106.7 | 108.9 | 94.4 | 114.6 | 44.3 | 31.6 | 1583 | 1835.3 | 1893 | 1827.5 | 1964.9 | 2155 | 1.154 | 1.071 | 1.138 | 0.983 | 0.93 | 0.905 | 9.5 | 9.64 | 7.86 | 0.915 | 0.928 | 0.799 | 9.44 | -8.93 | -7.38 | 0.827 | 0.99 | 0.909 | 8.93 | -8.14 | 5.96 | 0.875 | 0.838 | 0.906 | 7.48 | 6.98 | 8.94 | Very Poor_Mixed | 1583 | 1827.5 | 1.071 | 0.983 | 9.64 | 0.99 | 9.44 | 0.0821 | 0.6222 | 0.1249 | 0.3368 | 1 | 0.0905 | 0.1549 | 0.3251 | 0.3251 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1488 | 908.8 | 526.6 | 99.4 | 120.5 | 18 | 761.6 | 5243.1 | 46.3 | 33.1 | 90.3 | 90 | 80.7 | 98.3 | 39.5 | 25.7 | 6879 | 5839.5 | 6231.3 | 11533.7 | 9038.2 | 9830.6 | 1.677 | 1.548 | 1.578 | 0.689 | 0.751 | 0.744 | 5.45 | -5.68 | 5.77 | 0.58 | 0.664 | 0.627 | 3.49 | 4.54 | 4.26 | 0.678 | 0.691 | 0.686 | 4.44 | 3.57 | 4.38 | 0.624 | 0.613 | 0.71 | 4.51 | 5.42 | 4.59 | Poor_Mixed | 5839.5 | 9038.2 | 1.548 | 0.751 | 5.77 | 0.71 | 5.42 | 0.4445 | 0.7568 | 0.5304 | 0.5549 | 1 | 0.4288 | 0.5268 | 0.5976 | 0.5976 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1489 | 755.5 | 516 | 98 | 115.5 | 18 | 762.8 | 5305.4 | 56.3 | 24.7 | 78.1 | 79.4 | 73.9 | 83.8 | 35.8 | 12.6 | 8418.9 | 7085.9 | 7970.4 | 15975.1 | 13000.3 | 13659.9 | 1.898 | 1.835 | 1.714 | 0.558 | 0.531 | 0.544 | 3 | -2.25 | 3.39 | 0.5 | 0.549 | 0.606 | 2.82 | 3.67 | 2.5 | 0.559 | 0.511 | 0.548 | 2.04 | -2.45 | 2 | 0.5 | 0.5 | 0.547 | 2.76 | -2 | 2.27 | Poor_DGA | 7085.9 | 13000.3 | 1.714 | 0.558 | 3.39 | 0.606 | 3.67 | 0.4629 | 0.8751 | 0.8456 | 0.953 | 1 | 0.8062 | 0.8394 | 0.7769 | 0.7769 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1490 | 1393.1 | 721.3 | 132.9 | 180.8 | 28.5 | 1212.9 | 7683.6 | 31.9 | 45 | 105.8 | 103.7 | 93.1 | 114.9 | 44.1 | 30.4 | 1410.1 | 2417.5 | 1237.1 | 1505.6 | 2919.7 | 1298.9 | 1.068 | 1.208 | 1.05 | 0.97 | 0.932 | 0.967 | 9.68 | 9.69 | -9.34 | 0.798 | 0.755 | 0.743 | 7.58 | 5.06 | 7.3 | 0.927 | 0.756 | 0.825 | -8.19 | 7.62 | 8.12 | 0.895 | 0.72 | 0.828 | 5.63 | 6.57 | 7.23 | Very Poor_Mixed | 1237.1 | 1298.9 | 1.05 | 0.97 | 9.69 | 0.927 | 8.19 | 0.1696 | 0.6299 | 0.1658 | 0.3825 | 1 | 0.05 | 0.2631 | 0.368 | 0.368 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1491 | 253.8 | 218.5 | 78.4 | 57.2 | 2.4 | 417.4 | 3221.3 | 55 | 23.4 | 77.9 | 78.1 | 73.7 | 85 | 36 | 13.6 | 8720 | 6755 | 8825 | 16220.8 | 10969.5 | 16314.8 | 1.86 | 1.624 | 1.849 | 0.725 | 0.753 | 0.787 | -5.66 | 5.94 | 6.85 | 0.598 | 0.522 | 0.529 | 3.16 | 3 | 3.51 | 0.602 | 0.571 | 0.547 | 3.88 | 3.17 | 2.96 | 0.619 | 0.511 | 0.574 | 3.83 | 3.37 | -2.26 | Poor_Winding_TD_Cap | 6755 | 10969.5 | 1.624 | 0.787 | 6.85 | 0.619 | 3.88 | 0.8507 | 0.8988 | 0.8544 | 0.9294 | 1 | 0.3772 | 0.7193 | 0.7947 | 0.7947 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1492 | 179.8 | 217.1 | 65.6 | 66.3 | 4.7 | 403 | 2584.2 | 59.2 | 21.3 | 75 | 75.9 | 70.1 | 80 | 35.7 | 10.7 | 9929.8 | 9620.9 | 9524.8 | 19859.5 | 18949.5 | 18812.2 | 2 | 1.97 | 1.975 | 0.51 | 0.513 | 0.518 | 2.14 | 3 | -2 | 0.5 | 0.55 | 0.582 | 2.15 | 2.55 | 2.07 | 0.541 | 0.535 | 0.542 | 2 | 2.57 | 2.66 | 0.529 | 0.546 | 0.539 | 2.65 | 2 | 2.05 | Good_Mixed | 9524.8 | 18812.2 | 1.97 | 0.518 | 3 | 0.582 | 2.66 | 0.8158 | 0.9458 | 0.9793 | 0.9909 | 1 | 0.9072 | 0.8158 | 0.8988 | 0.8988 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1493 | 1594.3 | 858.3 | 135.3 | 191.7 | 27.9 | 1244.7 | 8010.8 | 32.3 | 46.8 | 100 | 103.6 | 90.1 | 114.8 | 44 | 30.5 | 1622.5 | 2084.9 | 1942.5 | 1927.3 | 2405.4 | 2229.3 | 1.188 | 1.154 | 1.148 | 0.95 | 0.895 | 0.88 | 8.89 | -7.87 | 8.43 | 0.812 | 0.776 | 0.857 | -8.64 | -8.05 | 6.13 | 0.929 | 0.897 | 0.849 | 7.36 | 7.84 | 6.47 | 0.773 | 0.786 | 0.825 | 8.51 | -5.85 | 6.08 | Very Poor_Mixed | 1622.5 | 1927.3 | 1.148 | 0.95 | 8.89 | 0.929 | 8.64 | 0.1244 | 0.6128 | 0.2175 | 0.3787 | 1 | 0.1421 | 0.2288 | 0.3664 | 0.3664 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1494 | 760.9 | 516.6 | 97 | 106.5 | 13.7 | 835 | 5380.7 | 56.9 | 23.4 | 78.5 | 80.1 | 73.7 | 82.2 | 35.7 | 11 | 9354.2 | 8806.2 | 8790.6 | 17867.3 | 16886 | 16765.5 | 1.91 | 1.918 | 1.907 | 0.5 | 0.515 | 0.535 | 2 | 2.17 | 2.88 | 0.528 | 0.527 | 0.58 | 3.17 | 2.97 | 2.94 | 0.564 | 0.563 | 0.558 | 2.58 | 2.44 | 2.78 | 0.621 | 0.565 | 0.526 | 3.11 | 3.5 | 4.01 | Fair_DGA | 8790.6 | 16765.5 | 1.907 | 0.535 | 2.88 | 0.621 | 4.01 | 0.4911 | 0.8988 | 0.8456 | 0.9858 | 1 | 0.9124 | 0.7315 | 0.7839 | 0.7839 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1495 | 1625.4 | 872.2 | 142.4 | 182.8 | 34.3 | 1243.2 | 8133.7 | 30.8 | 47.5 | 104.4 | 103.6 | 90.7 | 110.8 | 43.5 | 31.1 | 2785.2 | 1453.3 | 1743 | 3209.6 | 1583 | 1981.1 | 1.152 | 1.089 | 1.137 | 0.942 | 0.957 | 0.977 | 9.17 | 9.76 | 9.32 | 0.764 | 0.814 | 0.793 | 8.91 | 6.4 | -5.52 | 0.874 | 0.835 | 0.884 | 6.83 | -7.19 | 6.2 | 0.99 | 0.887 | 0.871 | 7.69 | 7.11 | 6.48 | Very Poor_Mixed | 1453.3 | 1583 | 1.089 | 0.977 | 9.76 | 0.99 | 8.91 | 0.0919 | 0.6062 | 0.2126 | 0.3559 | 1 | 0.0561 | 0.2177 | 0.3418 | 0.3418 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1496 | 1646 | 840.1 | 141.6 | 184.4 | 34.3 | 1268.7 | 7905.8 | 35.5 | 44.4 | 103.5 | 109.3 | 92.2 | 114.1 | 43 | 31.7 | 1096.8 | 1383.7 | 2314.8 | 1210.7 | 1490.6 | 2757.2 | 1.104 | 1.077 | 1.191 | 0.931 | 0.963 | 0.964 | 8.62 | 9.18 | 8.73 | 0.894 | 0.767 | 0.785 | -7.07 | -7.06 | 6.3 | 0.894 | 0.783 | 0.813 | 5.7 | -6.15 | 6.77 | 0.872 | 0.729 | 0.712 | 7.53 | 5.7 | 7.66 | Very Poor_Mixed | 1096.8 | 1210.7 | 1.077 | 0.964 | 9.18 | 0.894 | 7.66 | 0.0934 | 0.6357 | 0.1647 | 0.3329 | 1 | 0.0888 | 0.2748 | 0.3546 | 0.3546 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1497 | 908.2 | 522.8 | 107.8 | 123.7 | 18.2 | 838.5 | 5544.2 | 46.1 | 34.9 | 90.4 | 90.2 | 80.9 | 97.1 | 39.1 | 25.9 | 7870.5 | 5756 | 5759.7 | 12937.6 | 8732.8 | 8783.8 | 1.644 | 1.517 | 1.525 | 0.672 | 0.699 | 0.737 | 5.45 | 5.66 | 5.95 | 0.632 | 0.728 | 0.647 | 3.49 | -5.01 | 3.52 | 0.623 | 0.69 | 0.613 | 4.03 | 3.71 | -4.56 | 0.587 | 0.637 | 0.59 | 4.25 | 3.77 | -4.51 | Poor_Mixed | 5756 | 8732.8 | 1.517 | 0.737 | 5.95 | 0.728 | 5.01 | 0.4218 | 0.7356 | 0.5356 | 0.5478 | 1 | 0.4488 | 0.5561 | 0.5976 | 0.5976 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1498 | 1622.1 | 927.9 | 145.6 | 189.4 | 34.3 | 1329.8 | 8610.8 | 34.8 | 46.5 | 104.5 | 103.1 | 93.8 | 112.8 | 43.5 | 34.6 | 2209.9 | 784.9 | 1530.2 | 2563.5 | 1200 | 1708.1 | 1.16 | 1.529 | 1.116 | 0.98 | 0.959 | 0.961 | 9.65 | 9.82 | 9.28 | 0.842 | 0.935 | 0.721 | -7.71 | -5.76 | 7.26 | 0.897 | 0.781 | 0.791 | 7.9 | 6.07 | 6.96 | 0.824 | 0.905 | 0.751 | 8.23 | -5.72 | 8.43 | Very Poor_Mixed | 784.9 | 1200 | 1.116 | 0.98 | 9.82 | 0.935 | 8.43 | 0.0623 | 0.6156 | 0.1873 | 0.2197 | 1 | 0.0424 | 0.2394 | 0.3282 | 0.3282 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1499 | 1531.8 | 910.4 | 139.8 | 178.2 | 30.3 | 1221.7 | 7874.6 | 34.5 | 46.6 | 104.9 | 101.5 | 90.5 | 111.7 | 43.2 | 32.4 | 1379.5 | 2322.5 | 1927.1 | 1600.1 | 2604.8 | 2184 | 1.16 | 1.122 | 1.133 | 0.941 | 0.914 | 0.94 | 8.93 | 8.56 | 8.39 | 0.882 | 0.864 | 0.785 | -6.62 | 6.09 | -7.6 | 0.846 | 0.805 | 0.717 | 6.46 | 8.77 | 7.99 | 0.844 | 0.784 | 0.744 | 6.3 | 8.53 | 6.6 | Very Poor_Mixed | 1379.5 | 1600.1 | 1.122 | 0.941 | 8.93 | 0.882 | 8.77 | 0.1238 | 0.6147 | 0.2205 | 0.3059 | 1 | 0.114 | 0.2533 | 0.3636 | 0.3636 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1500 | 1583.9 | 895.1 | 139 | 190.8 | 33.9 | 1310 | 8324.8 | 30.6 | 48.4 | 104.7 | 108.6 | 94 | 115.5 | 45.1 | 31.9 | 800.2 | 704.3 | 927.9 | 1200 | 1200 | 1200 | 1.5 | 1.704 | 1.293 | 0.948 | 0.962 | 0.97 | 9.03 | 9.48 | -9.08 | 0.853 | 0.905 | 0.905 | 5.86 | 5.21 | 8.05 | 0.723 | 0.794 | 0.931 | 7.17 | 7.98 | -7.81 | 0.922 | 0.713 | 0.842 | 6.5 | 6.97 | -7.11 | Very Poor_Mixed | 704.3 | 1200 | 1.293 | 0.97 | 9.48 | 0.931 | 8.05 | 0.0804 | 0.5979 | 0.1295 | 0.3252 | 1 | 0.0661 | 0.2308 | 0.3319 | 0.3319 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1501 | 1766 | 978.2 | 145.8 | 192 | 33.7 | 1337.8 | 9100.7 | 16 | 27.1 | 81.9 | 86.3 | 76.1 | 88.6 | 37 | 11.7 | 6547.7 | 7136.2 | 7010.2 | 10870 | 12211.3 | 11879.6 | 1.66 | 1.711 | 1.695 | 0.661 | 0.616 | 0.672 | 4.43 | 3.65 | -4.27 | 0.507 | 0.518 | 0.5 | 2.48 | -2.09 | 2.35 | 0.55 | 0.519 | 0.5 | 2.4 | 2.24 | 2.31 | 0.528 | 0.5 | 0.5 | -2.25 | 2.12 | 2.57 | Critical_DGA | 6547.7 | 10870 | 1.66 | 0.672 | 4.43 | 0.55 | 2.57 | 0.0395 | 0.2534 | 0.7111 | 0.9724 | 1 | 0.5914 | 0.9074 | 0.5661 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
1502 | 1758.1 | 864 | 141.3 | 180 | 31.6 | 1305.9 | 8327.1 | 32.6 | 46 | 103.5 | 106.3 | 93 | 117 | 44.7 | 33.1 | 1423.6 | 1372.3 | 927 | 1494.8 | 1522.9 | 1200 | 1.05 | 1.11 | 1.294 | 0.969 | 0.932 | 0.99 | 9.17 | 9.04 | 9.28 | 0.874 | 0.835 | 0.835 | 9.37 | 7.25 | 5.77 | 0.85 | 0.892 | 0.925 | 6.09 | 6.22 | -9.07 | 0.881 | 0.969 | 0.845 | 7.07 | 8.46 | 8.6 | Very Poor_Mixed | 927 | 1200 | 1.05 | 0.99 | 9.28 | 0.969 | 9.37 | 0.089 | 0.6203 | 0.1498 | 0.2787 | 1 | 0.0655 | 0.1776 | 0.3267 | 0.3267 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1503 | 869.4 | 524.7 | 111.5 | 116.2 | 20.3 | 823.5 | 4657.5 | 46.2 | 32.5 | 87.1 | 90.3 | 77.7 | 93.8 | 39.5 | 23.6 | 5971 | 5722.8 | 5537.2 | 9356.9 | 8437.9 | 8133.5 | 1.567 | 1.474 | 1.469 | 0.757 | 0.686 | 0.704 | 5.71 | 5.43 | -4.97 | 0.678 | 0.733 | 0.707 | 4.52 | 3.91 | 5.75 | 0.664 | 0.582 | 0.636 | 4.64 | 5 | 4.51 | 0.757 | 0.649 | 0.74 | 4.52 | 3.7 | 4.94 | Poor_Mixed | 5537.2 | 8133.5 | 1.469 | 0.757 | 5.71 | 0.757 | 5.75 | 0.4273 | 0.7641 | 0.5929 | 0.628 | 1 | 0.4547 | 0.4802 | 0.5993 | 0.5993 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1504 | 1552.1 | 838.2 | 136.8 | 165.7 | 33.5 | 1275.9 | 8104 | 32.7 | 46.6 | 105.1 | 106.4 | 91.2 | 111.8 | 43.7 | 29.7 | 2094.3 | 2622.2 | 1992.5 | 2358.5 | 3236.6 | 2271 | 1.126 | 1.234 | 1.14 | 0.84 | 0.962 | 0.88 | 7.88 | -8.81 | 9.15 | 0.708 | 0.786 | 0.869 | -5.01 | 6.53 | 7.01 | 0.792 | 0.725 | 0.82 | 5.8 | -5.44 | 5.43 | 0.782 | 0.873 | 0.887 | 5.84 | 5.69 | 6.78 | Very Poor_Mixed | 1992.5 | 2271 | 1.126 | 0.962 | 9.15 | 0.887 | 7.01 | 0.1199 | 0.6147 | 0.1838 | 0.4089 | 1 | 0.1418 | 0.2995 | 0.3763 | 0.3763 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1505 | 1618.2 | 959.2 | 140.8 | 192.9 | 34.3 | 1257.5 | 8117 | 33.9 | 47.1 | 108.2 | 108.2 | 92.9 | 117.4 | 45.4 | 33.6 | 1154.2 | 2060.8 | 806 | 1321.7 | 2281.3 | 1200 | 1.145 | 1.107 | 1.489 | 0.945 | 0.99 | 0.984 | -8.92 | 9.34 | -9.26 | 0.785 | 0.744 | 0.809 | -7.03 | 8.01 | 6.37 | 0.74 | 0.882 | 0.757 | 8.06 | 6.11 | -4.89 | 0.83 | 0.825 | 0.844 | 7.72 | 7.98 | 9.24 | Very Poor_Mixed | 806 | 1200 | 1.107 | 0.99 | 9.34 | 0.882 | 9.24 | 0.0746 | 0.61 | 0.1068 | 0.2591 | 1 | 0.0588 | 0.2575 | 0.3301 | 0.3301 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1506 | 1258.9 | 732.6 | 131.5 | 159.3 | 36.4 | 1071.6 | 7610.2 | 57.8 | 22.9 | 76 | 76.9 | 71.9 | 82 | 36 | 16.1 | 9126 | 7427.2 | 7531.3 | 17750.7 | 12482 | 13478.4 | 1.945 | 1.681 | 1.79 | 0.66 | 0.608 | 0.618 | -4.55 | 3.86 | 4.41 | 0.631 | 0.55 | 0.574 | -3.86 | 4.02 | 3.23 | 0.549 | 0.605 | 0.623 | 2.49 | 3.7 | 3.59 | 0.574 | 0.591 | 0.627 | 3.48 | 3.76 | 3.93 | Critical_DGA | 7427.2 | 12482 | 1.681 | 0.66 | 4.55 | 0.631 | 4.02 | 0.1852 | 0.9088 | 0.9186 | 0.8635 | 1 | 0.6044 | 0.6482 | 0.6517 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1507 | 1350.3 | 815 | 129.3 | 165.6 | 33.8 | 1084.3 | 7618.8 | 32.6 | 44.3 | 105 | 108 | 92.7 | 114.5 | 43.4 | 29.6 | 1782.8 | 2142.2 | 1204.7 | 2044 | 2504.5 | 1334.6 | 1.147 | 1.169 | 1.108 | 0.99 | 0.99 | 0.884 | 9.44 | 9.06 | 8.86 | 0.935 | 0.919 | 0.759 | 5.28 | -6.85 | -6.81 | 0.957 | 0.754 | 0.781 | 8.44 | 7.96 | 7.33 | 0.874 | 0.763 | 0.869 | 7.43 | 5.62 | -6.54 | Very Poor_Mixed | 1204.7 | 1334.6 | 1.108 | 0.99 | 9.44 | 0.957 | 8.44 | 0.1693 | 0.6367 | 0.1557 | 0.4126 | 1 | 0.0743 | 0.2296 | 0.3667 | 0.3667 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1508 | 597.1 | 404.3 | 90.6 | 93.3 | 13.2 | 674.7 | 4074.7 | 46.1 | 32.1 | 86.9 | 86 | 79.6 | 94.1 | 38.3 | 22.1 | 6704 | 7049.4 | 7439.4 | 11429.4 | 11703 | 12723.3 | 1.705 | 1.66 | 1.71 | 0.712 | 0.645 | 0.705 | -5.03 | 3.89 | 5.07 | 0.603 | 0.516 | 0.62 | -4.69 | 4.26 | -3.95 | 0.628 | 0.664 | 0.65 | -4.16 | 4 | 4.19 | 0.651 | 0.613 | 0.616 | 3.6 | -4.62 | 5.16 | Poor_Mixed | 6704 | 11429.4 | 1.66 | 0.712 | 5.07 | 0.664 | 5.16 | 0.5722 | 0.7691 | 0.6166 | 0.6786 | 1 | 0.522 | 0.5817 | 0.6687 | 0.6687 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1509 | 100 | 120 | 70.1 | 50 | 1.4 | 418.6 | 2537.5 | 57.7 | 20 | 76.6 | 75.7 | 70.2 | 80.9 | 35 | 12.2 | 9607.6 | 9652.2 | 10000 | 19215.2 | 19304.5 | 19821.3 | 2 | 2 | 1.982 | 0.55 | 0.508 | 0.566 | -2.55 | 2.17 | 2.62 | 0.5 | 0.5 | 0.522 | 2 | 2.09 | 2 | 0.536 | 0.518 | 0.525 | 2.52 | 2 | 2 | 0.502 | 0.5 | 0.525 | -2.32 | 2.37 | 2 | Good_Mixed | 9607.6 | 19215.2 | 1.982 | 0.566 | 2.62 | 0.536 | 2.52 | 0.9384 | 1 | 0.9539 | 0.9618 | 1 | 0.8479 | 0.9115 | 0.9409 | 0.9409 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1510 | 350.3 | 247 | 78.4 | 67.1 | 4.6 | 511.9 | 3134.7 | 54.8 | 27.2 | 79.9 | 80.8 | 71.3 | 82.5 | 36.7 | 12.9 | 3962.1 | 4239.5 | 4514.3 | 5333.8 | 5791.1 | 6215.7 | 1.346 | 1.366 | 1.377 | 0.685 | 0.682 | 0.653 | -4.87 | 5.35 | 3.65 | 0.623 | 0.566 | 0.625 | 2.59 | 2.42 | 3.13 | 0.592 | 0.621 | 0.551 | 3.2 | -3.03 | -3.68 | 0.552 | 0.544 | 0.576 | 3.95 | 2.69 | 3.76 | Poor_IR_PI | 3962.1 | 5333.8 | 1.346 | 0.685 | 5.35 | 0.625 | 3.95 | 0.7673 | 0.8352 | 0.8418 | 0.9461 | 1 | 0.5375 | 0.6803 | 0.7813 | 0.7813 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1511 | 163.5 | 203 | 68 | 53 | 1 | 350 | 3118.1 | 59.9 | 21.4 | 75.4 | 75.7 | 72.7 | 80.8 | 35 | 11.7 | 10000 | 9372.8 | 8531.8 | 19520.1 | 17637.1 | 16291.9 | 1.952 | 1.882 | 1.91 | 0.512 | 0.586 | 0.535 | 2.05 | 3.03 | 2.38 | 0.524 | 0.5 | 0.5 | 2.17 | 2.89 | 2.38 | 0.51 | 0.538 | 0.525 | 2.64 | 3.33 | 2 | 0.516 | 0.529 | 0.555 | -2 | 2.12 | 2 | Good_Mixed | 8531.8 | 16291.9 | 1.882 | 0.586 | 3.03 | 0.555 | 3.33 | 0.9683 | 0.9432 | 0.9448 | 0.9724 | 1 | 0.8418 | 0.8677 | 0.9324 | 0.9324 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1512 | 419.4 | 289.4 | 78.7 | 81.1 | 3.8 | 417.5 | 3945.1 | 60 | 20.1 | 79.2 | 77.5 | 74.5 | 84.9 | 36 | 12.6 | 5961.1 | 4642.8 | 3777.6 | 9247.7 | 7068.2 | 5059 | 1.551 | 1.522 | 1.339 | 0.596 | 0.615 | 0.598 | 3.51 | -4.3 | -3.15 | 0.561 | 0.548 | 0.578 | -2.02 | 2.62 | 2.4 | 0.5 | 0.553 | 0.53 | 2.14 | 2.38 | 2.57 | 0.5 | 0.557 | 0.599 | 2.78 | -2.49 | 2.96 | Poor_IR_PI | 3777.6 | 5059 | 1.339 | 0.615 | 4.3 | 0.599 | 2.96 | 0.7605 | 0.9898 | 0.8423 | 0.953 | 1 | 0.6716 | 0.8007 | 0.8389 | 0.8389 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1513 | 342.8 | 182.9 | 76 | 58.8 | 2 | 456 | 3431.3 | 60 | 20 | 78.3 | 78 | 73.6 | 84.9 | 36.9 | 15.7 | 9449.3 | 9428.3 | 10000 | 17762 | 18856.7 | 20000 | 1.88 | 2 | 2 | 0.529 | 0.583 | 0.5 | -2.27 | 3.31 | 2.11 | 0.5 | 0.5 | 0.507 | -2 | 2.09 | 2.41 | 0.527 | 0.533 | 0.504 | -2.41 | 2.86 | 2.64 | 0.512 | 0.5 | 0.542 | 2.48 | 2 | -2 | Good_Mixed | 9428.3 | 17762 | 1.88 | 0.583 | 3.31 | 0.542 | 2.86 | 0.8477 | 1 | 0.8483 | 0.8746 | 1 | 0.8609 | 0.9035 | 0.9036 | 0.9036 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1514 | 292.5 | 188.6 | 76.9 | 70 | 5.3 | 494.2 | 3165.9 | 57.1 | 22.1 | 77.6 | 75 | 71.8 | 81.4 | 35.9 | 14.2 | 9382.3 | 9779.1 | 9607.1 | 16961.5 | 19470.1 | 18587.2 | 1.808 | 1.991 | 1.935 | 0.541 | 0.543 | 0.57 | 2.37 | 2.48 | 2.01 | 0.56 | 0.502 | 0.549 | 2 | -2 | 2.97 | 0.526 | 0.55 | 0.547 | -2.54 | 2.08 | -2 | 0.527 | 0.5 | 0.518 | 2.72 | 2.4 | 2.02 | Good_Mixed | 9382.3 | 16961.5 | 1.808 | 0.57 | 2.48 | 0.56 | 2.97 | 0.7698 | 0.926 | 0.9329 | 0.9144 | 1 | 0.8383 | 0.8448 | 0.872 | 0.872 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1515 | 882 | 549.1 | 100.3 | 115.5 | 20.2 | 796 | 5259.9 | 47 | 32.9 | 89.6 | 91.5 | 83.7 | 96.2 | 40.1 | 22.7 | 5002.2 | 5427.4 | 4830.4 | 7328.9 | 8284.6 | 6985.7 | 1.465 | 1.526 | 1.446 | 0.776 | 0.746 | 0.72 | 6.3 | 5.5 | 5.45 | 0.63 | 0.656 | 0.668 | 4.04 | -4.37 | 3.17 | 0.605 | 0.659 | 0.658 | -4.94 | 3.76 | 4.96 | 0.671 | 0.67 | 0.694 | 4.13 | 5.49 | -3.46 | Poor_Mixed | 4830.4 | 6985.7 | 1.446 | 0.776 | 6.3 | 0.694 | 5.49 | 0.4306 | 0.7593 | 0.5128 | 0.6585 | 1 | 0.4055 | 0.5232 | 0.5939 | 0.5939 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1516 | 263.1 | 179.8 | 70 | 50 | 2.7 | 391.9 | 2500 | 30.6 | 48.3 | 82.3 | 81.9 | 77 | 87.6 | 36.5 | 14.9 | 4885.2 | 4620.2 | 4614.6 | 7488.7 | 6704.3 | 6749.9 | 1.533 | 1.451 | 1.463 | 0.71 | 1.39 | 0.677 | 5.4 | 4.2 | 4.86 | 0.5 | 0.525 | 0.572 | 2.29 | -2.12 | 2.1 | 0.523 | 0.508 | 0.5 | 2.35 | 2.28 | 2 | 0.554 | 0.524 | 0.541 | 2.48 | 2.31 | -2 | Critical_Oil | 4614.6 | 6704.3 | 1.451 | 1.39 | 5.4 | 0.572 | 2.48 | 0.8771 | 0.5988 | 0.7421 | 0.8962 | 1 | 0.4286 | 0.8633 | 0.7855 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | Moisture_PPM
1517 | 193.6 | 146.3 | 67.7 | 50 | 1.2 | 350 | 2500 | 45.2 | 33 | 75 | 77.6 | 71.4 | 80.9 | 35.4 | 13.1 | 7956.6 | 6998.9 | 8237.3 | 13650.7 | 11911.7 | 14546 | 1.716 | 1.702 | 1.766 | 0.547 | 0.58 | 0.509 | -3.6 | 2.91 | -2.53 | 0.597 | 0.5 | 0.553 | 2.84 | 2.75 | 3.16 | 0.5 | 0.5 | 0.524 | 2 | 2.82 | 3.41 | 0.5 | 0.521 | 0.596 | -2 | 2.9 | 2.83 | Fair_Oil | 6998.9 | 11911.7 | 1.702 | 0.58 | 3.6 | 0.597 | 3.41 | 0.9517 | 0.7581 | 0.9414 | 0.9414 | 1 | 0.8021 | 0.8436 | 0.8942 | 0.8942 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1518 | 322 | 231.6 | 78.7 | 64.4 | 2.4 | 477.6 | 3433.4 | 14.7 | 21 | 87.4 | 83.8 | 79.4 | 92.7 | 38.6 | 18.4 | 690 | 1651.7 | 1319.2 | 709.3 | 1851 | 1436.1 | 1.028 | 1.121 | 1.089 | 0.671 | 0.686 | 0.676 | -4.46 | 5.08 | 5.34 | 0.552 | 0.536 | 0.535 | -2.35 | 2.67 | 2.65 | 0.574 | 0.559 | 0.521 | 2.9 | -3.14 | 3.21 | 0.5 | 0.527 | 0.553 | 2.35 | 2.14 | -3.37 | Critical_IR_PI | 690 | 709.3 | 1.028 | 0.686 | 5.34 | 0.574 | 3.37 | 0.8193 | 0.371 | 0.6359 | 0.7963 | 0.925 | 0.5129 | 0.7941 | 0.7155 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
1519 | 323.8 | 239.4 | 73.1 | 141.6 | 2.8 | 490.8 | 3752.4 | 17 | 25 | 103.9 | 102.8 | 91.2 | 111.6 | 44.2 | 11.1 | 8415 | 8426.2 | 8864.5 | 15434.2 | 15612.6 | 16638.6 | 1.834 | 1.853 | 1.877 | 0.589 | 0.59 | 0.644 | 3.78 | 3.75 | -4.26 | 0.563 | 0.618 | 0.559 | 3.77 | 3.38 | -3.03 | 0.548 | 0.531 | 0.528 | 3.74 | 3.7 | -2.48 | 0.589 | 0.6 | 0.565 | 2.89 | 3.55 | 2.77 | Critical_Thermal | 8415 | 15434.2 | 1.834 | 0.644 | 4.26 | 0.618 | 3.77 | 0.725 | 0.2867 | 0.208 | 0.984 | 1 | 0.6497 | 0.7067 | 0.6638 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1520 | 822.4 | 520.1 | 100.8 | 116.7 | 18 | 865.6 | 5285.8 | 45.5 | 34.8 | 91.6 | 88.7 | 82.2 | 97 | 38.9 | 25.3 | 5199.6 | 5263.6 | 5622.3 | 7784.9 | 7961.2 | 8761.1 | 1.497 | 1.513 | 1.558 | 0.725 | 0.787 | 0.708 | 5.93 | 6.14 | 6.25 | 0.651 | 0.667 | 0.679 | 4.87 | 4.25 | -4.75 | 0.628 | 0.654 | 0.693 | 3.99 | 4.55 | -4.45 | 0.689 | 0.672 | 0.612 | 5.92 | 5.87 | 5.52 | Poor_Mixed | 5199.6 | 7784.9 | 1.497 | 0.787 | 6.25 | 0.693 | 5.92 | 0.4412 | 0.7368 | 0.5312 | 0.569 | 1 | 0.3925 | 0.4935 | 0.5841 | 0.5841 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1521 | 1054 | 642.1 | 122.8 | 140.8 | 21.4 | 1006.7 | 6348 | 54.4 | 25 | 81.2 | 79.8 | 73.3 | 87.2 | 35.9 | 12.2 | 8728.7 | 8443.2 | 8225.8 | 16634.3 | 15339.5 | 15291.6 | 1.906 | 1.817 | 1.859 | 0.515 | 0.541 | 0.544 | 2.11 | 3.05 | 2.92 | 0.547 | 0.553 | 0.609 | -2.41 | -2.81 | 2.53 | 0.52 | 0.54 | 0.578 | 3.13 | 2.3 | 2.81 | 0.562 | 0.527 | 0.528 | -3.37 | 3.38 | 2.56 | Poor_DGA | 8225.8 | 15291.6 | 1.817 | 0.544 | 3.05 | 0.609 | 3.38 | 0.3222 | 0.87 | 0.8018 | 0.9618 | 1 | 0.8406 | 0.7585 | 0.7274 | 0.7274 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1522 | 890.2 | 465.9 | 109.3 | 126.7 | 16.2 | 779.4 | 5634 | 44.8 | 33.8 | 88.6 | 91.3 | 84.8 | 98.9 | 40.3 | 24.5 | 6106.6 | 5441 | 6164.3 | 10067.5 | 8341.7 | 9723.5 | 1.649 | 1.533 | 1.577 | 0.771 | 0.721 | 0.739 | 6.54 | 5.79 | 5.71 | 0.742 | 0.687 | 0.697 | 5.62 | -4.72 | -4.27 | 0.71 | 0.69 | 0.704 | 5.2 | 4.03 | 3.99 | 0.706 | 0.661 | 0.569 | 4.22 | 4.77 | -4.37 | Poor_Mixed | 5441 | 8341.7 | 1.533 | 0.771 | 6.54 | 0.742 | 5.62 | 0.4449 | 0.7485 | 0.4992 | 0.597 | 1 | 0.3941 | 0.478 | 0.582 | 0.582 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1523 | 764 | 504.7 | 100.4 | 110.2 | 14.2 | 819.4 | 5334.4 | 45.5 | 34.9 | 91.3 | 89.3 | 79.3 | 98.6 | 39.8 | 24.8 | 6009 | 6188.7 | 4998.4 | 9959.9 | 10061.5 | 7294.9 | 1.657 | 1.626 | 1.459 | 0.701 | 0.786 | 0.735 | -5.59 | -6.82 | 5.55 | 0.702 | 0.616 | 0.658 | 4.36 | 4.08 | 4.82 | 0.619 | 0.657 | 0.722 | 3.83 | 4.34 | -4.54 | 0.695 | 0.673 | 0.687 | 4.31 | 2.79 | 4.52 | Poor_Mixed | 4998.4 | 7294.9 | 1.459 | 0.786 | 6.82 | 0.722 | 4.82 | 0.4848 | 0.7356 | 0.5345 | 0.5865 | 1 | 0.3989 | 0.5102 | 0.5999 | 0.5999 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1524 | 1007.5 | 578.4 | 110.9 | 118.6 | 17.2 | 895.3 | 6171.8 | 46 | 34.9 | 87.6 | 86.3 | 79.5 | 94.6 | 39 | 26.6 | 6057.9 | 4127.7 | 4836.4 | 10100.6 | 5601.3 | 7024.3 | 1.667 | 1.357 | 1.452 | 0.776 | 0.76 | 0.72 | 5.94 | -6.18 | 5.05 | 0.683 | 0.719 | 0.635 | 4.66 | 4 | 4.4 | 0.671 | 0.684 | 0.563 | 5.91 | 4.86 | 4.44 | 0.624 | 0.652 | 0.713 | 6.44 | -3.6 | 4.44 | Poor_Mixed | 4127.7 | 5601.3 | 1.357 | 0.776 | 6.18 | 0.719 | 6.44 | 0.4029 | 0.7356 | 0.6036 | 0.5228 | 1 | 0.4032 | 0.5032 | 0.5825 | 0.5825 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1525 | 218.3 | 162 | 77 | 64.3 | 2.2 | 472.3 | 2853 | 56.6 | 21.1 | 77.4 | 77.4 | 71.7 | 82.1 | 35 | 13 | 6458.3 | 5140.8 | 6518 | 10600.6 | 7357.2 | 11037.6 | 1.641 | 1.431 | 1.693 | 0.615 | 0.645 | 0.607 | 3.65 | 3.6 | 3.2 | 0.544 | 0.534 | 0.5 | -2.69 | -3.02 | 2.42 | 0.579 | 0.556 | 0.521 | 3.31 | 2.4 | 2.89 | 0.592 | 0.527 | 0.5 | 2.29 | 2 | 2.52 | Fair_IR_PI | 5140.8 | 7357.2 | 1.431 | 0.645 | 3.65 | 0.592 | 3.31 | 0.8487 | 0.9514 | 0.9024 | 0.9438 | 1 | 0.6596 | 0.8135 | 0.8625 | 0.8625 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1526 | 897.7 | 515 | 98.7 | 124.7 | 17.2 | 846.6 | 4986 | 47.3 | 31.4 | 88.2 | 85.6 | 82 | 94.7 | 39.1 | 23.6 | 7783.3 | 5922.1 | 4547.3 | 12890.8 | 9314.7 | 6651.5 | 1.656 | 1.573 | 1.463 | 0.708 | 0.732 | 0.809 | 4.8 | -5.17 | 5.78 | 0.586 | 0.577 | 0.669 | 3.98 | 4.39 | 4.33 | 0.587 | 0.667 | 0.665 | -5.04 | 3.94 | 3.9 | 0.681 | 0.632 | 0.638 | 4.75 | 4.05 | 4.41 | Poor_Mixed | 4547.3 | 6651.5 | 1.463 | 0.809 | 5.78 | 0.681 | 5.04 | 0.44 | 0.7778 | 0.5869 | 0.628 | 1 | 0.4324 | 0.5543 | 0.6137 | 0.6137 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1527 | 295.5 | 293.3 | 75.9 | 90.6 | 1.7 | 422.6 | 2927.3 | 58.1 | 21.7 | 88.3 | 87.6 | 82.5 | 95.3 | 38.7 | 11.6 | 9771.8 | 10000 | 9000.5 | 19145.9 | 20000 | 16946.5 | 1.959 | 2 | 1.883 | 0.524 | 0.501 | 0.533 | 2.54 | 2.41 | 2 | 0.53 | 0.508 | 0.54 | 2.25 | 2.54 | -2.22 | 0.567 | 0.508 | 0.539 | 2.84 | 2 | 2.78 | 0.551 | 0.604 | 0.5 | 2.68 | 2.73 | 2.08 | Fair_Thermal | 9000.5 | 16946.5 | 1.883 | 0.533 | 2.54 | 0.604 | 2.84 | 0.8167 | 0.9355 | 0.5684 | 0.9744 | 1 | 0.9038 | 0.8194 | 0.856 | 0.856 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1528 | 1168.5 | 599.6 | 121.8 | 148.7 | 25.7 | 991.7 | 5737.9 | 56.9 | 23.3 | 77.4 | 80.1 | 72.3 | 81.1 | 35.2 | 11.9 | 8870.8 | 9518.1 | 9226.2 | 16593.3 | 18159.3 | 16613 | 1.871 | 1.908 | 1.801 | 0.51 | 0.544 | 0.561 | 2.2 | 2.98 | 2.62 | 0.55 | 0.528 | 0.547 | 3.27 | 2.01 | -3 | 0.541 | 0.525 | 0.535 | 2.42 | 2.89 | 2.61 | 0.503 | 0.505 | 0.595 | 2.74 | 2.14 | -2.27 | Poor_DGA | 8870.8 | 16593.3 | 1.801 | 0.561 | 2.98 | 0.595 | 3.27 | 0.2975 | 0.9008 | 0.8758 | 0.9682 | 1 | 0.8405 | 0.8105 | 0.742 | 0.742 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1529 | 1437 | 837.2 | 133 | 168.3 | 31.2 | 1196.7 | 8010.9 | 33.2 | 45.9 | 107.9 | 106.3 | 91.4 | 115.7 | 43.6 | 30.5 | 2099 | 2231.2 | 2383.7 | 2481.6 | 2500.8 | 2848.8 | 1.182 | 1.121 | 1.195 | 0.921 | 0.952 | 0.932 | 8.56 | 9.59 | 8.94 | 0.885 | 0.816 | 0.894 | -8.51 | 8.51 | 6.15 | 0.916 | 0.93 | 0.7 | -7.78 | -6.5 | -8.68 | 0.705 | 0.879 | 0.925 | -7.08 | -5.97 | 7.06 | Very Poor_Mixed | 2099 | 2481.6 | 1.121 | 0.952 | 9.59 | 0.93 | 8.68 | 0.1492 | 0.6213 | 0.149 | 0.3787 | 1 | 0.0914 | 0.2124 | 0.3567 | 0.3567 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1530 | 918.5 | 546.8 | 103.8 | 126.1 | 18.8 | 785.8 | 5797.3 | 47.8 | 32.7 | 87.7 | 88.2 | 84 | 95.4 | 39 | 25.8 | 5046.6 | 5072.3 | 5177.8 | 7083 | 7523.8 | 7692.8 | 1.404 | 1.483 | 1.486 | 0.772 | 0.725 | 0.753 | 5.62 | -6.1 | 6.29 | 0.706 | 0.733 | 0.662 | 5.47 | 3.19 | 5.36 | 0.638 | 0.761 | 0.711 | 4.2 | 4.2 | 3.47 | 0.681 | 0.72 | 0.629 | 5.29 | 4.74 | 5.21 | Poor_Mixed | 5046.6 | 7083 | 1.404 | 0.772 | 6.29 | 0.761 | 5.47 | 0.4192 | 0.7617 | 0.5566 | 0.5513 | 1 | 0.3891 | 0.4674 | 0.578 | 0.578 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1531 | 1708.1 | 969.8 | 148.3 | 197 | 34.3 | 1379 | 7988.4 | 32.3 | 48.2 | 108.6 | 103.2 | 94.2 | 115.1 | 44.4 | 31.8 | 1211.4 | 2260.2 | 690 | 1307.7 | 2541.3 | 1200 | 1.079 | 1.124 | 1.739 | 0.981 | 0.937 | 0.941 | 9.49 | 9.84 | 9.36 | 0.871 | 0.774 | 0.741 | 7.81 | 6.52 | 8.41 | 0.729 | 0.794 | 0.739 | 9.12 | -6.9 | 7.8 | 0.975 | 0.837 | 0.864 | 7.96 | 6.82 | 5.19 | Very Poor_Mixed | 690 | 1200 | 1.079 | 0.981 | 9.84 | 0.975 | 9.12 | 0.0463 | 0.5998 | 0.1439 | 0.3291 | 1 | 0.0526 | 0.244 | 0.3257 | 0.3257 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1532 | 1663.7 | 930.6 | 140.1 | 197 | 33.7 | 1340.9 | 8459.9 | 31.5 | 49 | 104.1 | 102.9 | 92.2 | 111.9 | 44.3 | 33.3 | 2211.6 | 2056.6 | 3706.2 | 2651.4 | 2210.8 | 4401.9 | 1.199 | 1.075 | 1.188 | 0.905 | 0.923 | 0.99 | 8.34 | 9.01 | 9.56 | 0.873 | 0.759 | 0.818 | -9.3 | 7.27 | -8.31 | 0.911 | 0.906 | 0.714 | -7.27 | 7.61 | -7.96 | 0.912 | 0.834 | 0.797 | -8.77 | -8.5 | 8.4 | Very Poor_Mixed | 2056.6 | 2210.8 | 1.075 | 0.99 | 9.56 | 0.912 | 9.3 | 0.0607 | 0.5924 | 0.1984 | 0.2709 | 1 | 0.0919 | 0.1974 | 0.328 | 0.328 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1533 | 1261 | 801.7 | 133.9 | 167.3 | 26.6 | 1090.4 | 6941.9 | 38.7 | 41.5 | 101.3 | 105.6 | 91 | 112.4 | 43.5 | 31.5 | 2458.9 | 1839.4 | 3333.6 | 3160.6 | 2191.9 | 4291.4 | 1.285 | 1.192 | 1.287 | 0.906 | 0.844 | 2.085 | -8.74 | 7.12 | 8.16 | 0.738 | 0.775 | 0.808 | 7.12 | 6.92 | 6.14 | 0.83 | 0.716 | 0.655 | 6.44 | 6.96 | 5.75 | 0.697 | 0.732 | 0.758 | 4.87 | 6.32 | 7.67 | Critical_Mixed | 1839.4 | 2191.9 | 1.192 | 2.085 | 8.74 | 0.83 | 7.67 | 0.2132 | 0.6645 | 0.2093 | 0.3406 | 1 | 0.1575 | 0.3417 | 0.4145 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
1534 | 141.3 | 201.1 | 69.6 | 76.7 | 2.5 | 416.9 | 3825.9 | 58.5 | 20 | 75.2 | 75.5 | 70 | 82 | 35 | 10.7 | 9912.2 | 10000 | 10000 | 19755.7 | 19180.1 | 20000 | 1.993 | 1.918 | 2 | 0.5 | 0.5 | 0.526 | -2 | 2.37 | 2.06 | 0.521 | 0.507 | 0.5 | 2.14 | -2.2 | 2.25 | 0.5 | 0.5 | 0.501 | 2 | -2.14 | 2.44 | 0.51 | 0.5 | 0.5 | -2 | 2 | 2.31 | Good_Mixed | 9912.2 | 19180.1 | 1.918 | 0.526 | 2.37 | 0.521 | 2.44 | 0.836 | 1 | 0.9745 | 0.9909 | 1 | 0.9559 | 0.9552 | 0.9417 | 0.9417 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1535 | 1508.7 | 868.3 | 135.8 | 181.9 | 32.7 | 1226.2 | 7967.1 | 32.9 | 47.4 | 100.7 | 102.7 | 89.6 | 113.1 | 42.1 | 29.8 | 1875.5 | 2236.9 | 1025.1 | 2168.3 | 2348.7 | 1200 | 1.156 | 1.05 | 1.171 | 0.964 | 0.912 | 0.961 | 9.52 | -8.82 | -9.25 | 0.808 | 0.763 | 0.77 | -8.41 | 6.53 | 7.01 | 0.735 | 0.786 | 0.895 | 8.21 | 8.3 | 6.42 | 0.873 | 0.776 | 0.808 | 7.03 | -9.16 | 5.9 | Very Poor_Mixed | 1025.1 | 1200 | 1.05 | 0.964 | 9.52 | 0.895 | 9.16 | 0.1176 | 0.6072 | 0.2434 | 0.4051 | 1 | 0.0759 | 0.2519 | 0.3628 | 0.3628 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1536 | 140.7 | 120 | 65 | 53 | 1 | 450.2 | 2533.9 | 58.8 | 20 | 76.7 | 75 | 70 | 80 | 36 | 12.5 | 9513.3 | 10000 | 10000 | 18432.2 | 20000 | 19875.3 | 1.938 | 2 | 1.988 | 0.56 | 0.5 | 0.507 | 3.29 | 2 | -2 | 0.537 | 0.524 | 0.5 | 2 | 2 | -2.18 | 0.519 | 0.505 | 0.506 | 2.11 | 2.51 | 2 | 0.523 | 0.5 | 0.518 | 2 | 2 | 2.49 | Good_Mixed | 9513.3 | 18432.2 | 1.938 | 0.56 | 3.29 | 0.537 | 2.51 | 0.9642 | 1 | 0.9703 | 0.9552 | 1 | 0.9034 | 0.9042 | 0.9551 | 0.9551 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
1537 | 753.6 | 439.2 | 95.2 | 105.3 | 12.7 | 744.4 | 5100.1 | 58 | 22.5 | 75.4 | 76.9 | 72.5 | 82.4 | 35.5 | 14.1 | 9201.6 | 8509.5 | 9760.2 | 17890.4 | 17019.1 | 19520.3 | 1.944 | 2 | 2 | 0.586 | 0.554 | 0.513 | 2.9 | -3.13 | -3.07 | 0.5 | 0.508 | 0.54 | 2.92 | -2.49 | 2.15 | 0.529 | 0.54 | 0.55 | 2.57 | 2.07 | -2.6 | 0.52 | 0.5 | 0.5 | -2.16 | 3.2 | 2.65 | Fair_DGA | 8509.5 | 17019.1 | 1.944 | 0.586 | 3.13 | 0.55 | 3.2 | 0.5247 | 0.9171 | 0.9221 | 0.9169 | 1 | 0.7895 | 0.8687 | 0.8062 | 0.8062 | Good | 1 | 1 | DGA | 0 |  | C2H2
1538 | 875.2 | 437.5 | 103.5 | 121.1 | 16.5 | 768.1 | 4661.1 | 44.7 | 32.5 | 91.6 | 88.8 | 81.8 | 99.3 | 39.6 | 26.8 | 5554.7 | 5897.9 | 5999.9 | 8631.2 | 9259.5 | 8972.7 | 1.554 | 1.57 | 1.495 | 0.743 | 0.702 | 0.694 | 5.69 | 5.78 | -4.76 | 0.678 | 0.614 | 0.668 | 4.04 | 4.32 | -5.97 | 0.701 | 0.727 | 0.723 | -4.59 | 3.99 | 5.17 | 0.713 | 0.711 | 0.689 | 3.49 | 5.82 | -4.48 | Poor_Mixed | 5554.7 | 8631.2 | 1.495 | 0.743 | 5.78 | 0.727 | 5.97 | 0.468 | 0.7641 | 0.5172 | 0.5156 | 1 | 0.4547 | 0.4656 | 0.5937 | 0.5937 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1539 | 1647.2 | 826.5 | 133.8 | 170.8 | 30.2 | 1216.3 | 8053.6 | 32.2 | 46.3 | 108.8 | 105.6 | 95.7 | 116.7 | 45.3 | 33.6 | 1503.4 | 1668 | 2064.3 | 1581.5 | 1877.6 | 2205.2 | 1.052 | 1.126 | 1.068 | 0.954 | 0.976 | 0.96 | 9.84 | 8.95 | 9.49 | 0.819 | 0.878 | 0.79 | 8.9 | 6.59 | 7.36 | 0.875 | 0.897 | 0.772 | 8.33 | 5.52 | 9.39 | 0.972 | 0.732 | 0.938 | 7.74 | 6.95 | 8.21 | Very Poor_Mixed | 1503.4 | 1581.5 | 1.052 | 0.976 | 9.84 | 0.972 | 9.39 | 0.1344 | 0.6175 | 0.1065 | 0.2591 | 1 | 0.0525 | 0.1989 | 0.3344 | 0.3344 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1540 | 1514.9 | 784.8 | 129.3 | 165.6 | 32.1 | 1203.9 | 6994.6 | 33.2 | 46.1 | 103.3 | 103.9 | 93.2 | 113.4 | 43.6 | 32.4 | 2210.6 | 2426 | 1382 | 2321.6 | 2900.6 | 1492.1 | 1.05 | 1.196 | 1.08 | 0.902 | 0.928 | 0.924 | -8.96 | 7.62 | 8.96 | 0.808 | 0.862 | 0.799 | 8.4 | 7.3 | 7.73 | 0.879 | 0.847 | 0.782 | -6.2 | 6.41 | 8.42 | 0.73 | 0.775 | 0.711 | 5.02 | 6.55 | -4.92 | Very Poor_Mixed | 1382 | 1492.1 | 1.05 | 0.928 | 8.96 | 0.879 | 8.42 | 0.1623 | 0.6194 | 0.1892 | 0.3059 | 1 | 0.1293 | 0.277 | 0.3771 | 0.3771 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1541 | 277.8 | 226.3 | 75.6 | 153 | 2.5 | 550.5 | 2961.7 | 54.2 | 24.4 | 103.7 | 105.5 | 92.5 | 115.7 | 44.1 | 11.9 | 7532.9 | 7199.8 | 8270.3 | 13549.8 | 12816 | 8108.8 | 1.799 | 1.78 | 0.98 | 0.547 | 0.516 | 0.535 | 3.33 | -2.08 | 2.92 | 0.525 | 0.5 | 0.517 | 2.62 | 2.51 | -2 | 0.5 | 0.52 | 0.502 | 2.65 | 2.45 | 2.29 | 0.54 | 0.533 | 0.557 | 2.48 | 2.28 | 2.07 | Critical_Thermal | 7199.8 | 8108.8 | 0.98 | 0.547 | 3.33 | 0.557 | 2.65 | 0.7222 | 0.8804 | 0.1668 | 0.9682 | 0.8125 | 0.8365 | 0.8709 | 0.7552 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H4
1542 | 1487.8 | 759 | 128.4 | 180.9 | 24.7 | 1277 | 7745.8 | 36.4 | 44 | 105.7 | 103.8 | 92.7 | 112.3 | 45.9 | 30.5 | 2198.3 | 2556.1 | 2315.8 | 2447.9 | 3249 | 2808.7 | 1.114 | 1.271 | 1.213 | 0.96 | 0.906 | 0.929 | -8.84 | 8.13 | 9.61 | 0.677 | 0.857 | 0.786 | -7.86 | 7.32 | 7.77 | 0.808 | 0.834 | 0.824 | -7.26 | 5.74 | 7.08 | 0.69 | 0.669 | 0.652 | 8.17 | 6.11 | 5.58 | Very Poor_Mixed | 2198.3 | 2447.9 | 1.114 | 0.96 | 9.61 | 0.857 | 8.17 | 0.173 | 0.6396 | 0.1677 | 0.3787 | 1 | 0.1024 | 0.3172 | 0.3871 | 0.3871 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1543 | 787.8 | 453.7 | 99.1 | 110.6 | 19.5 | 809.9 | 5089.3 | 46.2 | 34 | 85.8 | 88.7 | 79.5 | 92.6 | 39.2 | 24 | 6392.6 | 5874.8 | 6447.8 | 10171.7 | 8751.6 | 10284.9 | 1.591 | 1.49 | 1.595 | 0.781 | 0.719 | 0.774 | -6.13 | -5.47 | 5.98 | 0.616 | 0.676 | 0.747 | -4.88 | 4.48 | 4.27 | 0.656 | 0.649 | 0.642 | 4.98 | -5.43 | 5.85 | 0.696 | 0.663 | 0.698 | 4.52 | -3.91 | 4.79 | Poor_Mixed | 5874.8 | 8751.6 | 1.49 | 0.781 | 6.13 | 0.747 | 5.85 | 0.4585 | 0.7461 | 0.6084 | 0.6143 | 1 | 0.3905 | 0.4848 | 0.5977 | 0.5977 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1544 | 961.8 | 545.4 | 108.4 | 125.2 | 20.4 | 851.5 | 5927.3 | 44 | 36.5 | 89.3 | 92.5 | 82.2 | 97.9 | 39.8 | 25.5 | 5109.4 | 6986.7 | 6507.6 | 7948.6 | 11052.6 | 10445.1 | 1.556 | 1.582 | 1.605 | 0.76 | 0.702 | 0.704 | 5.96 | 5.53 | 5.99 | 0.635 | 0.649 | 0.723 | 5.69 | -5.72 | 5.27 | 0.673 | 0.715 | 0.623 | 4.96 | 4.48 | 5.29 | 0.64 | 0.669 | 0.66 | 4.31 | 5.7 | -4.32 | Poor_Mixed | 5109.4 | 7948.6 | 1.556 | 0.76 | 5.99 | 0.723 | 5.72 | 0.3944 | 0.7175 | 0.5112 | 0.562 | 1 | 0.4234 | 0.4815 | 0.5699 | 0.5699 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1545 | 1498.6 | 783.6 | 135.1 | 175.4 | 30.5 | 1152.2 | 7397 | 35.1 | 46.8 | 104.9 | 101.6 | 93.3 | 113.3 | 43 | 29.6 | 2272.1 | 1903.1 | 3016.2 | 2807 | 2254.7 | 3557.6 | 1.235 | 1.185 | 1.179 | 0.871 | 0.944 | 0.896 | 8.03 | 8.37 | -8.8 | 0.796 | 0.899 | 0.816 | 8.68 | 8.1 | 8.27 | 0.778 | 0.928 | 0.944 | 7.31 | 8.66 | 6.5 | 0.777 | 0.844 | 0.888 | 8.46 | 6.44 | 5.63 | Very Poor_Mixed | 1903.1 | 2254.7 | 1.179 | 0.944 | 8.8 | 0.944 | 8.68 | 0.1589 | 0.6128 | 0.1974 | 0.4126 | 1 | 0.1451 | 0.2012 | 0.3702 | 0.3702 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1546 | 342.9 | 169.7 | 78.7 | 62.6 | 1 | 485.6 | 3463.7 | 59.8 | 20 | 78.4 | 81 | 72.6 | 82.6 | 35.9 | 12.9 | 9208.9 | 9938 | 9581.1 | 17351.5 | 19651.7 | 17830.8 | 1.884 | 1.977 | 1.861 | 0.593 | 0.507 | 0.625 | 3.5 | 2.67 | -2.99 | 0.556 | 0.573 | 0.501 | 3.32 | 2.76 | 3.22 | 0.584 | 0.517 | 0.749 | 2.22 | -2.95 | -5.97 | 0.537 | 0.566 | 0.61 | 2.4 | 2.26 | -3.44 | Poor_Bushing_TD_Cap | 9208.9 | 17351.5 | 1.861 | 0.625 | 3.5 | 0.749 | 5.97 | 0.9021 | 1 | 0.8452 | 0.9461 | 1 | 0.7611 | 0.7139 | 0.8724 | 0.8724 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1547 | 214.3 | 205.2 | 66 | 55.4 | 5 | 470.6 | 2554.9 | 58.9 | 20 | 77.3 | 75.4 | 72 | 80.1 | 35.7 | 10.9 | 10000 | 10000 | 9854.8 | 20000 | 18759.3 | 19709.7 | 2 | 1.876 | 2 | 0.546 | 0.524 | 0.5 | 2.07 | -2.46 | 2.13 | 0.5 | 0.5 | 0.517 | 2.05 | 2.69 | 2 | 0.5 | 0.552 | 0.512 | 2.4 | 2.39 | 2.8 | 0.513 | 0.547 | 0.52 | 2 | -2.34 | 2.86 | Good_Mixed | 9854.8 | 18759.3 | 1.876 | 0.546 | 2.46 | 0.552 | 2.86 | 0.8144 | 1 | 0.9329 | 0.9875 | 1 | 0.9074 | 0.8858 | 0.9127 | 0.9127 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1548 | 931.2 | 549.6 | 109.9 | 121.7 | 22.5 | 896.6 | 5771.9 | 57.4 | 23.2 | 81.7 | 84 | 75.5 | 89.5 | 38 | 11.6 | 8742.1 | 9574.6 | 9871.4 | 16401.3 | 19149.3 | 19742.8 | 1.876 | 2 | 2 | 0.5 | 0.515 | 0.519 | 2 | 2.53 | 2.31 | 0.551 | 0.551 | 0.5 | 2.45 | 2.12 | -2.76 | 0.541 | 0.5 | 0.544 | 3.11 | 3.28 | -2.61 | 0.51 | 0.531 | 0.536 | 2.71 | 2.11 | -2 | Poor_DGA | 8742.1 | 16401.3 | 1.876 | 0.519 | 2.53 | 0.551 | 3.28 | 0.3829 | 0.9027 | 0.7239 | 0.9744 | 1 | 0.9279 | 0.8371 | 0.7658 | 0.7658 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1549 | 238.2 | 120 | 69.6 | 55.2 | 2 | 458.6 | 2633.9 | 58.6 | 21.5 | 78.1 | 79.7 | 72.8 | 83.8 | 35.3 | 14.2 | 7429.6 | 6986.4 | 7312.3 | 13430.1 | 11594.8 | 12414.8 | 1.808 | 1.66 | 1.698 | 0.556 | 0.617 | 0.568 | -2.7 | 3.16 | -2.73 | 0.506 | 0.5 | 0.5 | 2.3 | 2.39 | 2 | 0.511 | 0.5 | 0.509 | 2.46 | 2.32 | -2.18 | 0.507 | 0.555 | 0.537 | 2 | -2.14 | 2.11 | Fair_IR_PI | 6986.4 | 11594.8 | 1.66 | 0.617 | 3.16 | 0.555 | 2.46 | 0.8799 | 0.9406 | 0.854 | 0.9144 | 1 | 0.7536 | 0.9107 | 0.8934 | 0.8934 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1550 | 404.8 | 262.3 | 83.3 | 80.1 | 2.4 | 577.6 | 3775.7 | 30.6 | 49.4 | 82.6 | 81.6 | 75 | 87.7 | 37.3 | 16.1 | 6464.7 | 5014.9 | 5027.5 | 9995.2 | 7381.8 | 7843.9 | 1.546 | 1.472 | 1.56 | 0.685 | 0.624 | 0.72 | 4.61 | -4.3 | -5.83 | 0.62 | 0.557 | 0.586 | 3.27 | 2.66 | 2.85 | 0.609 | 1.767 | 0.627 | 2.23 | 3.49 | 3.49 | 0.579 | 0.646 | 0.612 | -3.7 | -3.72 | -2.89 | Critical_Oil | 5014.9 | 7381.8 | 1.472 | 0.72 | 5.83 | 1.767 | 3.72 | 0.7669 | 0.5888 | 0.7522 | 0.8635 | 1 | 0.5191 | 0.5993 | 0.7213 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1551 | 383.1 | 302 | 86.2 | 77 | 9.9 | 563.2 | 3819.3 | 54.5 | 27.4 | 81.9 | 83.3 | 77.6 | 91.4 | 38.7 | 15.6 | 7681 | 8664.9 | 8636.6 | 13943 | 16493.7 | 15792 | 1.815 | 1.904 | 1.828 | 0.6 | 0.593 | 0.597 | 3.89 | 3.48 | 3.63 | 0.594 | 0.623 | 0.611 | 2.49 | -2.78 | -2.81 | 0.617 | 0.615 | 0.655 | 3.14 | 2.99 | 2.33 | 0.604 | 0.511 | 0.584 | -4.46 | 2.92 | 2.96 | Fair_Mixed | 7681 | 13943 | 1.815 | 0.6 | 3.89 | 0.655 | 4.46 | 0.6689 | 0.8323 | 0.6988 | 0.8773 | 1 | 0.6779 | 0.6621 | 0.7549 | 0.7549 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1552 | 1564.7 | 860.9 | 136.7 | 182.2 | 29.9 | 1219.8 | 7983.4 | 31.4 | 46.5 | 105.9 | 109.1 | 95.2 | 115.9 | 43.8 | 28.6 | 2041.1 | 2233.8 | 2493.4 | 2571.7 | 2468.4 | 2960 | 1.26 | 1.105 | 1.187 | 0.976 | 0.896 | 0.908 | 9.4 | 8.73 | -7.79 | 0.927 | 0.868 | 0.675 | 7.04 | 7.78 | 5.45 | 0.882 | 0.789 | 0.886 | 8.6 | 8.23 | 7.7 | 0.822 | 0.765 | 0.899 | 5.46 | -8.77 | 8.82 | Very Poor_Mixed | 2041.1 | 2468.4 | 1.105 | 0.976 | 9.4 | 0.927 | 8.82 | 0.1266 | 0.6156 | 0.1209 | 0.4498 | 1 | 0.1173 | 0.2201 | 0.3561 | 0.3561 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1553 | 387.1 | 244.2 | 76.4 | 70.6 | 1.5 | 461.5 | 3878.1 | 56.7 | 52.4 | 84.7 | 84.1 | 76 | 88.8 | 39.1 | 13.6 | 7077.8 | 7468 | 6202.7 | 11971.1 | 13365.2 | 10237 | 1.691 | 1.79 | 1.65 | 0.973 | 0.964 | 0.98 | 9.71 | -9.84 | -9.84 | 0.611 | 0.578 | 0.544 | -3.46 | 3.11 | 3.81 | 0.666 | 0.597 | 0.602 | 3.72 | 3.18 | 4.85 | 0.603 | 0.587 | 0.623 | 3.63 | 3.51 | 3.45 | Critical_Winding_TD_Cap | 6202.7 | 10237 | 1.65 | 0.98 | 9.84 | 0.666 | 4.85 | 0.8322 | 0.5833 | 0.6932 | 0.9294 | 1 | 0.0281 | 0.6291 | 0.671 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1554 | 100 | 152.7 | 68.6 | 50 | 3.7 | 350 | 2500 | 60 | 21.5 | 80.5 | 75.2 | 70 | 80 | 36.6 | 13.5 | 6024.8 | 6792.8 | 5906.5 | 10017 | 11062.4 | 9295.5 | 1.663 | 1.629 | 1.574 | 0.594 | 0.654 | 0.657 | 3.73 | 4.39 | 3.79 | 0.5 | 0.535 | 0.508 | 2 | -2 | 2.21 | 0.575 | 0.5 | 0.546 | -2.69 | -2.18 | 2.12 | 0.5 | 0.5 | 0.538 | 2 | 2.65 | 2 | Fair_IR_PI | 5906.5 | 9295.5 | 1.574 | 0.657 | 4.39 | 0.575 | 2.69 | 0.8917 | 0.9406 | 0.9256 | 0.9318 | 1 | 0.6164 | 0.8931 | 0.882 | 0.882 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1555 | 1766 | 982.4 | 145.8 | 193.4 | 34.3 | 1364.3 | 8774.9 | 50.2 | 27.2 | 83.4 | 81.9 | 77.1 | 89.7 | 38.3 | 19.6 | 7468.4 | 7342.9 | 6953 | 13764.2 | 12610 | 11731.6 | 1.843 | 1.717 | 1.687 | 0.645 | 0.695 | 0.627 | -4.07 | -4.5 | 4.48 | 0.606 | 0.558 | 0.584 | 3.48 | 3.81 | -2.83 | 0.591 | 0.617 | 0.645 | -3.86 | 3.81 | 3.02 | 0.553 | 1.098 | 0.581 | 2.95 | 3.23 | 3.44 | Critical_DGA | 6953 | 11731.6 | 1.687 | 0.695 | 4.5 | 1.098 | 3.86 | 0.0369 | 0.8352 | 0.7124 | 0.7593 | 1 | 0.5712 | 0.6069 | 0.5679 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
1556 | 867.9 | 444.4 | 100 | 117.3 | 16.3 | 851.2 | 5716.1 | 44.9 | 35.1 | 87.8 | 90.1 | 81.8 | 95.7 | 40.5 | 25.6 | 5924.3 | 6667.3 | 5493.6 | 9526.7 | 10362.4 | 7948.5 | 1.608 | 1.554 | 1.447 | 0.732 | 0.789 | 0.739 | 5.11 | -7.25 | -6.29 | 0.709 | 0.64 | 0.643 | 3.97 | 4.33 | 5.39 | 0.63 | 0.627 | 0.712 | 3.68 | 4.03 | -3.43 | 0.612 | 0.744 | 0.677 | 4.9 | -4.04 | -3.65 | Poor_Mixed | 5493.6 | 7948.5 | 1.447 | 0.789 | 7.25 | 0.744 | 5.39 | 0.4543 | 0.7333 | 0.546 | 0.5584 | 1 | 0.3755 | 0.5169 | 0.5897 | 0.5897 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1557 | 602.2 | 243.5 | 85.2 | 76.2 | 6.3 | 566.9 | 3712.9 | 54.2 | 25.1 | 84.8 | 80.3 | 76 | 87.6 | 37.5 | 16.7 | 9151.7 | 8287.3 | 8105.5 | 17455.9 | 15120.3 | 15362.1 | 1.907 | 1.825 | 1.895 | 0.531 | 0.593 | 0.509 | 2.23 | 3.41 | 3.02 | 0.601 | 0.616 | 0.605 | 3.07 | 3.64 | 3.62 | 0.511 | 0.592 | 0.615 | 2.54 | 2.37 | 2.83 | 0.591 | 0.5 | 0.604 | 2.6 | 2.6 | 2.84 | Fair_Mixed | 8105.5 | 15120.3 | 1.825 | 0.593 | 3.41 | 0.616 | 3.64 | 0.695 | 0.8683 | 0.7382 | 0.8465 | 1 | 0.8154 | 0.7105 | 0.7961 | 0.7961 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1558 | 328.5 | 262.3 | 76.6 | 69 | 1.6 | 461 | 3508.8 | 57.9 | 21.2 | 76.2 | 77.7 | 70 | 80.3 | 35.6 | 16.2 | 10000 | 9104 | 9495.7 | 19878.3 | 18011.8 | 18689.7 | 1.988 | 1.978 | 1.968 | 0.81 | 0.809 | 0.843 | 6.03 | 7.41 | 6.85 | 0.501 | 0.542 | 0.528 | 2 | 2 | -2.64 | 0.506 | 0.5 | 0.566 | 2.55 | 2.21 | -2.42 | 0.545 | 0.544 | 0.519 | 3.48 | 3.05 | 2 | Poor_Winding_TD_Cap | 9104 | 18011.8 | 1.968 | 0.843 | 7.41 | 0.566 | 3.48 | 0.8363 | 0.9486 | 0.9399 | 0.8607 | 1 | 0.2912 | 0.8467 | 0.8131 | 0.8131 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
1559 | 826.6 | 546.4 | 103.3 | 114.4 | 20.4 | 884.5 | 5161.4 | 43.7 | 35.7 | 92.9 | 88.7 | 81.9 | 97.3 | 40 | 24.6 | 4347.6 | 4193.2 | 5329.9 | 6388 | 5689.6 | 7875.8 | 1.469 | 1.357 | 1.478 | 0.745 | 0.732 | 0.691 | 5.61 | 5.02 | 4.93 | 0.652 | 0.586 | 0.662 | 5.08 | 3.97 | -5.62 | 0.732 | 0.629 | 0.622 | 4.18 | -4.25 | -5.6 | 0.695 | 0.603 | 0.638 | 4.17 | 4.11 | 4.41 | Poor_Mixed | 4193.2 | 5689.6 | 1.357 | 0.745 | 5.61 | 0.732 | 5.62 | 0.423 | 0.7265 | 0.5164 | 0.5935 | 1 | 0.4585 | 0.5257 | 0.5931 | 0.5931 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1560 | 988.1 | 532.3 | 114.7 | 125.9 | 20.9 | 926.8 | 6031.6 | 46.3 | 33.8 | 89.3 | 94.7 | 81.3 | 97.2 | 39.8 | 26.6 | 5181.1 | 5616.6 | 5196.8 | 7770.7 | 8342.4 | 7890.8 | 1.5 | 1.485 | 1.518 | 0.749 | 0.728 | 0.707 | 6.15 | 5.45 | 5.14 | 0.6 | 0.638 | 0.752 | 5.78 | -4.62 | -4.87 | 0.689 | 0.629 | 0.692 | 3.81 | 4.03 | 4.41 | 0.734 | 0.656 | 0.728 | -4.87 | 5.01 | 5.63 | Poor_Mixed | 5181.1 | 7770.7 | 1.485 | 0.749 | 6.15 | 0.752 | 5.78 | 0.3753 | 0.7485 | 0.5067 | 0.5228 | 1 | 0.4316 | 0.4768 | 0.5667 | 0.5667 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1561 | 1411.6 | 815.2 | 131.3 | 177.4 | 27.1 | 1153.6 | 7724.4 | 30.8 | 46.7 | 104.8 | 109.3 | 93.4 | 115.7 | 44.9 | 32.6 | 2189.9 | 2378.2 | 2914.3 | 2557.2 | 2941.4 | 3637.3 | 1.168 | 1.237 | 1.248 | 0.919 | 0.909 | 0.946 | 8.86 | 9.54 | 9 | 0.804 | 0.747 | 0.783 | 8.02 | 5.73 | -5.43 | 0.685 | 0.817 | 0.892 | 4.56 | 7.27 | -5.59 | 0.893 | 0.843 | 0.8 | 5.42 | 6.87 | 7.59 | Very Poor_Mixed | 2189.9 | 2557.2 | 1.168 | 0.946 | 9.54 | 0.893 | 8.02 | 0.1749 | 0.6137 | 0.129 | 0.2982 | 1 | 0.0932 | 0.2868 | 0.3699 | 0.3699 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1562 | 262.4 | 150.9 | 65.7 | 51.9 | 3 | 400.9 | 2500 | 60 | 22.5 | 79.1 | 78.2 | 72.9 | 80 | 36.2 | 14.6 | 8573.9 | 9426.6 | 8742.6 | 15658.3 | 18050 | 16719.2 | 1.826 | 1.915 | 1.912 | 0.5 | 0.507 | 0.503 | -2 | -2.8 | 2.32 | 0.5 | 0.5 | 0.545 | 2.83 | 2.49 | 2.22 | 0.504 | 0.505 | 0.572 | 2.23 | 2.92 | 2.58 | 0.5 | 0.556 | 0.5 | 2.3 | 2 | 2 | Good_Mixed | 8573.9 | 15658.3 | 1.826 | 0.507 | 2.8 | 0.572 | 2.92 | 0.8687 | 0.9171 | 0.8727 | 0.904 | 1 | 0.946 | 0.8923 | 0.9128 | 0.9128 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1563 | 332 | 226.4 | 74 | 72.9 | 1.8 | 473.4 | 3040.9 | 58.2 | 21.3 | 75.7 | 76.7 | 71 | 82.9 | 35 | 11.1 | 8462.8 | 9199.1 | 8623.2 | 15296.2 | 17654.5 | 15680.9 | 1.807 | 1.919 | 1.818 | 0.785 | 0.746 | 0.721 | 5.71 | 5.69 | 5.78 | 0.54 | 0.529 | 0.5 | 2.72 | 3.16 | 2 | 0.537 | 0.508 | 0.556 | 2.79 | 2.73 | 2.84 | 0.543 | 0.5 | 0.5 | 2.91 | 2.52 | 2.51 | Fair_Winding_TD_Cap | 8462.8 | 15296.2 | 1.807 | 0.785 | 5.78 | 0.556 | 3.16 | 0.8304 | 0.9458 | 0.9332 | 0.984 | 1 | 0.4039 | 0.8534 | 0.8338 | 0.8338 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
1564 | 437.2 | 346.5 | 88.7 | 148.6 | 2.6 | 652.4 | 4092.4 | 12 | 22.6 | 105.2 | 104.2 | 93 | 110.7 | 43.5 | 15.2 | 9804.4 | 8580.9 | 10000 | 19474.3 | 16413.8 | 19040.4 | 1.986 | 1.913 | 1.904 | 0.6 | 0.543 | 0.609 | 4.01 | 2.55 | -3.83 | 0.54 | 0.563 | 0.574 | 2.91 | 3.4 | 3.13 | 0.569 | 0.58 | 0.611 | -3.31 | -2.76 | 3.03 | 0.563 | 0.6 | 0.583 | 3.9 | 2.32 | 2.6 | Critical_Thermal | 8580.9 | 16413.8 | 1.904 | 0.609 | 4.01 | 0.611 | 3.9 | 0.664 | 0.3317 | 0.1922 | 0.8882 | 1 | 0.7115 | 0.6963 | 0.6544 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1565 | 367.8 | 260.1 | 77.3 | 71.8 | 2.6 | 455.6 | 3674.1 | 41.2 | 40 | 78.2 | 80.5 | 72.2 | 82.4 | 36.3 | 14.7 | 7301.6 | 6873.2 | 7123.3 | 12487 | 11606.7 | 11944.6 | 1.71 | 1.689 | 1.677 | 0.638 | 0.593 | 0.63 | 4.15 | 4.06 | 4.5 | 0.558 | 0.602 | 0.53 | 3.51 | 2.85 | -2.65 | 0.597 | 0.571 | 0.54 | 2.61 | 3.25 | 3.05 | 0.571 | 0.583 | 0.537 | 2.92 | -3.51 | -3.52 | Poor_Oil | 6873.2 | 11606.7 | 1.677 | 0.638 | 4.5 | 0.602 | 3.52 | 0.7996 | 0.6799 | 0.854 | 0.9014 | 1 | 0.6158 | 0.7149 | 0.7868 | 0.7868 | Fair | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1566 | 781.2 | 482 | 105.7 | 116.3 | 15.2 | 793.3 | 5063.1 | 55.4 | 21.6 | 80.8 | 78.6 | 76.5 | 87.4 | 37.1 | 10 | 8763.5 | 8903.8 | 9186.3 | 16434.6 | 17221 | 16778.5 | 1.875 | 1.934 | 1.826 | 0.538 | 0.513 | 0.52 | 2.63 | 2.22 | 2.06 | 0.524 | 0.561 | 0.564 | -2.05 | 2.22 | -2.1 | 0.515 | 0.515 | 0.55 | 2.03 | 2.33 | 2.42 | 0.528 | 0.558 | 0.5 | 2.81 | -2.49 | -2.62 | Fair_DGA | 8763.5 | 16434.6 | 1.826 | 0.538 | 2.63 | 0.564 | 2.81 | 0.4752 | 0.938 | 0.7844 | 1 | 1 | 0.8885 | 0.8287 | 0.7934 | 0.7934 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1567 | 1764.2 | 938.5 | 148.3 | 179.9 | 31.6 | 1328.2 | 8468.6 | 32.7 | 49.4 | 108.1 | 107.3 | 94.3 | 115.6 | 45.3 | 34.8 | 1427.1 | 1153.1 | 1038.2 | 1629.6 | 1261.6 | 1200 | 1.142 | 1.094 | 1.156 | 0.99 | 0.969 | 0.99 | 9.26 | -9.15 | 9.27 | 0.881 | 0.845 | 0.716 | -7.25 | -9.34 | 7.61 | 0.806 | 0.882 | 0.761 | 6.97 | 8.65 | 7.02 | 0.783 | 0.715 | 0.84 | 7.93 | 6.33 | -8.5 | Very Poor_Mixed | 1038.2 | 1200 | 1.094 | 0.99 | 9.27 | 0.882 | 9.34 | 0.0707 | 0.5888 | 0.1142 | 0.2118 | 1 | 0.0495 | 0.2417 | 0.3208 | 0.3208 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1568 | 262.9 | 120 | 67.2 | 62.5 | 2.8 | 350 | 3228.6 | 60 | 20 | 76.1 | 80.8 | 70.7 | 82.5 | 35.4 | 20.2 | 8181.1 | 9193.7 | 9074.5 | 15619.9 | 17020.7 | 17470.6 | 1.909 | 1.851 | 1.925 | 0.573 | 0.529 | 0.564 | -3.14 | 2.23 | 3.14 | 0.547 | 0.553 | 0.525 | 2.2 | -2.69 | 2.76 | 0.527 | 0.534 | 0.566 | 2 | 2 | -2.75 | 0.564 | 0.507 | 0.502 | 2.86 | 2.14 | 2.4 | Fair_Age | 8181.1 | 15619.9 | 1.851 | 0.573 | 3.14 | 0.566 | 2.86 | 0.8665 | 1 | 0.8927 | 0.7404 | 1 | 0.7927 | 0.8196 | 0.8814 | 0.8814 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1569 | 379.6 | 274.8 | 83.3 | 74.2 | 3.6 | 544.2 | 4250 | 52.4 | 28.1 | 83.2 | 81.6 | 77.9 | 88.3 | 37.2 | 14.5 | 7986 | 7203.7 | 7349.8 | 14473 | 12109.7 | 12626.7 | 1.812 | 1.681 | 1.718 | 0.689 | 1.159 | 0.61 | -4.67 | 4 | 4.27 | 0.652 | 0.5 | 0.59 | 4 | -3.14 | 3.5 | 0.555 | 0.978 | 0.627 | -3.54 | 9.59 | 3.91 | 0.55 | 0.614 | 0.518 | 3.53 | 4.81 | 3.63 | Critical_Bushing_TD_Cap | 7203.7 | 12109.7 | 1.681 | 1.159 | 4.67 | 0.978 | 9.59 | 0.7515 | 0.8221 | 0.724 | 0.9067 | 1 | 0.4883 | 0.6139 | 0.7431 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
1570 | 948.4 | 507.6 | 102.9 | 121.8 | 20.7 | 736.7 | 5385.5 | 44.1 | 34.5 | 91.4 | 92.7 | 83.2 | 100.1 | 41.9 | 24.2 | 4624.1 | 4778.5 | 5062.3 | 6823.6 | 6421.5 | 7697.5 | 1.476 | 1.344 | 1.521 | 0.811 | 0.692 | 0.739 | 6.5 | -5.64 | 5.36 | 0.726 | 0.753 | 0.713 | 5.55 | -4.66 | 4.94 | 0.697 | 0.679 | 0.819 | 5.75 | 6.26 | 7.12 | 0.716 | 0.72 | 0.611 | 6.71 | 3.62 | -4.84 | Poor_Mixed | 4624.1 | 6421.5 | 1.344 | 0.811 | 6.5 | 0.819 | 7.12 | 0.4255 | 0.7403 | 0.4649 | 0.6074 | 1 | 0.4023 | 0.4101 | 0.5622 | 0.5622 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1571 | 1597.6 | 880.5 | 139.8 | 187.4 | 27 | 1278.4 | 8339.5 | 35.8 | 44.6 | 107.6 | 105.6 | 93.6 | 115 | 44.5 | 32.3 | 2761.8 | 2258.1 | 2170.4 | 3205.1 | 2601 | 2470.4 | 1.161 | 1.152 | 1.138 | 0.91 | 0.902 | 0.919 | 8.75 | 8.36 | 7.9 | 0.819 | 0.8 | 0.699 | 8.72 | 8.32 | 6.38 | 0.739 | 0.867 | 0.843 | 6.44 | -8.33 | -9.04 | 0.754 | 0.879 | 0.854 | 8.25 | 6.56 | 6.36 | Very Poor_Mixed | 2170.4 | 2470.4 | 1.138 | 0.919 | 8.75 | 0.879 | 9.04 | 0.1181 | 0.6338 | 0.1391 | 0.3098 | 1 | 0.1434 | 0.2435 | 0.3589 | 0.3589 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1572 | 875.9 | 497.7 | 106.5 | 114.6 | 15.7 | 783.9 | 5614.1 | 45.3 | 35.1 | 92.4 | 92.4 | 82.6 | 99.4 | 41.6 | 23.2 | 5727.8 | 7388.9 | 5861 | 8771.7 | 12416.8 | 9236.4 | 1.531 | 1.68 | 1.576 | 0.691 | 0.731 | 0.693 | 6.15 | -5.14 | 5.26 | 0.611 | 0.726 | 0.673 | 5.63 | -4.84 | -5.03 | 0.653 | 0.705 | 0.66 | 5.08 | 4.61 | 3.42 | 0.689 | 0.701 | 0.658 | 3.68 | -5.6 | -4.74 | Poor_Mixed | 5727.8 | 8771.7 | 1.531 | 0.731 | 6.15 | 0.726 | 5.63 | 0.4591 | 0.7333 | 0.4697 | 0.6416 | 1 | 0.4559 | 0.4823 | 0.5925 | 0.5925 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1573 | 315.7 | 187.3 | 78.8 | 70.1 | 1 | 557.4 | 3443.2 | 55.2 | 24.7 | 83.2 | 78.9 | 74.5 | 86.3 | 36.5 | 11.1 | 3332.8 | 3706.2 | 3292.9 | 4036.9 | 4850.2 | 4401.5 | 1.211 | 1.309 | 1.337 | 0.624 | 0.618 | 0.601 | -4.13 | 3.5 | 3.4 | 0.516 | 0.564 | 0.56 | 2.83 | 2.67 | 3.04 | 0.564 | 0.553 | 0.575 | 2.47 | 2.6 | 3.33 | 0.573 | 0.531 | 0.538 | -2 | 2.93 | 3.31 | Poor_IR_PI | 3292.9 | 4036.9 | 1.211 | 0.624 | 4.13 | 0.575 | 3.33 | 0.8811 | 0.8751 | 0.7859 | 0.984 | 1 | 0.6564 | 0.7552 | 0.8409 | 0.8409 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1574 | 190.2 | 120 | 65.3 | 55.3 | 1.4 | 350 | 2685.7 | 58.6 | 20 | 75.7 | 75 | 72.2 | 80 | 35 | 14.7 | 9139.4 | 9766.8 | 8264.4 | 17281.4 | 19533.6 | 15195.2 | 1.891 | 2 | 1.839 | 0.533 | 0.542 | 0.56 | 2.01 | -2.47 | 2 | 0.527 | 0.527 | 0.522 | 2.31 | 2.36 | 3.21 | 0.5 | 0.509 | 0.543 | -2.11 | -3.49 | -2.82 | 0.513 | 0.505 | 0.536 | -2.95 | 2 | 2.93 | Good_Mixed | 8264.4 | 15195.2 | 1.839 | 0.56 | 2.47 | 0.543 | 3.49 | 0.9314 | 1 | 0.962 | 0.9014 | 1 | 0.8602 | 0.8514 | 0.9278 | 0.9278 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1575 | 1570.9 | 853.1 | 132.2 | 180.9 | 31 | 1200.2 | 7871.8 | 35.7 | 46.8 | 101.3 | 104 | 90.5 | 111.4 | 44.4 | 32.7 | 2271 | 1511.3 | 2180.5 | 2648.7 | 1675.8 | 2679.9 | 1.166 | 1.109 | 1.229 | 0.892 | 0.984 | 0.981 | 8.6 | 9.21 | 9.31 | 0.895 | 0.857 | 0.815 | 6.63 | 6.51 | 5.61 | 0.723 | 0.736 | 0.729 | 7.28 | 5.31 | 5.42 | 0.719 | 0.911 | 0.812 | 5.89 | 5 | 6.68 | Very Poor_Mixed | 1511.3 | 1675.8 | 1.109 | 0.984 | 9.31 | 0.911 | 7.28 | 0.1302 | 0.6128 | 0.2196 | 0.2943 | 1 | 0.0797 | 0.3024 | 0.3683 | 0.3683 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1576 | 1441.1 | 870.4 | 136.2 | 173.3 | 28.9 | 1215.5 | 7971.8 | 32.5 | 41.4 | 101.7 | 103.1 | 89.2 | 112.9 | 43.4 | 31.5 | 1854.4 | 1713.2 | 2328.8 | 2286.4 | 1807.9 | 2879.9 | 1.233 | 1.055 | 1.237 | 0.915 | 0.938 | 0.944 | 8.28 | 9.01 | 8.63 | 0.829 | 0.745 | 0.69 | 6.67 | -8.16 | 8.27 | 0.766 | 0.802 | 0.917 | 9.5 | 5.69 | -5.41 | 0.738 | 0.7 | 0.865 | 5.7 | -8.15 | 6.5 | Very Poor_Mixed | 1713.2 | 1807.9 | 1.055 | 0.944 | 9.01 | 0.917 | 9.5 | 0.1476 | 0.6655 | 0.2296 | 0.3406 | 1 | 0.1129 | 0.283 | 0.3835 | 0.3835 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1577 | 1523.2 | 894.6 | 137.4 | 175.4 | 32.6 | 1209.9 | 8527.5 | 32.1 | 47.9 | 105.3 | 103.7 | 92.2 | 116.4 | 44 | 32.5 | 1136 | 919.4 | 2090.9 | 1232.7 | 1200 | 2402.5 | 1.085 | 1.305 | 1.149 | 0.938 | 0.894 | 0.92 | 8.87 | 8.11 | 8.54 | 0.915 | 0.962 | 0.767 | 7.97 | 8.47 | -7.73 | 0.866 | 0.775 | 0.727 | 6.89 | 6.57 | 5.61 | 0.898 | 0.848 | 0.715 | 5.36 | 8.78 | 7.6 | Very Poor_Mixed | 919.4 | 1200 | 1.085 | 0.938 | 8.87 | 0.962 | 8.78 | 0.1128 | 0.6025 | 0.1668 | 0.302 | 1 | 0.13 | 0.2348 | 0.3527 | 0.3527 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1578 | 1597.1 | 904.4 | 136.7 | 183.9 | 31.8 | 1317.5 | 8451.9 | 36.2 | 42.1 | 104.2 | 107 | 91.5 | 112.6 | 44.5 | 29.1 | 2835.3 | 2797.8 | 2165.1 | 3179.2 | 3530.1 | 2300.7 | 1.121 | 1.262 | 1.063 | 0.923 | 0.918 | 0.941 | 7.73 | -8.89 | 8.97 | 0.709 | 0.84 | 0.735 | 6.89 | 7.77 | 6.76 | 0.751 | 0.876 | 0.824 | 7.55 | 8.53 | 5.99 | 0.767 | 0.829 | 0.971 | -6.51 | 7.22 | 5.71 | Very Poor_Mixed | 2165.1 | 2300.7 | 1.063 | 0.941 | 8.97 | 0.971 | 8.53 | 0.0927 | 0.6584 | 0.174 | 0.4313 | 1 | 0.122 | 0.2592 | 0.3649 | 0.3649 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1579 | 714.8 | 324.1 | 89.1 | 89.5 | 1.8 | 702.9 | 4459.7 | 57.9 | 26 | 82.9 | 82.5 | 78.2 | 90.9 | 37.1 | 14 | 6302 | 7531.1 | 7837.7 | 10414.4 | 12604.1 | 13890.5 | 1.653 | 1.674 | 1.772 | 0.622 | 0.612 | 0.653 | 3.92 | 3.83 | 3.89 | 0.665 | 0.676 | 0.602 | 3.22 | 3.22 | 10.13 | 0.588 | 0.606 | 0.59 | -4.16 | 3.27 | 3.73 | 0.511 | 0.97 | 0.558 | -2.78 | -9.45 | 3.56 | Critical_Bushing_TD_Cap | 6302 | 10414.4 | 1.653 | 0.653 | 3.92 | 0.97 | 10.13 | 0.7124 | 0.8536 | 0.7046 | 0.9194 | 1 | 0.6273 | 0.5567 | 0.745 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
1580 | 784 | 471.1 | 94.7 | 115.5 | 18.8 | 858.3 | 5017.8 | 47.2 | 32.4 | 89.1 | 89.3 | 79.9 | 95.6 | 40 | 23.7 | 6727.7 | 5398.1 | 5902.4 | 11074.9 | 8245.2 | 9470.7 | 1.646 | 1.527 | 1.605 | 0.713 | 0.696 | 0.678 | 4.73 | 4.97 | 4.56 | 0.697 | 0.681 | 0.75 | -3.97 | 5.76 | 4.6 | 0.737 | 0.736 | 0.765 | 3.99 | -4.69 | 4.62 | 0.741 | 0.752 | 0.798 | -4.31 | 4.1 | 5.2 | Poor_Mixed | 5398.1 | 8245.2 | 1.527 | 0.713 | 4.97 | 0.798 | 5.76 | 0.454 | 0.7654 | 0.5587 | 0.6246 | 1 | 0.5076 | 0.413 | 0.5978 | 0.5978 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1581 | 870 | 530.5 | 102.2 | 121.7 | 19.2 | 826.5 | 5769.5 | 44.1 | 33.3 | 87.8 | 92.6 | 81.7 | 96.8 | 39.6 | 25.4 | 5897.3 | 5482.3 | 6098.9 | 9312.7 | 8210 | 9544.9 | 1.579 | 1.498 | 1.565 | 0.693 | 0.716 | 0.719 | 6.21 | 5.33 | 5.61 | 0.7 | 0.772 | 0.657 | 4.25 | 5.97 | 5.02 | 0.675 | 0.739 | 0.737 | 4.67 | -6.25 | 6.08 | 0.638 | 0.705 | 0.618 | 5.53 | 5.28 | 5.9 | Poor_Mixed | 5482.3 | 8210 | 1.498 | 0.719 | 6.21 | 0.772 | 6.25 | 0.4229 | 0.7544 | 0.5308 | 0.5655 | 1 | 0.4406 | 0.4358 | 0.5777 | 0.5777 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1582 | 888.1 | 478 | 95.6 | 110.4 | 14.8 | 871.7 | 5503.3 | 46.6 | 35.5 | 90.3 | 85.6 | 79.6 | 97.7 | 40.2 | 25 | 6020.4 | 5656.5 | 5038.8 | 9479 | 9097.9 | 7822.3 | 1.574 | 1.608 | 1.552 | 0.641 | 0.692 | 0.712 | 4.86 | -4.93 | 4.8 | 0.649 | 0.647 | 0.619 | -4.87 | 3.64 | 4.39 | 0.672 | 0.617 | 0.601 | 4.18 | 6.41 | 5.07 | 0.755 | 0.651 | 0.677 | 5.41 | -3.86 | -4.71 | Poor_Mixed | 5038.8 | 7822.3 | 1.552 | 0.712 | 4.93 | 0.755 | 6.41 | 0.4687 | 0.7287 | 0.5666 | 0.5796 | 1 | 0.5153 | 0.5107 | 0.6143 | 0.6143 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1583 | 100 | 136.4 | 69.8 | 50 | 1.9 | 371 | 2500 | 59.5 | 20 | 75.6 | 76.5 | 70.9 | 80 | 35 | 10.1 | 10000 | 9940.6 | 9661.5 | 19708.3 | 19639.1 | 18603 | 1.971 | 1.976 | 1.925 | 0.5 | 0.552 | 0.501 | 2.19 | 2.23 | -2.76 | 0.527 | 0.5 | 0.559 | 2.1 | 2.18 | -2.22 | 0.503 | 0.5 | 0.5 | 2.47 | 2 | 2.23 | 0.5 | 0.517 | 0.5 | 2 | 2.14 | 2.41 | Good_Mixed | 9661.5 | 18603 | 1.925 | 0.552 | 2.76 | 0.559 | 2.47 | 0.927 | 1 | 0.9525 | 0.9992 | 1 | 0.9148 | 0.9293 | 0.9523 | 0.9523 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1584 | 964.7 | 530.1 | 97.9 | 121.2 | 15.9 | 862 | 5220.6 | 45.5 | 33.4 | 88.2 | 88.9 | 79.6 | 95.1 | 40 | 22.5 | 5948 | 5966.2 | 5496.5 | 8838.6 | 9401.4 | 9093.6 | 1.486 | 1.576 | 1.654 | 0.66 | 0.682 | 0.739 | -5.62 | 5.49 | 5.79 | 0.648 | 0.709 | 0.666 | 4.2 | 5.38 | -4.36 | 0.692 | 0.741 | 0.717 | 4.74 | 5.37 | 5.76 | 0.703 | 0.681 | 0.678 | 4.03 | -4.7 | 5.86 | Poor_Mixed | 5496.5 | 8838.6 | 1.486 | 0.739 | 5.79 | 0.741 | 5.86 | 0.4412 | 0.7532 | 0.572 | 0.6652 | 1 | 0.4605 | 0.4526 | 0.5971 | 0.5971 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1585 | 318.2 | 130.9 | 71.7 | 70.9 | 2.6 | 435.8 | 2500 | 59.9 | 20.5 | 77 | 77 | 70 | 80 | 35.1 | 13.5 | 9292.5 | 9167.2 | 10000 | 18440.9 | 17270.9 | 20000 | 1.984 | 1.884 | 2 | 0.5 | 0.502 | 0.546 | -2 | 2.15 | -2.58 | 0.5 | 0.547 | 0.507 | 2.65 | 2.18 | -2.5 | 0.517 | 0.5 | 0.528 | -2.72 | 2.04 | 2.69 | 0.538 | 0.5 | 0.517 | 2 | 2.24 | -2.3 | Good_Mixed | 9167.2 | 17270.9 | 1.884 | 0.546 | 2.58 | 0.547 | 2.72 | 0.8345 | 0.9709 | 0.9413 | 0.9318 | 1 | 0.9289 | 0.8882 | 0.9158 | 0.9158 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1586 | 353.1 | 260.7 | 81.5 | 77.6 | 5.3 | 494.5 | 3449.3 | 56.1 | 23 | 76.5 | 76.3 | 72.1 | 81.1 | 35.9 | 14.5 | 8127.9 | 9627.5 | 8028.1 | 14614.9 | 17727.4 | 14274.7 | 1.798 | 1.841 | 1.778 | 0.816 | 0.798 | 0.793 | 7.19 | 6.64 | 6.94 | 0.513 | 0.549 | 0.552 | 4.03 | -2.44 | -2.76 | 0.555 | 0.529 | 0.513 | 2.43 | 2.36 | 2.7 | 0.555 | 0.533 | 0.555 | 3.37 | 2.47 | -2 | Poor_Winding_TD_Cap | 8028.1 | 14274.7 | 1.778 | 0.816 | 7.19 | 0.555 | 4.03 | 0.7409 | 0.9067 | 0.9226 | 0.9067 | 1 | 0.2966 | 0.7902 | 0.7754 | 0.7754 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1587 | 879.5 | 435.3 | 100.9 | 111.6 | 14.5 | 891.6 | 5237.4 | 44.9 | 34 | 90.2 | 89.8 | 82 | 95.7 | 40 | 24.1 | 6507.2 | 5209.4 | 6098.7 | 10512.2 | 8335.9 | 9899.9 | 1.615 | 1.6 | 1.623 | 0.781 | 0.76 | 0.765 | 6.61 | 5.46 | 6.4 | 0.673 | 0.617 | 0.632 | -5.44 | 4.66 | 3.28 | 0.612 | 0.675 | 0.606 | 4.92 | -4.3 | 5.09 | 0.711 | 0.631 | 0.634 | 4.37 | 4.95 | 4.94 | Poor_Mixed | 5209.4 | 8335.9 | 1.6 | 0.781 | 6.61 | 0.711 | 5.44 | 0.4716 | 0.7461 | 0.5338 | 0.6108 | 1 | 0.3651 | 0.5262 | 0.5972 | 0.5972 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1588 | 896 | 539.2 | 103.3 | 122.7 | 19.7 | 828.8 | 5381.4 | 46.4 | 33 | 89.6 | 91.3 | 82.8 | 97.4 | 40.2 | 26.7 | 6541.2 | 6347.7 | 6369.2 | 10989.7 | 9948.5 | 10165 | 1.68 | 1.567 | 1.596 | 0.673 | 0.672 | 0.716 | 5.72 | 5.5 | -5.85 | 0.594 | 0.696 | 0.62 | 3.42 | -4.93 | -4.14 | 0.726 | 0.664 | 0.665 | -3.84 | 4.7 | 4.77 | 0.746 | 0.66 | 0.651 | 4.28 | 5.54 | 5.38 | Poor_Mixed | 6347.7 | 9948.5 | 1.567 | 0.716 | 5.85 | 0.746 | 5.54 | 0.419 | 0.7581 | 0.5131 | 0.5192 | 1 | 0.463 | 0.4982 | 0.5875 | 0.5875 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1589 | 1560.5 | 891.1 | 132.1 | 178.4 | 34.1 | 1183 | 8053.4 | 33.9 | 44.2 | 100.9 | 100.2 | 90.2 | 109.2 | 43.1 | 29.3 | 3362.2 | 1719.3 | 2485.4 | 3927 | 1910.7 | 3195.8 | 1.168 | 1.111 | 1.286 | 0.94 | 0.931 | 0.941 | 8.89 | 9.56 | -8.92 | 0.797 | 0.86 | 0.902 | -7.67 | 6.8 | 5 | 0.778 | 0.789 | 0.757 | 5.1 | -7.69 | 7.3 | 0.656 | 0.759 | 0.889 | 6.08 | -6.62 | -6.18 | Very Poor_Mixed | 1719.3 | 1910.7 | 1.111 | 0.941 | 9.56 | 0.902 | 7.69 | 0.1148 | 0.6376 | 0.2656 | 0.4238 | 1 | 0.085 | 0.2886 | 0.3768 | 0.3768 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1590 | 245.7 | 159 | 71.9 | 66.9 | 2 | 547.1 | 2659.6 | 57.2 | 24.8 | 81.4 | 82.3 | 73.5 | 87.1 | 36.7 | 13.4 | 7058.4 | 8156.4 | 8741 | 12089.8 | 14904.4 | 15863 | 1.713 | 1.827 | 1.815 | 0.985 | 0.982 | 0.944 | 9.47 | 9.37 | 9.15 | 0.6 | 0.654 | 0.639 | 3.23 | 4.02 | 4.82 | 0.594 | 0.633 | 0.616 | 2.75 | -3.92 | -13.56 | 0.529 | 0.555 | 0.612 | 3.78 | 4.38 | 4.12 | Critical_Winding_TD_Cap | 7058.4 | 12089.8 | 1.713 | 0.985 | 9.47 | 0.654 | 13.56 | 0.8404 | 0.8734 | 0.7742 | 0.9342 | 1 | 0.0527 | 0.5957 | 0.7136 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Winding_HV_TanDelta_pct
1591 | 476.7 | 332.5 | 85.6 | 98 | 11.2 | 646.6 | 4455.3 | 52.5 | 27.1 | 83.2 | 86.3 | 80.4 | 88.6 | 37.9 | 16.1 | 7250.9 | 7598.3 | 7472.9 | 12330.6 | 13437.8 | 13533.7 | 1.701 | 1.769 | 1.811 | 0.623 | 0.615 | 0.593 | -4.52 | 4.21 | 4.1 | 0.588 | 0.56 | 0.548 | 3.33 | 3.23 | 3.14 | 0.586 | 0.535 | 0.598 | 3.14 | 3.33 | 3.36 | 0.595 | 0.589 | 0.596 | 3.11 | 3.23 | -3.94 | Fair_Mixed | 7250.9 | 12330.6 | 1.701 | 0.623 | 4.52 | 0.598 | 3.94 | 0.6053 | 0.8367 | 0.6661 | 0.8635 | 1 | 0.6245 | 0.682 | 0.7317 | 0.7317 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1592 | 978.3 | 578.2 | 109.8 | 120.9 | 21 | 902.1 | 5277.6 | 47.4 | 31.9 | 90.6 | 87.5 | 81.4 | 98.2 | 40.6 | 27.5 | 6120.9 | 4638.3 | 3996.2 | 9235.6 | 6356.3 | 5617.7 | 1.509 | 1.37 | 1.406 | 0.729 | 0.717 | 0.735 | -4.86 | -5.37 | 6.05 | 0.724 | 0.652 | 0.678 | 5.17 | 5.97 | 5.76 | 0.737 | 0.679 | 0.672 | 5.32 | -5.71 | 5.62 | 0.659 | 0.728 | 0.763 | -4.03 | 5.16 | 5.85 | Poor_Mixed | 3996.2 | 5617.7 | 1.37 | 0.735 | 6.05 | 0.763 | 5.97 | 0.3897 | 0.7716 | 0.5342 | 0.4902 | 1 | 0.4409 | 0.429 | 0.5669 | 0.5669 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1593 | 639.9 | 422.4 | 86.4 | 94.2 | 12.5 | 589.3 | 4287.8 | 51.3 | 30.1 | 85.9 | 85 | 81.3 | 91.6 | 38.5 | 18.4 | 6013.5 | 7032.8 | 6559.8 | 9619 | 12611.3 | 11281.5 | 1.6 | 1.793 | 1.72 | 0.631 | 0.615 | 0.617 | 4.08 | 4.45 | -4.14 | 0.638 | 0.679 | 0.659 | 3.19 | 4.16 | 4.03 | 0.678 | 0.596 | 0.603 | 4.31 | 3.09 | 3.38 | 0.665 | 0.699 | 0.592 | 2.65 | 4.13 | 4.93 | Fair_Mixed | 6013.5 | 9619 | 1.6 | 0.631 | 4.45 | 0.699 | 4.93 | 0.5838 | 0.7947 | 0.6311 | 0.7963 | 1 | 0.6151 | 0.5599 | 0.6911 | 0.6911 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1594 | 366 | 219 | 69.3 | 63.6 | 4.5 | 452.5 | 2500 | 58 | 20.5 | 75.1 | 77.9 | 71.2 | 80 | 35.1 | 14.5 | 9537.3 | 9819 | 9305.5 | 18525.7 | 18810.8 | 18610.9 | 1.942 | 1.916 | 2 | 0.546 | 0.507 | 0.5 | 2.21 | -2.26 | 2 | 0.59 | 0.519 | 0.5 | -2.76 | 2.46 | 2.07 | 0.534 | 0.519 | 0.506 | -2.21 | 2.54 | 2.43 | 0.535 | 0.54 | 0.564 | 2.44 | -2.51 | 2.94 | Good_Mixed | 9305.5 | 18525.7 | 1.916 | 0.546 | 2.26 | 0.59 | 2.94 | 0.7933 | 0.9709 | 0.9428 | 0.9067 | 1 | 0.9281 | 0.8258 | 0.893 | 0.893 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1595 | 336.2 | 306.3 | 80.8 | 89.3 | 1 | 473.2 | 3823.6 | 55.7 | 24.1 | 89.7 | 91.1 | 80.6 | 97.9 | 39.5 | 11.9 | 8940.9 | 8240 | 9727.8 | 17828.4 | 15582.5 | 18955.4 | 1.994 | 1.891 | 1.949 | 0.529 | 0.54 | 0.565 | -2.95 | 2.85 | 2.61 | 0.51 | 0.557 | 0.5 | -2 | 2.11 | 2.64 | 0.506 | 0.5 | 0.513 | 2.49 | 2 | 2.06 | 0.538 | 0.525 | 0.505 | 2 | 2.57 | 2.66 | Poor_Thermal | 8240 | 15582.5 | 1.891 | 0.565 | 2.95 | 0.557 | 2.66 | 0.8508 | 0.8857 | 0.5298 | 0.9682 | 1 | 0.8102 | 0.8918 | 0.8543 | 0.8543 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1596 | 1630.6 | 840 | 136.3 | 175.2 | 27.8 | 1235.5 | 8363.2 | 60 | 22.6 | 116.2 | 78.3 | 74.4 | 84.5 | 35.9 | 12.4 | 8316.8 | 8555.7 | 8065.6 | 15337.4 | 15487.7 | 14325.1 | 1.844 | 1.81 | 1.776 | 0.608 | 0.543 | 0.585 | 3.71 | 2.01 | 3.24 | 0.588 | 0.549 | 0.546 | 2.05 | -2.36 | -2.66 | 0.515 | 0.531 | 0.586 | 2.21 | 2.03 | 2.8 | 0.53 | 0.529 | 0.533 | 2.43 | 2.18 | 2.73 | Critical_DGA | 8065.6 | 14325.1 | 1.776 | 0.608 | 3.71 | 0.588 | 2.8 | 0.1335 | 0.915 | 0.6385 | 0.9575 | 1 | 0.7522 | 0.7944 | 0.6632 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature | C2H2
1597 | 1003 | 629.3 | 110.7 | 140.1 | 22.9 | 912.9 | 5784.6 | 57.5 | 23 | 75.4 | 76.7 | 71.8 | 84.7 | 35.2 | 11.5 | 9832.1 | 10000 | 8611.9 | 18643.9 | 19666.3 | 16590.9 | 1.896 | 1.967 | 1.927 | 0.521 | 0.507 | 0.5 | 2 | 2.23 | 2 | 0.524 | 0.55 | 0.522 | 2.64 | -2 | -2.67 | 0.551 | 0.5 | 0.519 | 2.4 | 2 | 2 | 0.582 | 0.534 | 0.5 | 2.85 | 2.9 | 2.72 | Poor_DGA | 8611.9 | 16590.9 | 1.896 | 0.521 | 2.23 | 0.582 | 2.9 | 0.3464 | 0.9067 | 0.9203 | 0.9764 | 1 | 0.952 | 0.8397 | 0.7807 | 0.7807 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1598 | 808.3 | 506.3 | 101.6 | 112.6 | 15.7 | 908.7 | 5631.7 | 44.9 | 32.8 | 89.6 | 90.6 | 81.6 | 95.5 | 39 | 24.9 | 5243.7 | 5794 | 6095.5 | 8488.4 | 8961.5 | 10027 | 1.619 | 1.547 | 1.645 | 0.775 | 0.699 | 0.707 | 6.58 | 5.8 | 5.58 | 0.701 | 0.733 | 0.674 | -3.54 | 4.85 | 4.21 | 0.625 | 0.698 | 0.66 | 4.67 | 4.13 | 4.58 | 0.679 | 0.616 | 0.655 | -3.99 | -5.83 | 4.46 | Poor_Mixed | 5243.7 | 8488.4 | 1.547 | 0.775 | 6.58 | 0.733 | 5.83 | 0.4534 | 0.7605 | 0.5424 | 0.5831 | 1 | 0.4107 | 0.4971 | 0.5949 | 0.5949 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1599 | 135.8 | 173.8 | 76.5 | 60.8 | 3.5 | 380.2 | 2714.4 | 57.2 | 25.2 | 79.4 | 81.6 | 74.5 | 85.7 | 35.5 | 12.9 | 9348 | 8988.1 | 7774.5 | 18416.2 | 17025.8 | 13518.2 | 1.97 | 1.894 | 1.739 | 0.558 | 0.548 | 0.549 | 2.7 | 2.3 | 3.14 | 0.557 | 0.594 | 0.504 | -2.68 | 2.04 | 2.64 | 0.558 | 0.687 | 0.618 | 2.92 | 4.85 | 3 | 0.526 | 0.542 | 0.558 | 2.01 | 3.24 | -2.24 | Fair_Bushing_TD_Cap | 7774.5 | 13518.2 | 1.739 | 0.558 | 3.14 | 0.687 | 4.85 | 0.8517 | 0.8666 | 0.8016 | 0.9461 | 1 | 0.8043 | 0.7307 | 0.8485 | 0.8485 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1600 | 775.3 | 427.2 | 96 | 104.2 | 15.7 | 653.8 | 5299 | 53.8 | 26.2 | 80 | 78.9 | 72.9 | 84.1 | 35.6 | 14.6 | 8407.5 | 8685.2 | 9458.4 | 15895.8 | 15472.3 | 18121.8 | 1.891 | 1.781 | 1.916 | 0.518 | 0.538 | 0.565 | -3.02 | 2.47 | 3.33 | 0.591 | 0.57 | 0.577 | -3.26 | 3.29 | 3.82 | 0.525 | 0.564 | 0.563 | -2.82 | 2.83 | 3.32 | 0.56 | 0.566 | 0.548 | -2.68 | 2.72 | -2.95 | Fair_DGA | 8407.5 | 15472.3 | 1.781 | 0.565 | 3.33 | 0.591 | 3.82 | 0.5135 | 0.8505 | 0.8402 | 0.904 | 1 | 0.8107 | 0.7194 | 0.7626 | 0.7626 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1601 | 817.2 | 515.1 | 108.7 | 112.1 | 18.2 | 784.1 | 5077.4 | 47.9 | 33.5 | 93.1 | 90.3 | 80.8 | 98 | 39.2 | 23.4 | 5081 | 4801 | 5786.4 | 7855.6 | 6755.7 | 8975.5 | 1.546 | 1.407 | 1.551 | 0.706 | 0.729 | 0.72 | 5.83 | 5.91 | 5.9 | 0.619 | 0.574 | 0.642 | 4.77 | 4.46 | -3.72 | 0.595 | 0.66 | 0.702 | 5.16 | 4.43 | 5.03 | 0.721 | 0.637 | 0.721 | 5.45 | -3.67 | 5.32 | Poor_Mixed | 4801 | 6755.7 | 1.407 | 0.729 | 5.91 | 0.721 | 5.45 | 0.4521 | 0.752 | 0.5131 | 0.6348 | 1 | 0.4232 | 0.5171 | 0.5986 | 0.5986 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1602 | 460.9 | 198.7 | 77.4 | 84.9 | 3.3 | 498.1 | 2914 | 56.4 | 22.6 | 75 | 75 | 70 | 81.8 | 35.8 | 10.5 | 8763.7 | 10000 | 10000 | 16719.5 | 19211.1 | 19420.1 | 1.908 | 1.921 | 1.942 | 0.536 | 0.565 | 0.5 | -2 | 2.79 | 2.24 | 0.517 | 0.529 | 0.518 | -3.38 | 2 | 2.81 | 0.512 | 0.571 | 0.643 | 2 | 3.79 | 4.6 | 0.553 | 0.5 | 0.51 | 3.03 | 2.41 | 2.66 | Fair_Bushing_TD_Cap | 8763.7 | 16719.5 | 1.908 | 0.565 | 2.79 | 0.643 | 4.6 | 0.7662 | 0.915 | 0.988 | 0.994 | 1 | 0.8812 | 0.8006 | 0.8773 | 0.8773 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1603 | 812 | 489 | 106.6 | 108.1 | 17.5 | 835.9 | 5026.9 | 49.4 | 31 | 93.4 | 92 | 81.7 | 97.6 | 39.8 | 24 | 5227.9 | 6474.2 | 6119.4 | 8191 | 10631.8 | 9309.8 | 1.567 | 1.642 | 1.521 | 0.725 | 0.752 | 0.694 | 4.99 | 5.87 | 5.27 | 0.646 | 0.727 | 0.694 | -4.59 | 5.57 | 4.95 | 0.669 | 0.676 | 0.765 | -4.18 | 4.28 | -4.61 | 0.656 | 0.709 | 0.675 | 4.73 | -4.13 | 4.6 | Poor_Mixed | 5227.9 | 8191 | 1.521 | 0.752 | 5.87 | 0.765 | 5.57 | 0.4593 | 0.7829 | 0.4926 | 0.6143 | 1 | 0.447 | 0.4668 | 0.5954 | 0.5954 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1604 | 255.1 | 221.1 | 73.7 | 113.7 | 1.3 | 511.3 | 3846 | 56.9 | 26 | 97.2 | 98.2 | 85.8 | 104.1 | 42.2 | 14.9 | 9308.5 | 8472 | 9321.8 | 16989 | 15746.2 | 17960 | 1.825 | 1.859 | 1.927 | 0.586 | 0.525 | 0.519 | 3.32 | 2.02 | 2.36 | 0.564 | 0.611 | 0.576 | -2.5 | 2.53 | 3.35 | 0.606 | 0.521 | 0.588 | -2.7 | 3.07 | 2.26 | 0.561 | 0.564 | 0.612 | 2.1 | -2.77 | 2.43 | Poor_Thermal | 8472 | 15746.2 | 1.825 | 0.586 | 3.32 | 0.612 | 3.35 | 0.8031 | 0.8536 | 0.357 | 0.8962 | 1 | 0.8377 | 0.7146 | 0.7896 | 0.7896 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H4
1605 | 153.7 | 120 | 66.6 | 51.8 | 1.2 | 350 | 2628.3 | 60 | 20 | 76.4 | 76.4 | 73 | 81.3 | 36.3 | 11.2 | 8467.4 | 8704 | 7381.1 | 15570.6 | 15758.1 | 13104.7 | 1.839 | 1.81 | 1.775 | 0.573 | 0.553 | 0.567 | 3.04 | 2.69 | 3.09 | 0.513 | 0.5 | 0.525 | 2.1 | 2 | 2.85 | 0.516 | 0.5 | 0.532 | 2.91 | 2.65 | 2 | 0.537 | 0.5 | 0.5 | 2 | 2 | 2.03 | Fair_IR_PI | 7381.1 | 13104.7 | 1.775 | 0.573 | 3.09 | 0.537 | 2.91 | 0.9541 | 1 | 0.9118 | 0.9821 | 1 | 0.7688 | 0.9099 | 0.9302 | 0.9302 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1606 | 818.8 | 536.1 | 100 | 115.1 | 19.2 | 864.9 | 4832.1 | 47.5 | 30.6 | 91 | 92.6 | 80.9 | 97.7 | 41.2 | 24.4 | 5489.7 | 5977.5 | 7195 | 8414.6 | 10112.6 | 12218.6 | 1.533 | 1.692 | 1.698 | 0.769 | 0.734 | 0.708 | 6.59 | 5.74 | 5.78 | 0.66 | 0.697 | 0.707 | 4.91 | 4.87 | 4.81 | 0.647 | 0.646 | 0.65 | -5.5 | 3.42 | -5.44 | 0.604 | 0.602 | 0.639 | 5.67 | -4.57 | 5.8 | Poor_Mixed | 5489.7 | 8414.6 | 1.533 | 0.769 | 6.59 | 0.707 | 5.8 | 0.4391 | 0.7881 | 0.4996 | 0.6005 | 1 | 0.3987 | 0.5048 | 0.591 | 0.591 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1607 | 164.5 | 192.6 | 71.4 | 55.9 | 4.6 | 449.7 | 2738.8 | 58.4 | 21.7 | 75 | 76.3 | 70.2 | 80.7 | 35.5 | 13.9 | 9512.3 | 7575.7 | 9825.5 | 17733.4 | 13665.8 | 19165.2 | 1.864 | 1.804 | 1.951 | 0.514 | 0.503 | 0.558 | -2 | 2 | 2.94 | 0.5 | 0.55 | 0.546 | 2 | 2.43 | 2.53 | 0.5 | 0.5 | 0.522 | 2 | -2.24 | 2.9 | 0.546 | 0.544 | 0.512 | -2.03 | 2 | 2.24 | Good_Mixed | 7575.7 | 13665.8 | 1.804 | 0.558 | 2.94 | 0.55 | 2.9 | 0.8262 | 0.9355 | 0.97 | 0.9219 | 1 | 0.8967 | 0.8746 | 0.9049 | 0.9049 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1608 | 1263.2 | 886.1 | 132.7 | 180.8 | 27 | 1177.1 | 7764.5 | 35.1 | 45 | 103.4 | 108.1 | 93.4 | 114 | 43.6 | 32.2 | 1586.2 | 2153.2 | 1493.8 | 1779.8 | 2289.1 | 1568.5 | 1.122 | 1.063 | 1.05 | 0.899 | 0.942 | 0.911 | 8.44 | 9.47 | -8.54 | 0.766 | 0.751 | 0.835 | -7.13 | 5.91 | -6.38 | 0.924 | 0.766 | 0.665 | -7.93 | 7.21 | 6.35 | 0.735 | 0.764 | 0.755 | -7.29 | 8.65 | -5.91 | Very Poor_Mixed | 1493.8 | 1568.5 | 1.05 | 0.942 | 9.47 | 0.924 | 8.65 | 0.1715 | 0.6299 | 0.1613 | 0.3137 | 1 | 0.1143 | 0.2967 | 0.3797 | 0.3797 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1609 | 1766 | 982.4 | 148.3 | 193.3 | 40.9 | 1379 | 8330.6 | 53.3 | 25.8 | 80.6 | 82.1 | 77.1 | 85.1 | 37.2 | 19.8 | 6705.9 | 7920.7 | 6593.8 | 11064.2 | 13417.9 | 11374.9 | 1.65 | 1.694 | 1.725 | 0.636 | 0.516 | 0.564 | -4.43 | 2.78 | 3.01 | 0.573 | 0.555 | 0.598 | 3.37 | -4.16 | 2.35 | 0.57 | 0.559 | 0.526 | 2.99 | 3.4 | 3 | 0.547 | 0.574 | 0.507 | 3.51 | -3.54 | 3.28 | Critical_DGA | 6593.8 | 11064.2 | 1.65 | 0.636 | 4.43 | 0.598 | 4.16 | 0.0364 | 0.8568 | 0.7626 | 0.753 | 1 | 0.7393 | 0.7279 | 0.6203 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1610 | 1641.7 | 869.1 | 136.8 | 186 | 34.3 | 1326.6 | 8015.2 | 34.3 | 44.1 | 104.7 | 102.1 | 91.1 | 111.5 | 43.6 | 31.2 | 2115.9 | 2152.5 | 1263.4 | 2427.8 | 2508.3 | 1429.5 | 1.147 | 1.165 | 1.131 | 0.927 | 0.919 | 0.864 | -8.98 | 8.47 | 8.55 | 0.789 | 0.895 | 0.77 | 6.35 | -5.83 | 6.93 | 0.8 | 0.726 | 0.888 | 6.29 | -8.6 | -6.82 | 0.858 | 0.843 | 0.831 | -5.37 | 5.91 | -7.88 | Very Poor_Mixed | 1263.4 | 1429.5 | 1.131 | 0.927 | 8.98 | 0.895 | 8.6 | 0.0853 | 0.6386 | 0.2129 | 0.3521 | 1 | 0.1318 | 0.258 | 0.3617 | 0.3617 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1611 | 918.5 | 469.5 | 97.4 | 100.3 | 15.6 | 749.9 | 5394 | 46.4 | 33.8 | 91.3 | 89.6 | 81.9 | 97 | 40.1 | 25.6 | 5661 | 5441.2 | 4999.1 | 8689.8 | 8170.3 | 7707.4 | 1.535 | 1.502 | 1.542 | 0.689 | 0.721 | 0.705 | -4.89 | 5.55 | 5.82 | 0.711 | 0.72 | 0.77 | 5.28 | 4.16 | 4.81 | 0.679 | 0.718 | 0.717 | 5.57 | 5.86 | 4.82 | 0.722 | 0.709 | 0.725 | 4.58 | 5.16 | 5.04 | Poor_Mixed | 4999.1 | 7707.4 | 1.502 | 0.721 | 5.82 | 0.77 | 5.86 | 0.4874 | 0.7485 | 0.5214 | 0.5584 | 1 | 0.4611 | 0.4183 | 0.5916 | 0.5916 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1612 | 521.5 | 283.6 | 84.5 | 90.7 | 3 | 514.2 | 3768.4 | 30.6 | 49.1 | 78 | 75.8 | 123 | 80.8 | 36.8 | 14.4 | 5151.4 | 5644.7 | 4960.5 | 7667.9 | 8680.4 | 7254.6 | 1.489 | 1.538 | 1.462 | 0.685 | 0.645 | 0.712 | 4.49 | 4.55 | 4.67 | 0.597 | 0.613 | 0.579 | 4.2 | 3.9 | 3.42 | 0.591 | 0.577 | 0.641 | 4.25 | 3.63 | 4.18 | 0.539 | 0.602 | 0.58 | -3.51 | 2.86 | 3.66 | Critical_Oil | 4960.5 | 7254.6 | 1.462 | 0.712 | 4.67 | 0.641 | 4.25 | 0.7374 | 0.5915 | 0.7338 | 0.9092 | 1 | 0.5331 | 0.6411 | 0.7242 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Moisture_PPM
1613 | 1609.2 | 847.7 | 138.1 | 184.4 | 31.7 | 1235.2 | 7896.1 | 38.8 | 44.3 | 106.9 | 106.9 | 91.1 | 116.6 | 44 | 33 | 3023.6 | 2231.4 | 2199.5 | 3562.7 | 2717.5 | 2433 | 1.178 | 1.218 | 1.106 | 0.941 | 0.864 | 0.934 | 8.97 | 8.61 | 9.43 | 0.862 | 0.789 | 0.796 | 6.83 | 7.98 | 5.61 | 0.822 | 0.782 | 0.761 | 8.35 | 7.65 | -7.26 | 0.833 | 0.798 | 0.92 | 6.95 | 6.64 | 6.92 | Very Poor_Mixed | 2199.5 | 2433 | 1.106 | 0.941 | 9.43 | 0.92 | 8.35 | 0.1131 | 0.6367 | 0.1455 | 0.2826 | 1 | 0.1082 | 0.2455 | 0.3527 | 0.3527 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1614 | 1464.1 | 791.8 | 139.1 | 178.7 | 32 | 1227.2 | 8274.1 | 34.5 | 45.8 | 105.5 | 106.8 | 93.6 | 116.4 | 43.8 | 31 | 2301.3 | 1441 | 2697 | 2757.6 | 1517.7 | 3245 | 1.198 | 1.053 | 1.203 | 0.922 | 0.965 | 0.917 | 9.35 | -9.34 | 8.94 | 0.788 | 0.764 | 0.834 | 7.49 | 6.59 | 7.63 | 0.848 | 0.87 | 0.944 | 7.73 | -6.06 | -6.68 | 0.764 | 0.752 | 0.861 | -6.28 | 7.14 | -6.1 | Very Poor_Mixed | 1441 | 1517.7 | 1.053 | 0.965 | 9.35 | 0.944 | 7.73 | 0.1282 | 0.6222 | 0.1421 | 0.3597 | 1 | 0.0826 | 0.249 | 0.3553 | 0.3553 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1615 | 1287.1 | 735.9 | 125.1 | 159.8 | 28.1 | 1099.6 | 7194.8 | 56.8 | 23 | 78.9 | 75 | 71.3 | 84.3 | 36.4 | 11.3 | 8440.3 | 7382.4 | 9249.4 | 15483.6 | 12995.2 | 16977.5 | 1.834 | 1.76 | 1.836 | 0.702 | 0.652 | 0.613 | 5.1 | -4.11 | 4.03 | 0.55 | 0.566 | 0.5 | 3.12 | -2.29 | 2.32 | 0.562 | 0.527 | 0.575 | 2.3 | 2 | 2.39 | 0.516 | 0.579 | 0.538 | 2.54 | 2.1 | -2.76 | Poor_DGA | 7382.4 | 12995.2 | 1.76 | 0.702 | 5.1 | 0.579 | 3.12 | 0.2203 | 0.9067 | 0.9082 | 0.9802 | 1 | 0.5685 | 0.799 | 0.6871 | 0.6871 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1616 | 958 | 565.9 | 108.4 | 133.8 | 20.2 | 835.3 | 5529.9 | 46.7 | 34.8 | 88.1 | 86.5 | 82.5 | 96.6 | 38.7 | 24.2 | 6801.7 | 6593.1 | 6596.2 | 10896.5 | 11028.9 | 10741.5 | 1.602 | 1.673 | 1.628 | 0.724 | 0.753 | 0.699 | -5.17 | 5.08 | 5.16 | 0.681 | 0.608 | 0.69 | -4.64 | 4.78 | -3.77 | 0.648 | 0.651 | 0.682 | 4 | 5.21 | 4.64 | 0.629 | 0.659 | 0.658 | 3.62 | -4.79 | 4.27 | Poor_Mixed | 6593.1 | 10741.5 | 1.602 | 0.753 | 5.17 | 0.69 | 5.21 | 0.3917 | 0.7368 | 0.571 | 0.6074 | 1 | 0.4588 | 0.5175 | 0.5912 | 0.5912 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1617 | 966 | 530.1 | 107.3 | 134.6 | 17.1 | 895 | 6152.7 | 57.1 | 22.5 | 79 | 82.8 | 74.7 | 86.3 | 36.6 | 15.6 | 7451.5 | 7528.2 | 7247.8 | 13909.6 | 13048.7 | 12330.3 | 1.867 | 1.733 | 1.701 | 0.557 | 0.558 | 0.579 | 2.95 | 2.78 | 3.26 | 0.511 | 0.502 | 0.521 | -2.58 | 2.35 | 2.62 | 0.507 | 0.611 | 0.561 | -2.92 | -2.68 | 3.44 | 0.643 | 0.555 | 0.522 | 3.39 | 3.49 | 3.24 | Poor_DGA | 7247.8 | 12330.3 | 1.701 | 0.579 | 3.26 | 0.643 | 3.49 | 0.3999 | 0.9171 | 0.7861 | 0.8773 | 1 | 0.7646 | 0.7766 | 0.7393 | 0.7393 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1618 | 919.2 | 540.1 | 109.5 | 128.9 | 23.4 | 878.2 | 5967.5 | 48.1 | 32.9 | 92 | 93.8 | 81.3 | 100.1 | 39.9 | 22.1 | 5839.3 | 6660.6 | 7191.8 | 9101.7 | 10947.9 | 11569.5 | 1.559 | 1.644 | 1.609 | 0.714 | 0.726 | 0.72 | 4.77 | -5.52 | 5.84 | 0.663 | 0.668 | 0.725 | 2.87 | 3.94 | -3.48 | 0.672 | 0.701 | 0.606 | 5.16 | 3.49 | -4.45 | 0.571 | 0.662 | 0.616 | 4.25 | -5.08 | -5.23 | Poor_Mixed | 5839.3 | 9101.7 | 1.559 | 0.726 | 5.84 | 0.725 | 5.23 | 0.3736 | 0.7593 | 0.4795 | 0.6786 | 1 | 0.4499 | 0.5322 | 0.5852 | 0.5852 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1619 | 1749.5 | 873.9 | 146.6 | 197 | 34.3 | 1379 | 8327.8 | 33.2 | 47.9 | 107.7 | 107.3 | 95.6 | 118.3 | 44.5 | 33.5 | 1673.9 | 1401.8 | 1515 | 1927.4 | 1541.7 | 1659.2 | 1.151 | 1.1 | 1.095 | 0.964 | 0.936 | 0.99 | 8.75 | 9.78 | 9.84 | 0.838 | 0.962 | 0.764 | -8.61 | 6.73 | -7.63 | 0.732 | 0.784 | 0.818 | -7.46 | 5.25 | -8.21 | 0.831 | 0.908 | 0.858 | 6.38 | -7.64 | -6.75 | Very Poor_Mixed | 1401.8 | 1541.7 | 1.095 | 0.99 | 9.84 | 0.962 | 8.61 | 0.0507 | 0.6025 | 0.1016 | 0.2631 | 1 | 0.0511 | 0.2318 | 0.3172 | 0.3172 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1620 | 886.2 | 613 | 109.4 | 121.5 | 20 | 879.1 | 5740.4 | 54.3 | 24.1 | 76 | 77.2 | 70.9 | 81.2 | 36.1 | 13.7 | 9180.9 | 8262.4 | 8707.3 | 16888.8 | 14659.6 | 15744.4 | 1.84 | 1.774 | 1.808 | 0.557 | 0.573 | 0.514 | 3.21 | 3.32 | 2.48 | 0.5 | 0.5 | 0.5 | 2.21 | 2.25 | 2.3 | 0.5 | 0.5 | 0.5 | 2.09 | 2 | 2.28 | 0.511 | 0.506 | 0.5 | 2.19 | -2 | 2.33 | Poor_DGA | 8262.4 | 14659.6 | 1.774 | 0.573 | 3.32 | 0.511 | 2.33 | 0.3965 | 0.8857 | 0.9288 | 0.9269 | 1 | 0.7956 | 0.9699 | 0.7906 | 0.7906 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1621 | 219.3 | 176.2 | 73.6 | 68.2 | 1.3 | 484.9 | 3810.8 | 57.4 | 23 | 77.2 | 79.4 | 72.8 | 82.9 | 35 | 10.3 | 8566.8 | 8920.1 | 9152.8 | 15819.3 | 16466.3 | 18269.8 | 1.847 | 1.846 | 1.996 | 0.654 | 0.696 | 0.659 | 4.5 | 4.88 | -4.94 | 0.566 | 0.565 | 0.556 | -2.24 | 2.46 | -2.69 | 0.593 | 0.557 | 0.529 | 3.43 | 2.12 | 2.46 | 0.579 | 0.528 | 0.532 | 3.17 | 2.62 | 2.5 | Fair_Winding_TD_Cap | 8566.8 | 15819.3 | 1.846 | 0.696 | 4.94 | 0.593 | 3.43 | 0.8681 | 0.9067 | 0.8713 | 0.9968 | 1 | 0.5317 | 0.7557 | 0.8333 | 0.8333 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
1622 | 1582 | 882.1 | 140 | 190.1 | 31.4 | 1226 | 8198.3 | 31.6 | 46.6 | 106.3 | 106.3 | 94.2 | 113.8 | 44.6 | 34.6 | 871.6 | 1484.9 | 1277.2 | 1200 | 1621.3 | 1341.1 | 1.377 | 1.092 | 1.05 | 0.954 | 0.937 | 0.933 | -9.38 | 9.16 | 8.36 | 0.896 | 0.801 | 0.775 | 9.84 | 6.29 | -8.67 | 0.958 | 0.74 | 0.99 | -7.7 | -9.29 | 7.58 | 0.771 | 0.875 | 0.897 | -8.6 | -8 | 8.14 | Very Poor_Mixed | 871.6 | 1200 | 1.05 | 0.954 | 9.38 | 0.99 | 9.84 | 0.1036 | 0.6147 | 0.1442 | 0.2197 | 1 | 0.0903 | 0.1781 | 0.3298 | 0.3298 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1623 | 1455.8 | 864.4 | 133.6 | 182.6 | 33.5 | 1332.8 | 7833.7 | 33.2 | 45.5 | 104.6 | 105.2 | 94.9 | 115.7 | 43.8 | 32.6 | 2846.1 | 1774.9 | 1729.1 | 3541.5 | 2152.1 | 1915.4 | 1.244 | 1.213 | 1.108 | 0.903 | 0.901 | 0.915 | 8.78 | 8.03 | 8.44 | 0.898 | 0.805 | 0.918 | 8.32 | 7.48 | -8.55 | 0.799 | 0.77 | 0.69 | -7.6 | 6.37 | -8.9 | 0.847 | 0.797 | 0.889 | 8.55 | 7.42 | 8.32 | Very Poor_Mixed | 1729.1 | 1915.4 | 1.108 | 0.915 | 8.78 | 0.918 | 8.9 | 0.1096 | 0.6251 | 0.1522 | 0.2982 | 1 | 0.1421 | 0.2159 | 0.3513 | 0.3513 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1624 | 635 | 430.8 | 86.6 | 94.5 | 4.4 | 669.1 | 4350.6 | 30.6 | 47.4 | 79.9 | 80.7 | 73.5 | 86.7 | 37.1 | 17.3 | 5091.1 | 4480.3 | 5462.5 | 4026.4 | 6243.1 | 8063.3 | 0.791 | 1.393 | 1.476 | 0.72 | 0.682 | 0.606 | 5.83 | -5.13 | -4 | 0.5 | 0.527 | 0.513 | 3.06 | -2.39 | -3.24 | 0.502 | 0.5 | 0.522 | -2.23 | 2.69 | 2.39 | 0.535 | 0.5 | 0.5 | 2.3 | 2 | 2.32 | Critical_Oil | 4480.3 | 4026.4 | 0.791 | 0.72 | 5.83 | 0.535 | 3.24 | 0.654 | 0.6072 | 0.7999 | 0.8291 | 0.8187 | 0.523 | 0.9066 | 0.7252 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
1625 | 185.9 | 186.7 | 73.7 | 58.8 | 3.3 | 350 | 3496.6 | 59.3 | 23 | 77.3 | 76.3 | 75.2 | 84.1 | 37.1 | 13 | 9946.2 | 8485.9 | 8551.1 | 19892.4 | 15199 | 14935.4 | 2 | 1.791 | 1.747 | 0.579 | 0.552 | 0.547 | 2.85 | -2.98 | 2.46 | 0.539 | 0.518 | 0.739 | 2 | 2.47 | 4.78 | 0.551 | 0.527 | 0.535 | 3.53 | 3.12 | 2.99 | 0.518 | 0.559 | 0.559 | 2.72 | 2.51 | 2 | Poor_Bushing_TD_Cap | 8485.9 | 14935.4 | 1.747 | 0.579 | 2.98 | 0.739 | 4.78 | 0.8564 | 0.9067 | 0.8672 | 0.9438 | 1 | 0.7892 | 0.7519 | 0.8626 | 0.8626 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1626 | 703.5 | 422.6 | 95.5 | 90.1 | 11.6 | 736.7 | 4711.8 | 49.4 | 29.2 | 87.6 | 92.6 | 80.3 | 95.4 | 39.6 | 19.7 | 6799.3 | 6145.8 | 6940.6 | 10570.6 | 10137.4 | 11687.4 | 1.555 | 1.649 | 1.684 | 0.695 | 0.641 | 0.641 | -5.56 | 4.34 | -4.67 | 0.659 | 0.654 | 0.581 | -3.8 | -4.45 | 4.17 | 0.605 | 0.568 | 0.558 | 4.13 | -3.2 | 3.6 | 0.614 | 0.636 | 0.553 | 2.76 | 5.51 | -5.46 | Poor_Mixed | 6145.8 | 10137.4 | 1.555 | 0.695 | 5.56 | 0.659 | 5.51 | 0.56 | 0.8067 | 0.5483 | 0.7562 | 1 | 0.5383 | 0.6092 | 0.6745 | 0.6745 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1627 | 1056.2 | 641.1 | 116.3 | 132.7 | 17.5 | 904.6 | 5546.4 | 46.9 | 36 | 93.9 | 90.8 | 83.4 | 99.8 | 38.9 | 24.5 | 5752 | 6412.3 | 4653.6 | 8647.3 | 10339.3 | 6594 | 1.503 | 1.612 | 1.417 | 0.751 | 0.735 | 0.769 | 6.22 | 5.21 | 6.12 | 0.637 | 0.686 | 0.612 | 5.18 | -5.36 | -3.97 | 0.687 | 0.668 | 0.726 | 4.2 | 2.92 | 5.5 | 0.601 | 0.738 | 0.674 | 6.2 | 5.17 | -4.92 | Poor_Mixed | 4653.6 | 6594 | 1.417 | 0.769 | 6.22 | 0.738 | 6.2 | 0.3786 | 0.7231 | 0.481 | 0.597 | 1 | 0.3962 | 0.4877 | 0.5626 | 0.5626 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1628 | 829 | 461.4 | 101.9 | 114.5 | 18.8 | 861.6 | 4726.3 | 46.1 | 34.3 | 89.2 | 90.1 | 83.2 | 98.3 | 40.8 | 24 | 7329.7 | 6121 | 6204.9 | 12738.8 | 9508 | 9879.6 | 1.738 | 1.553 | 1.592 | 0.738 | 0.687 | 0.731 | -5.54 | 5.46 | -5.46 | 0.681 | 0.657 | 0.744 | 4.28 | -4.77 | 3.7 | 0.684 | 0.698 | 0.687 | 4.11 | 4.86 | -5.16 | 0.732 | 0.633 | 0.697 | 3.34 | -3.81 | 4.49 | Poor_Mixed | 6121 | 9508 | 1.553 | 0.738 | 5.54 | 0.744 | 5.16 | 0.4498 | 0.7426 | 0.5127 | 0.6143 | 1 | 0.4451 | 0.4806 | 0.5924 | 0.5924 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1629 | 248.4 | 200.2 | 79.4 | 73.8 | 2.9 | 386.9 | 3042.4 | 26.6 | 22.6 | 79.8 | 81.5 | 74.6 | 83.1 | 36.4 | 14.2 | 987.5 | 690 | 789 | 1095.1 | 755.9 | 824 | 1.109 | 1.096 | 1.044 | 0.699 | 0.661 | 0.654 | 5.17 | -5.2 | 5.06 | 0.635 | 0.564 | 0.554 | -4.42 | 4.05 | 3.11 | 0.567 | 0.591 | 0.569 | -4.76 | 2.45 | 3.25 | 0.559 | 0.57 | 0.597 | -3.1 | 3.41 | -3.47 | Critical_IR_PI | 690 | 755.9 | 1.044 | 0.699 | 5.2 | 0.635 | 4.76 | 0.8248 | 0.3317 | 0.807 | 0.9144 | 0.85 | 0.5088 | 0.6701 | 0.7003 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
1630 | 123.8 | 131.2 | 80.4 | 56.3 | 5.3 | 448.3 | 2965.8 | 58.9 | 21 | 78.6 | 78 | 72.7 | 84.2 | 35.5 | 13.5 | 9413.8 | 9249.6 | 9945.4 | 18655.7 | 17012.1 | 19890.7 | 1.982 | 1.839 | 2 | 0.537 | 0.503 | 0.515 | 2.24 | -2 | -2 | 0.519 | 0.535 | 0.533 | 2.3 | -2 | 2.2 | 0.528 | 0.5 | 0.508 | -2.2 | 2 | 2.34 | 0.503 | 0.5 | 0.502 | 2.47 | 2.61 | 2.77 | Good_Mixed | 9249.6 | 17012.1 | 1.839 | 0.537 | 2.24 | 0.535 | 2.77 | 0.8223 | 0.9543 | 0.8632 | 0.9318 | 1 | 0.9246 | 0.8979 | 0.9041 | 0.9041 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1631 | 619.1 | 385.1 | 93.1 | 96.2 | 13.9 | 658.1 | 4221.1 | 52 | 28 | 85.3 | 85.1 | 80 | 91.9 | 37.8 | 18.8 | 7624.5 | 6847.7 | 7652 | 12565.1 | 10962.6 | 13124.4 | 1.648 | 1.601 | 1.715 | 0.715 | 0.669 | 0.719 | 4.42 | -4.95 | 5.24 | 0.603 | 0.674 | 0.693 | 4.04 | -4.07 | -3.82 | 0.654 | 0.615 | 0.638 | 4.3 | 4.06 | 3.86 | 0.594 | 0.696 | 0.618 | 3.84 | 3.7 | 3.48 | Fair_Mixed | 6847.7 | 10962.6 | 1.601 | 0.719 | 5.24 | 0.696 | 4.3 | 0.5636 | 0.8235 | 0.6458 | 0.7841 | 1 | 0.4963 | 0.5563 | 0.6731 | 0.6731 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1632 | 1515.7 | 868.4 | 137.2 | 180.9 | 32.8 | 1294.7 | 8131.6 | 30.6 | 47.7 | 109.2 | 105.4 | 92.6 | 114.4 | 44.4 | 33.1 | 2518.1 | 690 | 1027.7 | 2981.7 | 1200 | 1200 | 1.184 | 1.739 | 1.168 | 0.949 | 0.937 | 0.913 | 8.99 | 9.11 | 9.37 | 0.832 | 0.788 | 0.837 | 8.41 | 7.91 | 5.74 | 0.895 | 0.844 | 0.894 | 6.64 | 6.11 | 8.75 | 0.773 | 0.911 | 0.898 | 5.69 | 5.72 | 5.78 | Very Poor_Mixed | 690 | 1200 | 1.168 | 0.949 | 9.37 | 0.911 | 8.75 | 0.1067 | 0.6044 | 0.1408 | 0.2787 | 1 | 0.0863 | 0.2271 | 0.3402 | 0.3402 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1633 | 478.9 | 286.3 | 87.8 | 96.9 | 9.8 | 563.4 | 4148.8 | 48.8 | 30.9 | 88.4 | 85.7 | 77.9 | 92.5 | 39.2 | 20.1 | 7978.4 | 9260.8 | 8125.5 | 14032.6 | 16095.7 | 14322 | 1.759 | 1.738 | 1.763 | 0.708 | 0.59 | 0.7 | 5.14 | 3.79 | -5.54 | 0.622 | 0.549 | 0.65 | 3.88 | 3.62 | 3.24 | 0.588 | 0.64 | 0.571 | 4.26 | 3.76 | 3.99 | 0.624 | 0.55 | 0.621 | 4.94 | -3.64 | 2.18 | Fair_Mixed | 7978.4 | 14032.6 | 1.738 | 0.708 | 5.54 | 0.65 | 4.94 | 0.6366 | 0.7842 | 0.6226 | 0.7436 | 1 | 0.537 | 0.6274 | 0.7008 | 0.7008 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1634 | 152.8 | 120 | 69.2 | 50 | 2.8 | 409.5 | 3290.4 | 54.9 | 22.8 | 77.4 | 78.8 | 74.1 | 81.6 | 36.1 | 11.3 | 8573 | 7729.8 | 8926.2 | 15457.7 | 13796.1 | 16330.3 | 1.803 | 1.785 | 1.829 | 0.666 | 0.635 | 0.637 | 4.24 | 4.86 | 4.03 | 0.554 | 0.552 | 0.519 | 2.13 | 3.74 | -2.94 | 0.554 | 0.533 | 0.523 | 2.65 | 3.22 | -3.5 | 0.573 | 0.529 | 0.596 | 2.78 | 2.6 | 2.11 | Fair_Winding_TD_Cap | 7729.8 | 13796.1 | 1.785 | 0.666 | 4.86 | 0.596 | 3.74 | 0.8876 | 0.9108 | 0.8662 | 0.9802 | 1 | 0.5791 | 0.7645 | 0.8455 | 0.8455 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1635 | 565.8 | 474.3 | 94.2 | 96.2 | 13 | 668.1 | 4210.9 | 50.2 | 29.2 | 85.1 | 87.5 | 78.5 | 96.1 | 38.1 | 18.5 | 6279.7 | 6723 | 7882 | 10027.1 | 11264.2 | 12971.9 | 1.597 | 1.675 | 1.646 | 0.643 | 0.722 | 0.604 | -3.41 | 4.77 | 3.9 | 0.641 | 0.606 | 0.627 | 3.95 | 3.34 | 3.41 | 0.635 | 0.571 | 0.557 | -3.36 | 2.77 | 3.4 | 0.63 | 0.558 | 0.582 | -4.63 | -4.3 | -4.39 | Fair_Mixed | 6279.7 | 10027.1 | 1.597 | 0.722 | 4.77 | 0.641 | 4.63 | 0.5626 | 0.8067 | 0.6176 | 0.7933 | 1 | 0.5926 | 0.6267 | 0.6946 | 0.6946 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1636 | 1491.6 | 843.9 | 135.2 | 178 | 34.3 | 1252.2 | 7770 | 35.5 | 43.1 | 108.1 | 107.4 | 93.9 | 116.3 | 43.5 | 32.3 | 3014.5 | 2134.6 | 2302.4 | 3789.1 | 2504.5 | 3033.1 | 1.257 | 1.173 | 1.317 | 0.875 | 0.883 | 0.916 | 8.47 | 8.93 | -9.34 | 0.971 | 0.865 | 0.695 | 6.79 | 8.11 | 6.05 | 0.752 | 0.768 | 0.745 | 7.82 | 6.28 | 7.96 | 0.93 | 0.863 | 0.953 | 6.32 | 9.07 | 6.39 | Very Poor_Mixed | 2134.6 | 2504.5 | 1.173 | 0.916 | 9.34 | 0.971 | 9.07 | 0.1179 | 0.6484 | 0.1255 | 0.3098 | 1 | 0.1276 | 0.2295 | 0.3545 | 0.3545 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1637 | 1026.8 | 597.1 | 112.8 | 125 | 23.5 | 957.9 | 6145 | 57.2 | 23.2 | 79.9 | 80.6 | 72.8 | 84.3 | 35.9 | 14.1 | 7747.7 | 9305.4 | 8889.5 | 14879.9 | 18296.8 | 17299.3 | 1.921 | 1.966 | 1.946 | 0.569 | 0.512 | 0.513 | -2.48 | 2.22 | 3.3 | 0.5 | 0.506 | 0.512 | -2.45 | 2 | 2.23 | 0.524 | 0.516 | 0.527 | 2 | -2.13 | 2 | 0.5 | 0.524 | 0.513 | 2.3 | 2 | 2 | Poor_DGA | 7747.7 | 14879.9 | 1.921 | 0.569 | 3.3 | 0.527 | 2.45 | 0.3481 | 0.9027 | 0.8246 | 0.9169 | 1 | 0.8521 | 0.9072 | 0.7662 | 0.7662 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1638 | 903.2 | 538.6 | 101.8 | 123.8 | 15.9 | 865.7 | 5098.8 | 44.6 | 35.5 | 95.2 | 93.7 | 84.8 | 100.8 | 39.6 | 26.4 | 6148.6 | 5457.3 | 5276.9 | 9957.4 | 8299.7 | 7724.1 | 1.619 | 1.521 | 1.464 | 0.715 | 0.663 | 0.789 | 4.82 | 4.33 | 6.4 | 0.702 | 0.655 | 0.709 | 5.2 | 4.42 | 3.57 | 0.66 | 0.556 | 0.613 | 5.03 | 5.51 | 4.49 | 0.643 | 0.681 | 0.673 | 3.88 | 5.42 | 5.29 | Poor_Mixed | 5276.9 | 7724.1 | 1.464 | 0.789 | 6.4 | 0.709 | 5.51 | 0.4406 | 0.7287 | 0.4364 | 0.5299 | 1 | 0.4616 | 0.5103 | 0.5842 | 0.5842 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
1639 | 1137.4 | 686.5 | 114.7 | 138.3 | 20.1 | 943.6 | 5869 | 56.3 | 22 | 80.9 | 81.4 | 73.5 | 84.9 | 35.2 | 15.1 | 9192.1 | 9172.3 | 9234.7 | 17257 | 18230.6 | 17315.8 | 1.877 | 1.988 | 1.875 | 0.569 | 0.583 | 0.561 | -3.51 | -3.7 | 2.94 | 0.593 | 0.53 | 0.55 | 3.39 | 3.17 | 2.41 | 0.584 | 0.543 | 0.58 | 2.01 | -2.7 | 2.54 | 0.513 | 0.527 | 0.543 | 2.25 | 2.51 | 2.15 | Poor_DGA | 9172.3 | 17257 | 1.875 | 0.583 | 3.7 | 0.593 | 3.39 | 0.3396 | 0.9283 | 0.8034 | 0.8908 | 1 | 0.7302 | 0.7723 | 0.7224 | 0.7224 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1640 | 957.5 | 481.8 | 103.5 | 109.9 | 13.6 | 857.9 | 5392.2 | 47.7 | 33.4 | 92.7 | 91.8 | 82.5 | 98 | 39.7 | 26.1 | 5918 | 5799.8 | 6204.8 | 9653.1 | 9862.2 | 9866.1 | 1.631 | 1.7 | 1.59 | 0.727 | 0.702 | 0.683 | -6.73 | -5 | -5.14 | 0.692 | 0.76 | 0.662 | 5.1 | -4.84 | 4.89 | 0.665 | 0.68 | 0.621 | -5.19 | 5.07 | 4.29 | 0.609 | 0.627 | 0.666 | 5.32 | 4.09 | -5.42 | Poor_Mixed | 5799.8 | 9653.1 | 1.59 | 0.727 | 6.73 | 0.76 | 5.42 | 0.4691 | 0.7532 | 0.4918 | 0.5407 | 1 | 0.4513 | 0.4896 | 0.5952 | 0.5952 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1641 | 902.4 | 579.5 | 103.7 | 122 | 19.2 | 840.1 | 5420.1 | 43.8 | 35.6 | 92.7 | 93.9 | 82.6 | 100.2 | 39.3 | 26.1 | 4925.1 | 4686.8 | 5793.3 | 7250.3 | 6881.9 | 8591.8 | 1.472 | 1.468 | 1.483 | 0.714 | 0.741 | 0.716 | -4.37 | -5.69 | 6.14 | 0.709 | 0.627 | 0.709 | 3.69 | 5.7 | 4.86 | 0.693 | 0.737 | 0.66 | -4.06 | 5.12 | -5 | 0.682 | 0.675 | 0.631 | 5.22 | 5.02 | 4.92 | Poor_Mixed | 4686.8 | 6881.9 | 1.468 | 0.741 | 6.14 | 0.737 | 5.7 | 0.4155 | 0.7276 | 0.4694 | 0.5407 | 1 | 0.4459 | 0.4717 | 0.5725 | 0.5725 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1642 | 1004.8 | 577.7 | 102.5 | 119.2 | 16.2 | 879.8 | 5738.4 | 45.9 | 37 | 95.2 | 91.4 | 85.6 | 102.6 | 41.1 | 23.6 | 5995.7 | 5786.3 | 4815.6 | 9906.2 | 8646.9 | 6990.8 | 1.652 | 1.494 | 1.452 | 0.784 | 0.778 | 0.784 | 7.09 | 6.44 | -7.08 | 0.588 | 0.661 | 0.717 | 4.75 | -5.04 | 4.05 | 0.69 | 0.701 | 0.723 | 5.69 | 4.88 | 4.21 | 0.646 | 0.714 | 0.678 | 4.87 | 4.58 | 5.22 | Poor_Mixed | 4815.6 | 6990.8 | 1.452 | 0.784 | 7.09 | 0.723 | 5.69 | 0.4219 | 0.712 | 0.4274 | 0.628 | 1 | 0.3157 | 0.4746 | 0.5547 | 0.5547 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1643 | 1651.5 | 871.3 | 142.5 | 184.4 | 31.5 | 1332.3 | 7833.9 | 33.3 | 47.6 | 104.3 | 100.7 | 91.9 | 112.5 | 43.6 | 30 | 2233.9 | 2284.3 | 1768.7 | 2826.2 | 2599.2 | 2089.8 | 1.265 | 1.138 | 1.182 | 0.952 | 0.938 | 0.927 | 9.1 | 9.07 | 8.38 | 0.847 | 0.889 | 0.728 | 6.72 | 7.17 | 8.6 | 0.757 | 0.79 | 0.884 | -5.46 | 7.93 | 6.46 | 0.719 | 0.823 | 0.846 | 6.05 | -4.99 | -8.05 | Very Poor_Mixed | 1768.7 | 2089.8 | 1.138 | 0.952 | 9.1 | 0.889 | 8.6 | 0.0951 | 0.6053 | 0.2136 | 0.3976 | 1 | 0.0977 | 0.2659 | 0.3592 | 0.3592 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1644 | 786.4 | 580.5 | 108.9 | 122 | 14.8 | 908.6 | 5644.8 | 57.4 | 23 | 75 | 75 | 70 | 80 | 35.1 | 14 | 9073.6 | 8345.7 | 8599 | 16834.8 | 16172.5 | 15809.5 | 1.855 | 1.938 | 1.839 | 0.546 | 0.566 | 0.563 | -2.7 | 2.98 | 2.98 | 0.5 | 0.5 | 0.507 | 2.07 | 2.44 | 2.56 | 0.528 | 0.548 | 0.5 | 2.25 | 2 | 3.52 | 0.5 | 0.577 | 0.52 | 2 | 2.62 | 2.43 | Poor_DGA | 8345.7 | 15809.5 | 1.839 | 0.566 | 2.98 | 0.577 | 3.52 | 0.4383 | 0.9067 | 0.9998 | 0.9194 | 1 | 0.7814 | 0.8877 | 0.7935 | 0.7935 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1645 | 297.1 | 227.7 | 67.2 | 51.3 | 78.7 | 421.3 | 2895.3 | 33.7 | 44.9 | 77 | 76.2 | 71.6 | 83.3 | 35.2 | 14.6 | 4738.6 | 4561 | 3971 | 6708.2 | 6389.2 | 5697.9 | 1.416 | 1.401 | 1.435 | 0.607 | 0.651 | 0.69 | 4.04 | 4.91 | 4.13 | 0.589 | 0.552 | 0.53 | 2.78 | 3.33 | 2.31 | 0.559 | 0.531 | 0.532 | 2.81 | 2 | 2.74 | 0.549 | 0.568 | 0.573 | 3.3 | 2.22 | 2.7 | Critical_Oil | 3971 | 5697.9 | 1.401 | 0.69 | 4.91 | 0.589 | 3.33 | 0.6208 | 0.6309 | 0.9146 | 0.904 | 1 | 0.578 | 0.758 | 0.7449 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1646 | 736.1 | 488.8 | 101.3 | 111.8 | 15.3 | 758 | 4666.1 | 48.5 | 34.5 | 91.6 | 88 | 81.2 | 100.2 | 40 | 25.3 | 5246.2 | 6141.4 | 6194.4 | 7662 | 9625.7 | 9876.7 | 1.46 | 1.567 | 1.594 | 0.72 | 0.759 | 0.769 | 5.61 | 6.25 | -5.84 | 0.715 | 0.631 | 0.626 | 6.47 | 4.22 | 3.77 | 0.679 | 0.624 | 0.711 | 5.18 | 5.25 | 4.36 | 0.709 | 0.683 | 0.663 | 6.02 | -4.86 | 5.08 | Poor_Mixed | 5246.2 | 7662 | 1.46 | 0.769 | 6.25 | 0.715 | 6.47 | 0.4933 | 0.7403 | 0.5195 | 0.569 | 1 | 0.3954 | 0.4769 | 0.5938 | 0.5938 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1647 | 878.6 | 529.5 | 101.5 | 109.5 | 18.1 | 964.8 | 5844.4 | 43.1 | 36.1 | 91.3 | 93.3 | 84.4 | 99.7 | 40.2 | 23.2 | 5657 | 6081 | 6014.6 | 9325.9 | 9751.7 | 10042.9 | 1.649 | 1.604 | 1.67 | 0.762 | 0.803 | 0.785 | 5.93 | 6.41 | 6.69 | 0.594 | 0.742 | 0.755 | 5.76 | 5.2 | 4.47 | 0.699 | 0.618 | 0.633 | -6.28 | 5.84 | -4.35 | 0.729 | 0.754 | 0.767 | 4.95 | -6.14 | 5.55 | Poor_Mixed | 5657 | 9325.9 | 1.604 | 0.803 | 6.69 | 0.767 | 6.28 | 0.4239 | 0.722 | 0.4676 | 0.6416 | 1 | 0.343 | 0.4337 | 0.5575 | 0.5575 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1648 | 801.1 | 560.2 | 107.9 | 119.9 | 19.5 | 802.7 | 5916.4 | 48 | 32.2 | 92.5 | 92.7 | 82.2 | 99.2 | 40.9 | 26.1 | 5005.7 | 5398.9 | 6505.9 | 7214.7 | 7937.7 | 10213.2 | 1.441 | 1.47 | 1.57 | 0.755 | 0.715 | 0.681 | -5.55 | 5.78 | 5.19 | 0.689 | 0.694 | 0.661 | 3.53 | 4.84 | 4.3 | 0.715 | 0.666 | 0.716 | 5.25 | 5.99 | 4.97 | 0.636 | 0.734 | 0.7 | 4.96 | -4.83 | -4.82 | Poor_Mixed | 5005.7 | 7214.7 | 1.441 | 0.755 | 5.78 | 0.734 | 5.99 | 0.4223 | 0.7678 | 0.4754 | 0.5407 | 1 | 0.4459 | 0.4598 | 0.5775 | 0.5775 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1649 | 1627.2 | 915 | 144.4 | 186.7 | 31.2 | 1276.1 | 8669 | 36 | 43.5 | 109.3 | 109.3 | 95 | 118.9 | 43.4 | 32.7 | 1711.1 | 2386.4 | 2373.2 | 1882 | 2747.5 | 2948.6 | 1.1 | 1.151 | 1.242 | 0.842 | 0.907 | 0.907 | 7.94 | 8.4 | 8.16 | 0.903 | 0.818 | 0.912 | -8.29 | -7.83 | -7.54 | 0.711 | 0.794 | 0.844 | 7 | -8.12 | -7.39 | 0.924 | 0.746 | 0.851 | -6.62 | -6.96 | -8.29 | Very Poor_Mixed | 1711.1 | 1882 | 1.1 | 0.907 | 8.4 | 0.924 | 8.29 | 0.0852 | 0.6445 | 0.0903 | 0.2943 | 1 | 0.17 | 0.2188 | 0.3456 | 0.3456 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1650 | 770.3 | 452 | 106.8 | 116.6 | 17.1 | 867.5 | 5441.1 | 59.1 | 20.8 | 76 | 79.9 | 71.4 | 84.3 | 35 | 14.4 | 8283.3 | 9718 | 9160.5 | 15249.8 | 18140.8 | 17150.5 | 1.841 | 1.867 | 1.872 | 0.51 | 0.537 | 0.52 | 2 | 2 | 2 | 0.513 | 0.516 | 0.506 | 2 | 2.13 | 2.31 | 0.508 | 0.527 | 0.543 | -2.72 | 2 | 2.09 | 0.523 | 0.514 | 0.546 | -2.5 | 2.53 | -2.12 | Poor_DGA | 8283.3 | 15249.8 | 1.841 | 0.537 | 2 | 0.546 | 2.72 | 0.4527 | 0.9605 | 0.8867 | 0.9092 | 1 | 0.9196 | 0.863 | 0.8066 | 0.8066 | Good | 1 | 1 | DGA | 0 |  | C2H2
1651 | 289.6 | 183.2 | 75.1 | 69.3 | 1.6 | 438.8 | 3448.3 | 57.2 | 22 | 78.5 | 78.5 | 73 | 83.4 | 35.3 | 12.4 | 8848.2 | 9081.7 | 8698.7 | 17312.7 | 18163.4 | 16128.9 | 1.957 | 2 | 1.854 | 0.717 | 0.776 | 0.778 | -5.56 | 6.34 | -5.97 | 0.517 | 0.555 | 0.5 | 2.49 | 3.22 | 2.92 | 0.569 | 0.599 | 0.573 | 2.49 | 2.93 | -2.15 | 0.554 | 0.541 | 0.53 | 2.38 | 2.65 | -2.41 | Poor_Winding_TD_Cap | 8698.7 | 16128.9 | 1.854 | 0.778 | 6.34 | 0.599 | 3.22 | 0.8542 | 0.9283 | 0.8615 | 0.9575 | 1 | 0.3861 | 0.7824 | 0.8139 | 0.8139 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
1652 | 766.9 | 477.2 | 97.9 | 107.9 | 14.4 | 719.4 | 4990.9 | 48.8 | 30.2 | 90 | 86.8 | 79.5 | 92.3 | 39.1 | 23.2 | 7271.2 | 6891.2 | 6208 | 12919.1 | 11808.2 | 10195.8 | 1.777 | 1.714 | 1.642 | 0.696 | 0.693 | 0.726 | 5.41 | 5.05 | 5.66 | 0.67 | 0.694 | 0.649 | 6.19 | 5.11 | 4.84 | 0.678 | 0.644 | 0.695 | 4.11 | 4.34 | -4.84 | 0.612 | 0.69 | 0.664 | 4.08 | -4.64 | 3.32 | Poor_Mixed | 6208 | 10195.8 | 1.642 | 0.726 | 5.66 | 0.695 | 6.19 | 0.5066 | 0.7933 | 0.5947 | 0.6416 | 1 | 0.4637 | 0.4977 | 0.6279 | 0.6279 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1653 | 670.3 | 503.4 | 99.1 | 105.3 | 16 | 792.9 | 4668 | 56.5 | 21.2 | 80 | 81.5 | 70.7 | 85.6 | 35.5 | 12.1 | 9805.9 | 10000 | 9109.6 | 18910.4 | 20000 | 17423.1 | 1.928 | 2 | 1.913 | 0.511 | 0.506 | 0.545 | -2.84 | -2 | 2.11 | 0.552 | 0.527 | 0.569 | 3.07 | 2.45 | 3.12 | 0.5 | 0.548 | 0.527 | -3.1 | 2.81 | 2.24 | 0.578 | 0.548 | 0.56 | 2.34 | 2.38 | 2.69 | Fair_DGA | 9109.6 | 17423.1 | 1.913 | 0.545 | 2.84 | 0.578 | 3.12 | 0.496 | 0.9486 | 0.8316 | 0.964 | 1 | 0.9004 | 0.7837 | 0.7963 | 0.7963 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1654 | 819.5 | 546.8 | 103.7 | 127.1 | 15 | 765 | 4967.3 | 46.2 | 36.2 | 94.2 | 91.4 | 82.2 | 100.2 | 39.5 | 23.8 | 6715 | 6028.6 | 5240.2 | 10981.1 | 10062.5 | 8032.5 | 1.635 | 1.669 | 1.533 | 0.722 | 0.79 | 0.667 | -5.99 | 6.53 | 5.25 | 0.653 | 0.717 | 0.633 | 4.61 | 5.26 | 5.71 | 0.626 | 0.745 | 0.729 | 4.22 | 4.2 | 4.27 | 0.652 | 0.645 | 0.688 | 4.87 | 4.39 | 3.62 | Poor_Mixed | 5240.2 | 8032.5 | 1.533 | 0.79 | 6.53 | 0.745 | 5.71 | 0.4618 | 0.7208 | 0.4771 | 0.6212 | 1 | 0.4159 | 0.4874 | 0.5867 | 0.5867 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1655 | 1477.6 | 862.5 | 140.8 | 174.7 | 27.8 | 1210.3 | 8198.6 | 34 | 46.1 | 105.7 | 107.4 | 94.6 | 115.9 | 46 | 32.8 | 1067.1 | 2246.8 | 1833.9 | 1219 | 2591.5 | 2215.6 | 1.142 | 1.153 | 1.208 | 0.9 | 0.863 | 0.928 | -8.67 | -8.31 | 9.7 | 0.806 | 0.99 | 0.915 | 5.35 | 5.78 | 6.07 | 0.842 | 0.758 | 0.696 | 8.02 | 7.65 | 6.34 | 0.833 | 0.756 | 0.927 | 9.25 | 6.4 | 5.45 | Very Poor_Mixed | 1067.1 | 1219 | 1.142 | 0.928 | 9.7 | 0.99 | 9.25 | 0.1438 | 0.6194 | 0.1184 | 0.2904 | 1 | 0.1249 | 0.2475 | 0.3587 | 0.3587 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1656 | 173.5 | 170.9 | 71.3 | 104.5 | 1.5 | 447 | 3400 | 59 | 20.2 | 89.3 | 93.5 | 80.4 | 97.1 | 40.5 | 13.9 | 8093.2 | 9621.9 | 9388.7 | 15632.3 | 18849 | 17845.5 | 1.932 | 1.959 | 1.901 | 0.5 | 0.501 | 0.5 | 2 | 2.13 | 2 | 0.506 | 0.567 | 0.5 | 2.84 | 2.34 | 2 | 0.525 | 0.514 | 0.5 | 2.62 | 2 | -2.22 | 0.5 | 0.503 | 0.524 | 2.03 | -2 | 2.86 | Poor_Thermal | 8093.2 | 15632.3 | 1.901 | 0.501 | 2.13 | 0.567 | 2.86 | 0.8324 | 0.984 | 0.5161 | 0.9219 | 1 | 0.991 | 0.9019 | 0.885 | 0.885 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1657 | 1766 | 969.2 | 148.3 | 197 | 32.4 | 1379 | 8354.3 | 50.5 | 86.4 | 77 | 78.8 | 73.7 | 83.5 | 35.9 | 11 | 8313.5 | 8755.3 | 9316.4 | 15764.1 | 15693.5 | 17407.9 | 1.896 | 1.792 | 1.869 | 0.513 | 0.561 | 0.61 | -2.37 | 2.5 | 4.19 | 0.5 | 0.539 | 0.553 | 2.89 | 2.81 | 2.65 | 0.567 | 0.572 | 0.597 | 2.83 | 3.2 | 2.59 | 0.57 | 0.552 | 0.543 | 3.33 | 2.71 | 2.63 | Critical_DGA | 8313.5 | 15693.5 | 1.792 | 0.61 | 4.19 | 0.597 | 3.33 | 0.0457 | 0.5833 | 0.8651 | 0.9858 | 1 | 0.78 | 0.7556 | 0.6224 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
1658 | 1470.4 | 886 | 140.6 | 187.7 | 34.3 | 1292.3 | 8073.8 | 35.6 | 43.8 | 104.4 | 105.2 | 93.6 | 113.3 | 44.2 | 32.3 | 3883.2 | 1988.5 | 1462.9 | 5081.3 | 2360.3 | 1616.6 | 1.309 | 1.187 | 1.105 | 0.867 | 0.901 | 0.894 | 8.16 | -8.12 | 8.21 | 0.833 | 0.758 | 0.909 | 7.39 | 9.37 | 6.64 | 0.749 | 0.871 | 0.924 | 6.12 | -6.37 | 8.51 | 0.728 | 0.845 | 0.772 | -8.51 | 5.93 | -7.63 | Very Poor_Mixed | 1462.9 | 1616.6 | 1.105 | 0.901 | 8.21 | 0.924 | 9.37 | 0.0943 | 0.6415 | 0.1696 | 0.3098 | 1 | 0.1685 | 0.2367 | 0.3592 | 0.3592 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1659 | 712.8 | 403.5 | 91.1 | 107.1 | 15.2 | 735.9 | 4974.3 | 49.6 | 31.6 | 89 | 91.1 | 79.4 | 99.3 | 38.6 | 22.4 | 6351.1 | 6794 | 7445.5 | 9746.3 | 11786.7 | 12850.3 | 1.535 | 1.735 | 1.726 | 0.728 | 0.66 | 0.734 | -5.92 | 4.78 | 5.75 | 0.616 | 0.69 | 0.611 | 3.02 | 4.4 | 4.64 | 0.593 | 0.621 | 0.654 | 4.4 | 3.51 | 3.1 | 0.608 | 0.601 | 0.593 | 3.3 | 3.43 | 3.53 | Poor_Mixed | 6351.1 | 9746.3 | 1.535 | 0.734 | 5.92 | 0.69 | 4.64 | 0.5173 | 0.7753 | 0.541 | 0.6686 | 1 | 0.4565 | 0.5955 | 0.641 | 0.641 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1660 | 751.4 | 404 | 99.2 | 103.9 | 11.2 | 747.3 | 4614.4 | 49.1 | 31.6 | 85.6 | 87.2 | 78.3 | 91.4 | 39.4 | 20.5 | 6080.2 | 5872.3 | 6475.3 | 9077.8 | 9075.8 | 9988.2 | 1.493 | 1.546 | 1.543 | 0.658 | 0.65 | 0.646 | 3.95 | -4.71 | 4.63 | 0.57 | 0.679 | 0.605 | 4.08 | 4.42 | -4.35 | 0.625 | 0.689 | 0.692 | 4.71 | 4.74 | 3.66 | 0.683 | 0.68 | 0.624 | 4.28 | 3.16 | 3.98 | Poor_Mixed | 5872.3 | 9075.8 | 1.493 | 0.658 | 4.71 | 0.692 | 4.74 | 0.5436 | 0.7753 | 0.633 | 0.7308 | 1 | 0.5701 | 0.5389 | 0.6656 | 0.6656 | Fair | 1 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1661 | 701.2 | 468 | 100.5 | 118.3 | 16.3 | 731.7 | 4796.5 | 56.9 | 22.3 | 75 | 76.7 | 70.3 | 81.4 | 35.5 | 12.3 | 9582.5 | 7526.6 | 8288.6 | 18729.6 | 13303.3 | 14840.8 | 1.955 | 1.768 | 1.791 | 0.556 | 0.537 | 0.587 | 3.48 | -2.8 | 3.56 | 0.541 | 0.556 | 0.54 | -2.99 | 3.71 | 2.93 | 0.547 | 0.521 | 0.553 | -2.87 | 2.5 | 3.63 | 0.587 | 0.571 | 0.589 | -3.09 | 2.72 | 2.72 | Poor_DGA | 7526.6 | 13303.3 | 1.768 | 0.587 | 3.56 | 0.589 | 3.71 | 0.4881 | 0.9215 | 0.9604 | 0.9597 | 1 | 0.7547 | 0.7368 | 0.7749 | 0.7749 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1662 | 269.9 | 231.9 | 74.5 | 70.1 | 1.5 | 414.7 | 3548.7 | 57.6 | 20.4 | 78.5 | 79.1 | 72.8 | 82.3 | 35.9 | 12.6 | 5311.6 | 6794.7 | 7062.7 | 8416.1 | 11305.3 | 12235 | 1.584 | 1.664 | 1.732 | 0.561 | 0.6 | 0.569 | 2.43 | -2.91 | 3.26 | 0.548 | 0.527 | 0.533 | 2 | 2.07 | -2.48 | 0.54 | 0.556 | 0.534 | 2.86 | -2.46 | -2.67 | 0.538 | 0.549 | 0.505 | 2 | 2.34 | 2.32 | Fair_IR_PI | 5311.6 | 8416.1 | 1.584 | 0.6 | 3.26 | 0.556 | 2.86 | 0.8573 | 0.9748 | 0.8606 | 0.953 | 1 | 0.7576 | 0.8153 | 0.8778 | 0.8778 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1663 | 837.3 | 480.4 | 105 | 111.5 | 17.9 | 777.5 | 4537.1 | 60 | 20.1 | 78.3 | 78.7 | 75.2 | 83.6 | 35 | 10 | 8558.1 | 9185.1 | 9925.8 | 17017.6 | 17152.3 | 18556.1 | 1.988 | 1.867 | 1.869 | 0.573 | 0.5 | 0.52 | 3.05 | 2.84 | -2.44 | 0.544 | 0.534 | 0.551 | 3.1 | 2.22 | 3.39 | 0.512 | 0.515 | 0.503 | -2.81 | 2 | -2.54 | 0.535 | 0.544 | 0.531 | 2.61 | 2.39 | 3.03 | Fair_DGA | 8558.1 | 17017.6 | 1.867 | 0.573 | 3.05 | 0.551 | 3.39 | 0.4655 | 0.9898 | 0.8439 | 1 | 1 | 0.8543 | 0.8186 | 0.7965 | 0.7965 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1664 | 422.5 | 369.1 | 84 | 85.1 | 8.5 | 605 | 4526.2 | 52.1 | 27.1 | 81.7 | 86.3 | 75.7 | 90.5 | 38 | 19.1 | 7780.1 | 8265.6 | 8870.4 | 13898.9 | 15080 | 16411.4 | 1.786 | 1.824 | 1.85 | 0.573 | 0.623 | 0.584 | 3.77 | -4.33 | 2.87 | 0.57 | 0.539 | 0.635 | 3.44 | 3.46 | 3.75 | 0.591 | 0.632 | 0.615 | -3.68 | 3.32 | 2.67 | 0.602 | 0.573 | 0.553 | 2.62 | 2.48 | -3.22 | Fair_Mixed | 7780.1 | 13898.9 | 1.786 | 0.623 | 4.33 | 0.635 | 3.75 | 0.6503 | 0.8367 | 0.7006 | 0.7749 | 1 | 0.6848 | 0.6679 | 0.7479 | 0.7479 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1665 | 1766 | 982.4 | 148.3 | 197 | 33.6 | 1379 | 8388.7 | 53.3 | 25 | 81.6 | 85.5 | 78.1 | 90.3 | 36.5 | 14.6 | 7913.3 | 8092.5 | 6455.1 | 15078.2 | 13955.8 | 11109.4 | 1.905 | 1.725 | 1.721 | 0.689 | 0.593 | 0.632 | 4.27 | 23.79 | 4.34 | 0.542 | 0.539 | 0.569 | -3.06 | 3.57 | 2.59 | 0.565 | 0.54 | 0.512 | 2.76 | 3.04 | 2.19 | 0.55 | 0.507 | 0.559 | 2 | 2.85 | 2.77 | Critical_DGA | 6455.1 | 11109.4 | 1.721 | 0.689 | 23.79 | 0.569 | 3.57 | 0.0386 | 0.87 | 0.6991 | 0.904 | 1 | 0.4927 | 0.783 | 0.5991 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1666 | 780.3 | 599.7 | 109.3 | 130 | 17.5 | 869.5 | 5524.4 | 57.7 | 23.6 | 80.2 | 81.9 | 72.5 | 88.7 | 35.5 | 15.6 | 9904.8 | 9549.5 | 9712.6 | 19066 | 18238.2 | 19021.6 | 1.925 | 1.91 | 1.958 | 0.535 | 0.574 | 0.55 | 2.19 | 3.07 | -2.55 | 0.52 | 0.545 | 0.567 | 3.45 | 2.22 | 2.13 | 0.559 | 0.516 | 0.565 | 2.6 | 2.94 | 3.14 | 0.544 | 0.575 | 0.551 | 2.11 | 2.65 | 3.03 | Poor_DGA | 9549.5 | 18238.2 | 1.91 | 0.574 | 3.07 | 0.575 | 3.45 | 0.417 | 0.895 | 0.7936 | 0.8773 | 1 | 0.8119 | 0.7684 | 0.7468 | 0.7468 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1667 | 501.6 | 362.9 | 95.4 | 95.3 | 2.7 | 684.6 | 4331.4 | 57.4 | 20.8 | 80.4 | 82.3 | 76 | 87.5 | 36.6 | 13.1 | 8430.7 | 8463.7 | 8515.4 | 15002.9 | 15250.6 | 15686.4 | 1.78 | 1.802 | 1.842 | 0.92 | 0.922 | 0.915 | -9.25 | 8.8 | 8.83 | 0.551 | 0.524 | 0.5 | -2.72 | -2.56 | 2 | 0.581 | 0.56 | 0.524 | 2.68 | 2.81 | 2.42 | 0.505 | 1.974 | 0.52 | 3.04 | -2.77 | 3.08 | Critical_Winding_TD_Cap | 8430.7 | 15002.9 | 1.78 | 0.922 | 9.25 | 1.974 | 3.08 | 0.6948 | 0.9605 | 0.7618 | 0.9414 | 1 | 0.1058 | 0.7582 | 0.7235 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_LV_TanDelta_pct
1668 | 211.8 | 180.2 | 73.4 | 94.3 | 1 | 402.9 | 2500 | 57.2 | 21.1 | 89.4 | 85.4 | 83 | 94.7 | 39.1 | 10.4 | 9501.6 | 9467.7 | 9325.1 | 18592 | 18274.3 | 18273.6 | 1.957 | 1.93 | 1.96 | 0.633 | 0.554 | 0.558 | 3.83 | 2.67 | 3.78 | 0.528 | 0.5 | 0.536 | 2.45 | 2.01 | 2 | 0.519 | 0.523 | 0.524 | 2.62 | -2.53 | -2 | 0.5 | 0.5 | 0.543 | -2 | 2.18 | 2.22 | Poor_Thermal | 9325.1 | 18273.6 | 1.93 | 0.633 | 3.83 | 0.543 | 2.62 | 0.8972 | 0.9514 | 0.5739 | 0.9955 | 1 | 0.7172 | 0.8887 | 0.866 | 0.866 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1669 | 1092.5 | 729.5 | 117.3 | 139.4 | 24.1 | 1019 | 6709.3 | 55 | 23.4 | 75.2 | 76.9 | 71.1 | 80.6 | 36.5 | 12.3 | 9912.4 | 9295 | 8912.3 | 19663.2 | 18383.4 | 16358.4 | 1.984 | 1.978 | 1.835 | 0.504 | 0.5 | 0.556 | 2.67 | 2.57 | 2.96 | 0.564 | 0.56 | 0.5 | -2.95 | 3.37 | 3.26 | 0.568 | 0.537 | 0.577 | 2.78 | 2.93 | 2.98 | 0.507 | 0.597 | 0.59 | 2.42 | 2 | -3.01 | Poor_DGA | 8912.3 | 16358.4 | 1.835 | 0.556 | 2.96 | 0.597 | 3.37 | 0.2948 | 0.8988 | 0.9432 | 0.9597 | 1 | 0.8814 | 0.7604 | 0.7441 | 0.7441 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1670 | 212 | 198.6 | 70.1 | 68 | 3.2 | 424 | 2910.9 | 59.9 | 20 | 77.2 | 76 | 71.6 | 81.8 | 36 | 14.1 | 10000 | 9677 | 10000 | 19682.5 | 18974.3 | 20000 | 1.968 | 1.961 | 2 | 0.567 | 0.615 | 0.538 | -2.71 | -3.4 | 2 | 0.521 | 0.586 | 0.56 | 3.28 | 2.69 | 2.3 | 0.56 | 0.514 | 0.553 | 3.35 | 2.69 | 2.61 | 0.504 | 0.5 | 0.5 | 2.27 | -2.71 | 2.58 | Good_Mixed | 9677 | 18974.3 | 1.961 | 0.615 | 3.4 | 0.586 | 3.35 | 0.8294 | 1 | 0.9192 | 0.9169 | 1 | 0.7796 | 0.8265 | 0.883 | 0.883 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1671 | 981 | 546.7 | 103.6 | 128.6 | 17.8 | 802.8 | 5790.4 | 45.8 | 32 | 92.6 | 95.2 | 83.9 | 100.3 | 39.6 | 26.3 | 4927 | 4544.5 | 5752.8 | 7115.7 | 6349 | 8885.9 | 1.444 | 1.397 | 1.545 | 0.754 | 0.75 | 0.72 | -6.04 | 5.06 | -6.41 | 0.744 | 0.683 | 0.693 | 5.44 | 5.22 | 4.63 | 0.735 | 0.749 | 0.677 | -6.31 | 3.85 | 4.52 | 0.667 | 0.63 | 0.691 | -4.52 | 4.48 | 4.15 | Poor_Mixed | 4544.5 | 6349 | 1.397 | 0.754 | 6.41 | 0.749 | 6.31 | 0.4162 | 0.7703 | 0.4514 | 0.5335 | 1 | 0.4059 | 0.4545 | 0.5669 | 0.5669 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1672 | 756.9 | 536.7 | 101.1 | 117.4 | 19 | 784.3 | 5578.6 | 43.5 | 36.3 | 92 | 87.7 | 81.5 | 100.4 | 38.6 | 24.3 | 5977.7 | 4721.2 | 6500.7 | 9011.9 | 6744.2 | 9839.1 | 1.508 | 1.428 | 1.514 | 0.829 | 0.771 | 0.745 | 6.36 | 6 | 5.69 | 0.703 | 0.699 | 0.746 | 4.82 | 6.33 | -4.26 | 0.624 | 0.708 | 0.701 | -4.54 | 6.07 | 6.21 | 0.638 | 0.658 | 0.654 | 4.08 | 4.96 | 4.82 | Poor_Mixed | 4721.2 | 6744.2 | 1.428 | 0.829 | 6.36 | 0.746 | 6.33 | 0.4447 | 0.7197 | 0.5248 | 0.6039 | 1 | 0.3626 | 0.461 | 0.574 | 0.574 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1673 | 129.6 | 167.2 | 66.9 | 62 | 4.2 | 439 | 3175.1 | 60 | 20.9 | 78 | 77.1 | 70 | 82.9 | 35 | 11.6 | 9458.6 | 10000 | 9756.2 | 18146.9 | 20000 | 19158.1 | 1.919 | 2 | 1.964 | 0.519 | 0.5 | 0.512 | 2.19 | 2 | -2.04 | 0.547 | 0.533 | 0.5 | 2.59 | -2.52 | 2.13 | 0.56 | 0.536 | 0.527 | -2.34 | 2 | -2 | 0.564 | 0.539 | 0.519 | -2.25 | 2.02 | -2.28 | Good_Mixed | 9458.6 | 18146.9 | 1.919 | 0.519 | 2.19 | 0.564 | 2.59 | 0.8315 | 0.9574 | 0.9156 | 0.9744 | 1 | 0.9477 | 0.8297 | 0.905 | 0.905 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1674 | 995.5 | 558.1 | 106.8 | 129.9 | 23.1 | 984.9 | 6447.3 | 58.5 | 24.5 | 75.5 | 75 | 70.5 | 82.5 | 35 | 10 | 8710 | 9792.1 | 9021.7 | 15661.6 | 18751.5 | 17223 | 1.798 | 1.915 | 1.909 | 0.563 | 0.618 | 0.57 | -3.27 | 3.7 | 2.65 | 0.5 | 0.524 | 0.517 | 2 | 2.75 | 2 | 0.517 | 0.526 | 0.5 | 2.68 | -2.28 | 2.16 | 0.517 | 0.559 | 0.5 | 2.19 | 2 | 2 | Poor_DGA | 8710 | 15661.6 | 1.798 | 0.618 | 3.7 | 0.559 | 2.75 | 0.3501 | 0.8786 | 0.9696 | 1 | 1 | 0.7263 | 0.8947 | 0.7626 | 0.7626 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1675 | 240.4 | 261.7 | 78 | 143.6 | 2.7 | 496.6 | 3640.9 | 58 | 22.8 | 103.8 | 106.2 | 90.2 | 111.1 | 43.1 | 12.2 | 9234.5 | 9846 | 9467.3 | 17615.2 | 19482.9 | 18199.8 | 1.908 | 1.979 | 1.922 | 0.585 | 0.566 | 1.346 | 3.38 | 2.99 | -2.84 | 0.554 | 0.559 | 0.573 | 3.76 | 2.5 | 2.72 | 0.538 | 0.556 | 0.568 | -3.29 | 4.14 | 2.72 | 0.57 | 0.581 | 0.535 | 3.31 | 2.3 | 3.22 | Critical_Thermal | 9234.5 | 17615.2 | 1.908 | 1.346 | 3.38 | 0.581 | 4.14 | 0.7279 | 0.9108 | 0.2057 | 0.9618 | 1 | 0.623 | 0.7247 | 0.7376 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H4
1676 | 1371.6 | 745.8 | 127.5 | 158.9 | 32.4 | 1045.6 | 6851.5 | 34.6 | 44.4 | 102.3 | 102.9 | 90.3 | 111.3 | 42.8 | 29.8 | 2191.7 | 946.7 | 2032.5 | 2301.3 | 1200 | 2321.8 | 1.05 | 1.268 | 1.142 | 0.966 | 0.91 | 0.925 | -8.89 | 8.29 | 8.08 | 0.749 | 0.729 | 0.878 | 7.86 | 5.36 | 5.44 | 0.787 | 0.771 | 0.753 | 7.01 | 6.38 | -7.03 | 0.842 | 0.884 | 0.797 | 7.68 | 7.11 | 8.31 | Very Poor_Mixed | 946.7 | 1200 | 1.05 | 0.966 | 8.89 | 0.884 | 8.31 | 0.2025 | 0.6357 | 0.2331 | 0.4051 | 1 | 0.1233 | 0.2723 | 0.3967 | 0.3967 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1677 | 410.2 | 304.7 | 77.3 | 76.7 | 2.3 | 536.7 | 3653.9 | 53.5 | 25.4 | 110.1 | 82.3 | 78.1 | 90.8 | 37.5 | 16.2 | 690 | 1216.8 | 1104 | 749.4 | 1289.1 | 1184.7 | 1.086 | 1.059 | 1.073 | 0.668 | 0.658 | 0.689 | 5.3 | 5.2 | 5.72 | 0.52 | 0.559 | 0.577 | 2.23 | 2.1 | 2 | 0.51 | 0.528 | 0.549 | 2.47 | 2.86 | 2 | 0.531 | 0.518 | 0.505 | 3.09 | 2 | -2.47 | Critical_IR_PI | 690 | 749.4 | 1.059 | 0.689 | 5.72 | 0.577 | 3.09 | 0.7788 | 0.8633 | 0.537 | 0.8607 | 0.925 | 0.4935 | 0.8305 | 0.7616 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature; IR_Min_10min<1000 Mohm: critical insulation resistance | WTI_HV
1678 | 1419.3 | 786.9 | 131.4 | 161.6 | 27.2 | 1143.2 | 7616.1 | 33.2 | 45.7 | 107.7 | 106.1 | 94 | 116.8 | 45 | 32.7 | 4073.6 | 3872.1 | 2980.1 | 5306.7 | 5196.9 | 3545.1 | 1.303 | 1.342 | 1.19 | 0.921 | 0.9 | 0.883 | 8.49 | 8.39 | 8.32 | 0.927 | 0.668 | 0.869 | 7.8 | 7.68 | -5.72 | 0.867 | 0.717 | 0.776 | 4.61 | -6.92 | 5.05 | 0.806 | 0.862 | 0.823 | 5.15 | 6.81 | 5.58 | Very Poor_Mixed | 2980.1 | 3545.1 | 1.19 | 0.921 | 8.49 | 0.927 | 7.8 | 0.1928 | 0.6232 | 0.1208 | 0.2943 | 1 | 0.1465 | 0.2874 | 0.382 | 0.382 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1679 | 1416.3 | 902.3 | 141.3 | 185.1 | 32.2 | 1304.3 | 8459.9 | 34.1 | 46.9 | 107.4 | 102.4 | 95.7 | 115.6 | 44.4 | 30.8 | 1977.1 | 1955 | 1460.5 | 2075.9 | 2237.7 | 1576.4 | 1.05 | 1.145 | 1.079 | 0.958 | 0.99 | 0.99 | -9.4 | 9.84 | -9.71 | 0.963 | 0.799 | 0.902 | 7.8 | 5.73 | 6.49 | 0.924 | 0.888 | 0.773 | 8.32 | 7.58 | 8.51 | 0.891 | 0.759 | 0.949 | 9.84 | -8.59 | 6.31 | Very Poor_Mixed | 1460.5 | 1576.4 | 1.05 | 0.99 | 9.84 | 0.963 | 9.84 | 0.1008 | 0.6119 | 0.1442 | 0.3673 | 1 | 0.0308 | 0.1806 | 0.3282 | 0.3282 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1680 | 481.8 | 363 | 90.7 | 92.5 | 4.1 | 667.2 | 4251.6 | 57.4 | 23.3 | 78.7 | 77.3 | 70.9 | 82.2 | 35.9 | 11.3 | 8410.1 | 7477.1 | 7788.6 | 15259.5 | 13033.4 | 13307.5 | 1.814 | 1.743 | 1.709 | 0.986 | 0.99 | 1.008 | -9.84 | 9.41 | -9.21 | 0.565 | 0.53 | 0.5 | -2.53 | 2.97 | 2 | 0.526 | 0.546 | 0.555 | 2.34 | -2.39 | 2 | 0.5 | 0.531 | 0.5 | 2.77 | -2.13 | -2.37 | Critical_Winding_TD_Cap | 7477.1 | 13033.4 | 1.709 | 1.008 | 9.84 | 0.565 | 2.97 | 0.68 | 0.9008 | 0.8947 | 0.9802 | 1 | 0.0307 | 0.8571 | 0.7352 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
1681 | 945.5 | 531.7 | 99.6 | 130.8 | 20.6 | 942.6 | 5782.1 | 46.6 | 33.2 | 91.8 | 92.1 | 82.3 | 98.8 | 39.7 | 26.1 | 6890.9 | 6879.4 | 5658 | 11309.1 | 11413.3 | 9109.1 | 1.641 | 1.659 | 1.61 | 0.813 | 0.717 | 0.761 | 6.71 | 5.89 | 6.22 | 0.717 | 0.636 | 0.611 | 4.71 | -4.59 | 3.83 | 0.642 | 0.689 | 0.596 | 4.16 | -5.76 | 4.31 | 0.61 | 0.709 | 0.619 | 4.81 | 4.43 | -4.07 | Poor_Mixed | 5658 | 9109.1 | 1.61 | 0.813 | 6.71 | 0.717 | 5.76 | 0.3876 | 0.7556 | 0.4929 | 0.5407 | 1 | 0.3637 | 0.5271 | 0.5697 | 0.5697 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1682 | 819.6 | 508.1 | 101.3 | 108 | 21.4 | 849.7 | 5038.4 | 48.4 | 32.6 | 88.7 | 88.2 | 79.6 | 96.5 | 39.6 | 24.1 | 6400.6 | 6528.2 | 5696.3 | 10201.1 | 10389.2 | 8867.1 | 1.594 | 1.591 | 1.557 | 0.703 | 0.741 | 0.714 | -5.48 | -5.16 | 5.24 | 0.699 | 0.704 | 0.685 | -5.4 | 5.14 | 4.3 | 0.708 | 0.672 | 0.638 | -4.06 | 4.84 | 4.19 | 0.676 | 0.683 | 0.75 | 3.51 | 4.98 | 5.03 | Poor_Mixed | 5696.3 | 8867.1 | 1.557 | 0.741 | 5.48 | 0.75 | 5.4 | 0.4355 | 0.7629 | 0.5689 | 0.6108 | 1 | 0.4551 | 0.4676 | 0.5957 | 0.5957 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1683 | 506.1 | 286.2 | 87.2 | 86.3 | 13.2 | 604.3 | 4028.2 | 52.8 | 26.6 | 83.1 | 83.3 | 76 | 89.7 | 37.9 | 15.3 | 8066.6 | 8195.4 | 8335.5 | 14971.6 | 15074.9 | 15344.6 | 1.856 | 1.839 | 1.841 | 0.635 | 0.637 | 0.605 | -4.25 | -4.42 | 4.18 | 0.549 | 0.574 | 0.618 | 3.13 | 3 | 2.34 | 0.569 | 0.597 | 0.56 | 3.22 | 4.29 | 2.44 | 0.59 | 0.567 | 0.561 | -2.9 | -4.65 | 3.12 | Fair_Mixed | 8066.6 | 14971.6 | 1.839 | 0.637 | 4.42 | 0.618 | 4.65 | 0.6139 | 0.8443 | 0.714 | 0.8855 | 1 | 0.6066 | 0.6882 | 0.7392 | 0.7392 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1684 | 532.7 | 313.5 | 90.7 | 91.5 | 11.1 | 608 | 4922.3 | 51.5 | 28.5 | 87 | 82.5 | 76.1 | 95.6 | 38.2 | 17.6 | 7305.5 | 7703.7 | 7864.5 | 12202.1 | 12525.4 | 13457.4 | 1.67 | 1.626 | 1.711 | 0.605 | 0.642 | 0.657 | 3.79 | -4.11 | -4.4 | 0.608 | 0.594 | 0.613 | -3.39 | 3.4 | 4.64 | 0.601 | 0.603 | 0.642 | 3.05 | -2.62 | -3.59 | 0.609 | 0.577 | 0.579 | 3.8 | 3.22 | -3.7 | Fair_Mixed | 7305.5 | 12202.1 | 1.626 | 0.657 | 4.4 | 0.642 | 4.64 | 0.6081 | 0.8164 | 0.6597 | 0.8203 | 1 | 0.6081 | 0.6303 | 0.7156 | 0.7156 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1685 | 925.1 | 560 | 105.1 | 116.6 | 15.9 | 889.2 | 5591.6 | 48.5 | 35.2 | 91.5 | 91.6 | 81.4 | 100.5 | 40.2 | 23.7 | 5949.6 | 7704.9 | 6152.9 | 10218.8 | 12792.5 | 10018 | 1.718 | 1.66 | 1.628 | 0.674 | 0.708 | 0.772 | 5.15 | -5.27 | 6.41 | 0.685 | 0.688 | 0.721 | -4.4 | 5.29 | -4.06 | 0.723 | 0.685 | 0.715 | 4.87 | 5.48 | 4.16 | 0.631 | 0.638 | 0.744 | 5.02 | 4.99 | 5.08 | Poor_Mixed | 5949.6 | 10018 | 1.628 | 0.772 | 6.41 | 0.744 | 5.48 | 0.4331 | 0.7322 | 0.4921 | 0.6246 | 1 | 0.4401 | 0.4583 | 0.5807 | 0.5807 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1686 | 201.9 | 167.6 | 69.7 | 63.8 | 3.5 | 352.7 | 2731 | 57.7 | 20.5 | 75 | 75.2 | 70.2 | 80 | 35 | 12.6 | 10000 | 8751 | 8650.7 | 20000 | 17502.1 | 16207.9 | 2 | 2 | 1.874 | 0.517 | 0.529 | 0.578 | 2.59 | 2.37 | 3.1 | 0.5 | 0.527 | 0.57 | 2.78 | 2 | 3.16 | 0.5 | 0.517 | 0.519 | 2 | -2.79 | 2.19 | 0.538 | 0.5 | 0.546 | 2.73 | 2.26 | 2 | Good_Mixed | 8650.7 | 16207.9 | 1.874 | 0.578 | 3.1 | 0.57 | 3.16 | 0.8513 | 0.9709 | 0.9912 | 0.953 | 1 | 0.8287 | 0.867 | 0.9082 | 0.9082 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1687 | 536.4 | 397.6 | 94.2 | 82.8 | 8.3 | 630.6 | 4155.7 | 51.9 | 27.6 | 87.2 | 85.3 | 77 | 90.4 | 37.8 | 17.9 | 6355.8 | 6397.4 | 6648.1 | 10676.6 | 10060.3 | 11208 | 1.68 | 1.573 | 1.686 | 0.656 | 0.581 | 0.622 | 4.66 | 3.88 | 4.57 | 0.612 | 0.598 | 0.573 | 3.31 | 3.48 | 3.54 | 0.632 | 0.665 | 0.645 | 3.9 | 2.94 | 2.9 | 0.575 | 0.585 | 0.626 | 4.69 | 3.3 | -4.02 | Fair_Mixed | 6355.8 | 10060.3 | 1.573 | 0.656 | 4.66 | 0.665 | 4.69 | 0.6345 | 0.8293 | 0.6589 | 0.8114 | 1 | 0.6099 | 0.6143 | 0.7206 | 0.7206 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1688 | 440.1 | 278.9 | 86 | 154.8 | 1 | 550.5 | 3779.5 | 52.5 | 29.2 | 109 | 107.7 | 93.8 | 119.2 | 44.6 | 13.7 | 8984.5 | 7939.3 | 9328.1 | 15556.9 | 14420.3 | 17164.5 | 1.732 | 1.816 | 1.84 | 0.519 | 0.533 | 0.541 | 2 | 3.73 | -2.83 | 0.524 | 0.589 | 0.555 | 4.23 | 3.06 | 3.24 | 0.568 | 0.552 | 1.961 | -2.89 | -3.83 | -2.53 | 0.553 | 0.596 | 0.565 | -3.32 | -3.41 | 3.94 | Critical_Thermal | 7939.3 | 14420.3 | 1.732 | 0.541 | 3.73 | 1.961 | 4.23 | 0.7658 | 0.8067 | 0.0971 | 0.9269 | 1 | 0.8355 | 0.6538 | 0.739 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H4
1689 | 100 | 188.1 | 69.8 | 50 | 1 | 350 | 2500 | 60 | 20 | 77.2 | 75.7 | 71.9 | 80.8 | 35 | 11.6 | 9915.4 | 9920.2 | 9924.5 | 19121.4 | 18773.6 | 19849 | 1.928 | 1.892 | 2 | 0.524 | 0.514 | 0.5 | 2.04 | 2 | 2.26 | 0.567 | 0.574 | 0.503 | -2 | 2 | 2.51 | 0.519 | 0.512 | 0.5 | -2.78 | 2.33 | 2.81 | 0.537 | 0.503 | 0.543 | 2.63 | 2.09 | -2.03 | Good_Mixed | 9915.4 | 18773.6 | 1.892 | 0.524 | 2.26 | 0.574 | 2.81 | 0.989 | 1 | 0.9293 | 0.9744 | 1 | 0.9401 | 0.8536 | 0.9542 | 0.9542 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_HV_Y_TanDelta_pct
1690 | 817.7 | 462.6 | 102.3 | 121.5 | 13 | 798.3 | 5422.6 | 44.4 | 33.1 | 90.7 | 92.1 | 84.7 | 100.5 | 41.4 | 27.4 | 5524.6 | 5932.8 | 6367.1 | 9154.7 | 9275.4 | 10185.1 | 1.657 | 1.563 | 1.6 | 0.773 | 0.753 | 0.647 | 5.74 | 6.2 | 5.15 | 0.682 | 0.659 | 0.68 | 5.47 | 5.13 | 4.81 | 0.752 | 0.737 | 0.755 | 5.07 | 4.83 | -4.56 | 0.704 | 0.669 | 0.76 | 4.52 | 6.36 | 5.61 | Poor_Mixed | 5524.6 | 9154.7 | 1.563 | 0.773 | 6.2 | 0.76 | 6.36 | 0.4833 | 0.7568 | 0.4654 | 0.4938 | 1 | 0.4308 | 0.4243 | 0.5796 | 0.5796 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1691 | 100 | 120 | 65 | 53.3 | 1 | 363.2 | 2664.9 | 58.8 | 22.6 | 76.5 | 76.2 | 70.2 | 83.1 | 35.8 | 10 | 10000 | 9353.2 | 9852 | 19829.7 | 18413.6 | 19704.1 | 1.983 | 1.969 | 2 | 0.538 | 0.567 | 0.507 | -2.33 | 2.43 | 2 | 0.57 | 0.501 | 0.509 | -2.31 | -2.38 | 2 | 0.505 | 0.535 | 0.5 | 2.77 | 2.48 | 3.03 | 0.5 | 0.561 | 0.568 | 2.5 | -2.99 | 2.72 | Good_Mixed | 9353.2 | 18413.6 | 1.969 | 0.567 | 2.43 | 0.57 | 3.03 | 0.9862 | 0.915 | 0.9344 | 1 | 1 | 0.8715 | 0.8527 | 0.9353 | 0.9353 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1692 | 778.9 | 432.2 | 94.5 | 103.5 | 13.8 | 702.2 | 4441.1 | 60 | 20 | 78.2 | 78.7 | 71.6 | 83.3 | 35.1 | 13.3 | 10000 | 10000 | 10000 | 19020.1 | 19995.6 | 19565.8 | 1.902 | 2 | 1.957 | 0.58 | 0.595 | 0.592 | 3.2 | 2.99 | 4.2 | 0.527 | 0.544 | 0.518 | 2.05 | 2.57 | 2 | 0.552 | 0.567 | 0.514 | -2.76 | -2.12 | 2 | 0.532 | 0.514 | 0.574 | 2.3 | 2.57 | 2.75 | Fair_DGA | 10000 | 19020.1 | 1.902 | 0.595 | 4.2 | 0.574 | 2.76 | 0.5294 | 1 | 0.8762 | 0.9367 | 1 | 0.7012 | 0.8149 | 0.7916 | 0.7916 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1693 | 408.3 | 208.2 | 73.4 | 82.2 | 1.3 | 584.8 | 3626.3 | 58 | 23.1 | 82.6 | 82.5 | 74.1 | 87.7 | 37.7 | 16 | 8459.4 | 7380.6 | 7846.5 | 15943.9 | 12944 | 13727.4 | 1.885 | 1.754 | 1.749 | 0.912 | 0.925 | 0.859 | 8.96 | -14.48 | -8.13 | 0.518 | 0.536 | 0.525 | 3.03 | -2 | -2.08 | 0.505 | 0.509 | 0.529 | 2.3 | 2.1 | 2.08 | 0.504 | 0.5 | 0.51 | -2 | 2.08 | 2 | Critical_Winding_TD_Cap | 7380.6 | 12944 | 1.749 | 0.925 | 14.48 | 0.536 | 3.03 | 0.8148 | 0.9047 | 0.7498 | 0.8663 | 1 | 0.117 | 0.8964 | 0.7683 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_LV_TanDelta_pct
1694 | 992.1 | 662.5 | 104.2 | 130.7 | 18.2 | 849.3 | 5990.3 | 43.4 | 35.2 | 91.9 | 90.5 | 81.4 | 100.8 | 39.8 | 25.7 | 5262.5 | 5843.2 | 5582.8 | 7847.4 | 9174.1 | 8676.3 | 1.491 | 1.57 | 1.554 | 0.746 | 0.735 | 0.657 | 5.64 | -5.72 | 5.15 | 0.676 | 0.657 | 0.71 | 4.92 | -4.5 | 4.92 | 0.637 | 0.691 | 0.736 | 5.34 | 5.46 | 4.57 | 0.638 | 0.687 | 0.716 | 5.62 | 4.77 | 3.94 | Poor_Mixed | 5262.5 | 7847.4 | 1.491 | 0.746 | 5.72 | 0.736 | 5.62 | 0.3895 | 0.7322 | 0.4978 | 0.5549 | 1 | 0.4506 | 0.4661 | 0.5698 | 0.5698 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1695 | 414 | 310.4 | 79.4 | 76.3 | 2.4 | 528.3 | 3007.2 | 55.3 | 26.1 | 81.1 | 78.5 | 73.3 | 85.1 | 36.5 | 10 | 4555.8 | 4195.4 | 4293.9 | 6392.3 | 5975.1 | 5528.4 | 1.403 | 1.424 | 1.288 | 0.685 | 0.635 | 0.637 | 4.43 | 3.83 | 3.9 | 0.569 | 0.554 | 0.593 | 3.92 | -3.65 | 3.61 | 0.615 | 0.555 | 0.626 | 2.83 | 2.86 | 2.98 | 0.59 | 0.583 | 0.53 | 3.72 | 3.02 | 2.73 | Poor_IR_PI | 4195.4 | 5528.4 | 1.288 | 0.685 | 4.43 | 0.626 | 3.92 | 0.78 | 0.852 | 0.8221 | 1 | 1 | 0.5922 | 0.6825 | 0.7952 | 0.7952 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1696 | 1710.4 | 929.9 | 140.8 | 181.9 | 32.5 | 1264 | 8044.8 | 32.1 | 49.2 | 106.1 | 105.2 | 93.6 | 115.6 | 45.1 | 31 | 1251.3 | 1413.9 | 2722 | 1396.4 | 1606.9 | 3133.3 | 1.116 | 1.137 | 1.151 | 0.989 | 0.937 | 0.932 | 9.11 | 9.28 | -8.96 | 0.861 | 0.816 | 0.826 | 5.71 | 5.96 | 5.45 | 0.91 | 0.772 | 0.744 | -6.9 | -7 | 8.82 | 0.763 | 0.793 | 0.896 | 7.68 | 8.02 | -5.56 | Very Poor_Mixed | 1251.3 | 1396.4 | 1.116 | 0.989 | 9.28 | 0.91 | 8.82 | 0.0883 | 0.5906 | 0.1421 | 0.3597 | 1 | 0.0752 | 0.2562 | 0.3418 | 0.3418 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1697 | 474.8 | 295.2 | 74.6 | 87.4 | 1 | 534.8 | 3482.8 | 32.2 | 47.2 | 75.2 | 78.2 | 71.9 | 82.4 | 35.9 | 12.6 | 4411 | 5231.3 | 4704.4 | 6330.8 | 7682.6 | 6814.3 | 1.435 | 1.469 | 1.448 | 0.659 | 0.631 | 0.646 | 4.73 | -16.65 | 4.94 | 0.51 | 0.545 | 0.546 | 2.2 | -3.54 | 2.63 | 0.511 | 0.558 | 0.511 | -2.56 | 3.32 | 2.07 | 0.614 | 0.55 | 0.555 | 2.59 | -2.19 | 2.88 | Critical_Oil | 4411 | 6330.8 | 1.435 | 0.659 | 16.65 | 0.614 | 3.54 | 0.8383 | 0.609 | 0.9158 | 0.953 | 1 | 0.462 | 0.7878 | 0.7884 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
1698 | 483.2 | 175.7 | 79.6 | 83.4 | 6.8 | 539.9 | 3656.1 | 54.1 | 23.6 | 80.6 | 81.6 | 75.2 | 87.6 | 36.5 | 16.7 | 8584.3 | 7793.6 | 8447.3 | 15616.6 | 13867.9 | 15420.5 | 1.819 | 1.779 | 1.825 | 0.56 | 0.628 | 0.567 | -2.75 | 4.09 | -3.05 | 0.5 | 0.563 | 0.572 | -2.4 | 3.06 | 3.04 | 0.541 | 0.571 | 0.569 | 2.98 | 2.58 | -3 | 0.564 | 0.559 | 0.566 | 2.95 | -3.14 | 2.96 | Fair_Mixed | 7793.6 | 13867.9 | 1.779 | 0.628 | 4.09 | 0.572 | 3.14 | 0.7071 | 0.895 | 0.7717 | 0.8465 | 1 | 0.72 | 0.7493 | 0.7993 | 0.7993 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1699 | 100 | 148.3 | 65 | 51.6 | 1 | 350 | 2500 | 60 | 20 | 76.7 | 75 | 71.8 | 80 | 35.5 | 12.7 | 9916.8 | 9417 | 9244.4 | 19687.9 | 17337.6 | 18152.7 | 1.985 | 1.841 | 1.964 | 0.514 | 0.5 | 0.53 | -2 | 2 | 2.49 | 0.532 | 0.502 | 0.519 | 2 | -2 | 2.16 | 0.532 | 0.5 | 0.5 | -2.09 | 3.19 | 2.66 | 0.5 | 0.507 | 0.51 | 2 | 2 | 2 | Good_Mixed | 9244.4 | 17337.6 | 1.841 | 0.53 | 2.49 | 0.532 | 3.19 | 0.9909 | 1 | 0.9514 | 0.9507 | 1 | 0.9317 | 0.9184 | 0.9661 | 0.9661 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1700 | 1524.6 | 937 | 141.6 | 180.9 | 33.8 | 1300.8 | 8315.4 | 31.4 | 48.5 | 108.4 | 106.4 | 96.4 | 114.4 | 44.6 | 34.7 | 1420.3 | 1270.5 | 2018.7 | 1491.3 | 1348.2 | 2327.9 | 1.05 | 1.061 | 1.153 | 0.976 | 0.982 | 0.962 | -9.62 | 9.48 | 9.35 | 0.823 | 0.766 | 0.838 | -6.75 | 9.18 | 8.41 | 0.91 | 0.834 | 0.716 | -5.96 | -5.94 | 7.4 | 0.759 | 0.759 | 0.796 | 7.45 | 6.07 | -6.76 | Very Poor_Mixed | 1270.5 | 1348.2 | 1.05 | 0.982 | 9.62 | 0.91 | 9.18 | 0.0877 | 0.597 | 0.1171 | 0.2157 | 1 | 0.043 | 0.2648 | 0.3297 | 0.3297 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1701 | 439.6 | 344.5 | 79.4 | 85.2 | 9.3 | 551.8 | 3786 | 51.7 | 27.1 | 83.4 | 83.3 | 74.7 | 87.5 | 37.4 | 15.4 | 8154.4 | 8143 | 8233.9 | 15363.2 | 15095.3 | 14935.1 | 1.884 | 1.854 | 1.814 | 0.568 | 0.602 | 0.648 | 2.76 | 3.37 | 4.54 | 0.623 | 0.544 | 0.591 | 3.49 | -4.1 | 2.76 | 0.597 | 0.604 | 0.642 | 4.1 | 4.07 | 2.35 | 0.639 | 0.526 | 0.545 | 4.21 | 3.7 | 4.02 | Fair_Mixed | 8143 | 14935.1 | 1.814 | 0.648 | 4.54 | 0.642 | 4.21 | 0.6609 | 0.8367 | 0.7353 | 0.8828 | 1 | 0.6774 | 0.6521 | 0.7555 | 0.7555 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1702 | 857.6 | 597 | 98.7 | 102.5 | 22 | 906.3 | 6130.6 | 44.1 | 38.5 | 90.4 | 92.8 | 83.1 | 99.4 | 40.4 | 24.1 | 5141.2 | 5134.8 | 5418.9 | 7445.7 | 7949.1 | 8183.2 | 1.448 | 1.548 | 1.51 | 0.789 | 0.775 | 0.768 | 7.15 | 6.69 | 6.03 | 0.727 | 0.722 | 0.685 | 4.68 | 4.89 | -6.16 | 0.67 | 0.769 | 0.724 | -3.95 | 5.85 | -5.38 | 0.697 | 0.729 | 0.765 | 4.29 | 5.38 | -4.54 | Poor_Mixed | 5134.8 | 7445.7 | 1.448 | 0.789 | 7.15 | 0.769 | 6.16 | 0.4083 | 0.6957 | 0.485 | 0.6108 | 1 | 0.3328 | 0.4177 | 0.5464 | 0.5464 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1703 | 784.6 | 556.3 | 109.7 | 127.2 | 20.9 | 885.5 | 5266.2 | 46.6 | 34.6 | 90.1 | 89.5 | 79.8 | 96.4 | 39.1 | 25.9 | 6283.2 | 6424 | 5774.5 | 9981.7 | 10177 | 8880.9 | 1.589 | 1.584 | 1.538 | 0.735 | 0.695 | 0.717 | 6.45 | 5.06 | -5.62 | 0.68 | 0.653 | 0.654 | 4.79 | -6.07 | 3.91 | 0.717 | 0.716 | 0.661 | 5.91 | 6.02 | 5.81 | 0.721 | 0.716 | 0.747 | 3.86 | 5.77 | 4.18 | Poor_Mixed | 5774.5 | 8880.9 | 1.538 | 0.735 | 6.45 | 0.747 | 6.07 | 0.4042 | 0.7391 | 0.553 | 0.5478 | 1 | 0.4355 | 0.4419 | 0.5729 | 0.5729 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1704 | 1755.7 | 951 | 147.4 | 191.3 | 29.8 | 1295.6 | 8704 | 36.4 | 45.8 | 106.4 | 103.5 | 96.1 | 116.3 | 44.6 | 34.8 | 2565.8 | 980.3 | 2579.7 | 3006.8 | 1200 | 3136.2 | 1.172 | 1.224 | 1.216 | 0.907 | 0.98 | 0.973 | 8.5 | 9.84 | 9.24 | 0.889 | 0.927 | 0.711 | 6.87 | 5.83 | -7.11 | 0.901 | 0.77 | 0.846 | -7.86 | 7.19 | -7.06 | 0.748 | 0.865 | 0.848 | 8.11 | 7.58 | 6.99 | Very Poor_Mixed | 980.3 | 1200 | 1.172 | 0.98 | 9.84 | 0.927 | 8.11 | 0.0699 | 0.6222 | 0.1363 | 0.2118 | 1 | 0.0712 | 0.2311 | 0.3279 | 0.3279 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1705 | 126.4 | 120 | 67.4 | 50 | 3.5 | 350 | 2500 | 58.6 | 21.9 | 75 | 77.5 | 72.4 | 82 | 35 | 11.1 | 9592.8 | 9386.9 | 9943 | 18903.3 | 18720.4 | 19664.3 | 1.971 | 1.994 | 1.978 | 0.553 | 0.5 | 0.5 | 3.28 | 2.08 | 2 | 0.55 | 0.528 | 0.5 | 2.03 | -2.15 | 2 | 0.508 | 0.5 | 0.512 | 2.95 | 2 | 2.1 | 0.526 | 0.5 | 0.531 | -2.03 | 2.69 | 2 | Good_Mixed | 9386.9 | 18720.4 | 1.971 | 0.553 | 3.28 | 0.55 | 2.95 | 0.8961 | 0.9307 | 0.9289 | 0.984 | 1 | 0.9179 | 0.8981 | 0.928 | 0.928 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1706 | 1540.3 | 853.4 | 141.4 | 175.1 | 29.1 | 1270.4 | 7963.4 | 34.5 | 45.1 | 107.6 | 109.3 | 95.4 | 115.9 | 43.8 | 33.2 | 1167.3 | 1573.5 | 1554 | 1321.3 | 1652.2 | 1679.8 | 1.132 | 1.05 | 1.081 | 0.95 | 0.988 | 0.953 | 8.55 | -9.68 | 9.67 | 0.735 | 0.836 | 0.881 | -8.02 | 8.76 | -7.06 | 0.936 | 0.731 | 0.766 | 7.17 | 5.48 | 5.42 | 0.752 | 0.899 | 0.871 | 8.24 | 8.35 | -5.51 | Very Poor_Mixed | 1167.3 | 1321.3 | 1.05 | 0.988 | 9.68 | 0.936 | 8.76 | 0.1297 | 0.6289 | 0.1094 | 0.2748 | 1 | 0.0587 | 0.2446 | 0.3448 | 0.3448 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1707 | 276.9 | 212.4 | 67.1 | 65.4 | 2.1 | 442.1 | 2710.7 | 58.8 | 20 | 76.8 | 79.8 | 71.6 | 84 | 36.3 | 14.7 | 7527.3 | 6221 | 6202.4 | 12480 | 10076.2 | 10281.2 | 1.658 | 1.62 | 1.658 | 0.6 | 0.568 | 0.619 | -3.69 | -3.2 | 4.01 | 0.571 | 0.549 | 0.512 | 3.01 | 2.45 | 2.55 | 0.54 | 0.519 | 0.523 | 2.65 | 2.87 | 3.19 | 0.531 | 0.538 | 0.601 | 3.17 | 2 | 2.29 | Fair_IR_PI | 6202.4 | 10076.2 | 1.62 | 0.619 | 4.01 | 0.601 | 3.19 | 0.849 | 1 | 0.8722 | 0.9014 | 1 | 0.6826 | 0.7867 | 0.8617 | 0.8617 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1708 | 962.7 | 532.9 | 103.9 | 130.7 | 19.7 | 847 | 5435.1 | 44 | 33.2 | 91.3 | 91.7 | 84.5 | 101.1 | 40.6 | 24.4 | 6523.5 | 6003 | 5678.7 | 10258.1 | 9774.8 | 8552 | 1.572 | 1.628 | 1.506 | 0.651 | 0.714 | 0.756 | 5.05 | -6.11 | 5.18 | 0.705 | 0.601 | 0.698 | -5.77 | 3.83 | 5.08 | 0.684 | 0.705 | 0.652 | 3.69 | -4.44 | -4.03 | 0.622 | 0.707 | 0.675 | 5.51 | 4.32 | -5.45 | Poor_Mixed | 5678.7 | 8552 | 1.506 | 0.756 | 6.11 | 0.707 | 5.77 | 0.4037 | 0.7556 | 0.4676 | 0.6005 | 1 | 0.4594 | 0.4888 | 0.5807 | 0.5807 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1709 | 992.7 | 525.7 | 102 | 122.1 | 16.5 | 817 | 5676.8 | 47.2 | 33 | 92.2 | 92.2 | 83.4 | 100 | 39.8 | 25.4 | 4885.7 | 6230.7 | 4738 | 7015.3 | 10125.5 | 6791 | 1.436 | 1.625 | 1.433 | 0.694 | 0.761 | 0.781 | 5.87 | 6.49 | 6.38 | 0.654 | 0.672 | 0.643 | 5.69 | 4.56 | -5.93 | 0.688 | 0.707 | 0.714 | 3.76 | 5.61 | -4.1 | 0.718 | 0.644 | 0.613 | -4.76 | 4.88 | 5.32 | Poor_Mixed | 4738 | 6791 | 1.433 | 0.781 | 6.49 | 0.718 | 5.93 | 0.4327 | 0.7581 | 0.4761 | 0.5655 | 1 | 0.3806 | 0.4774 | 0.5742 | 0.5742 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1710 | 1580.5 | 939.4 | 140.4 | 184.3 | 28.3 | 1268.5 | 7956.2 | 31.8 | 47 | 108.2 | 106.3 | 93.4 | 116.8 | 43.6 | 34.1 | 3159.4 | 2169.3 | 1035.4 | 4215.3 | 2564.4 | 1200 | 1.334 | 1.182 | 1.159 | 0.979 | 0.99 | 0.981 | 9.49 | 9.7 | 8.89 | 0.942 | 0.957 | 0.68 | 7.58 | 5.05 | 8.44 | 0.934 | 0.95 | 0.886 | 7.62 | 7.43 | -7.98 | 0.815 | 0.912 | 0.733 | 8.58 | -5.74 | 9.71 | Very Poor_Mixed | 1035.4 | 1200 | 1.159 | 0.99 | 9.7 | 0.957 | 9.71 | 0.1148 | 0.6109 | 0.1306 | 0.2395 | 1 | 0.0426 | 0.1914 | 0.3274 | 0.3274 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1711 | 675.9 | 353.5 | 97.1 | 97.6 | 14.6 | 641.3 | 4700.4 | 50.5 | 31.4 | 86.4 | 85.2 | 77.1 | 92.1 | 37.9 | 20.3 | 6990.8 | 7058.5 | 6690.9 | 12053.6 | 11358 | 10949.4 | 1.724 | 1.609 | 1.636 | 0.615 | 0.622 | 0.644 | 4.58 | 4.03 | 5.16 | 0.596 | 0.609 | 0.674 | -4.36 | 4.5 | 3.81 | 0.67 | 0.653 | 0.646 | 5.15 | 3.5 | 4.47 | 0.62 | 0.647 | 0.638 | 4.98 | 3.41 | -3.67 | Fair_Mixed | 6690.9 | 10949.4 | 1.609 | 0.644 | 5.16 | 0.674 | 5.15 | 0.5513 | 0.7778 | 0.6555 | 0.7372 | 1 | 0.5872 | 0.5486 | 0.6745 | 0.6745 | Fair | 1 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1712 | 703.3 | 426.4 | 100.6 | 123.4 | 13.4 | 725.7 | 5142.8 | 49.1 | 30 | 94 | 92 | 80.7 | 100.2 | 39.2 | 21.8 | 6647.9 | 6826.1 | 5852 | 11349.7 | 10650.4 | 10066.4 | 1.707 | 1.56 | 1.72 | 0.708 | 0.734 | 0.675 | 5.17 | -5.62 | -4.44 | 0.641 | 0.614 | 0.556 | 3.75 | 5.43 | 3.81 | 0.636 | 0.663 | 0.695 | -5.03 | 3.3 | 4.14 | 0.639 | 0.644 | 0.716 | -3.64 | 4.66 | 4.21 | Poor_Mixed | 5852 | 10066.4 | 1.56 | 0.734 | 5.62 | 0.716 | 5.43 | 0.5053 | 0.796 | 0.4861 | 0.6885 | 1 | 0.4804 | 0.5436 | 0.63 | 0.63 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1713 | 377.2 | 309.3 | 75.8 | 67.9 | 1.8 | 498.2 | 3007.2 | 56.1 | 24.3 | 81.1 | 78.7 | 74.1 | 87.1 | 36.5 | 11.8 | 3094.4 | 3697.5 | 3585.3 | 4277.3 | 4724.7 | 4895.2 | 1.382 | 1.278 | 1.365 | 0.558 | 0.617 | 0.677 | 2.88 | -3.87 | 5.05 | 0.5 | 0.546 | 0.528 | -2.23 | 3.14 | 3.12 | 0.545 | 0.521 | 0.5 | -2.74 | 2.88 | 2.37 | 0.545 | 0.527 | 0.522 | 2.1 | 2.84 | 2 | Poor_IR_PI | 3094.4 | 4277.3 | 1.278 | 0.677 | 5.05 | 0.546 | 3.14 | 0.8182 | 0.8821 | 0.8037 | 0.9703 | 1 | 0.6436 | 0.8427 | 0.8411 | 0.8411 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1714 | 1601.4 | 937.4 | 143.5 | 179.2 | 33.5 | 1349.5 | 8866.6 | 32 | 46.6 | 106.3 | 105.1 | 93.5 | 115.8 | 43.9 | 33.4 | 2276.4 | 722.1 | 1725.4 | 2534.4 | 1200 | 1855.2 | 1.113 | 1.662 | 1.075 | 0.969 | 0.98 | 0.952 | 9.23 | 9.84 | 9.57 | 0.793 | 0.922 | 0.801 | 6.89 | -9.35 | 7.48 | 0.716 | 0.89 | 0.867 | 6.18 | 7.02 | -8.58 | 0.732 | 0.758 | 0.76 | 7.96 | 5.69 | -8.01 | Very Poor_Mixed | 722.1 | 1200 | 1.075 | 0.98 | 9.84 | 0.922 | 9.35 | 0.0707 | 0.6147 | 0.1499 | 0.267 | 1 | 0.044 | 0.2502 | 0.331 | 0.331 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1715 | 1545.1 | 848.3 | 139 | 176.1 | 34 | 1300.5 | 8516 | 34.8 | 46.7 | 107.7 | 106.3 | 95.1 | 117.4 | 44.5 | 33.1 | 2048.1 | 1271.3 | 1027.7 | 2150.5 | 1478 | 1200 | 1.05 | 1.163 | 1.168 | 0.941 | 0.952 | 0.958 | -9.42 | 9.57 | 9.53 | 0.787 | 0.709 | 0.815 | -7.16 | -6.74 | 8.11 | 0.97 | 0.851 | 0.881 | 8.17 | 6.3 | 6.87 | 0.86 | 0.844 | 0.832 | 9.12 | 5.92 | 6.89 | Very Poor_Mixed | 1027.7 | 1200 | 1.05 | 0.958 | 9.57 | 0.97 | 9.12 | 0.0985 | 0.6137 | 0.1143 | 0.2787 | 1 | 0.0571 | 0.224 | 0.3319 | 0.3319 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1716 | 472.1 | 257.6 | 81.8 | 83.1 | 1 | 635.1 | 4065.9 | 49.8 | 30 | 76.7 | 78 | 70 | 81.5 | 35 | 11.1 | 7841.9 | 8530.4 | 8605.5 | 14260.6 | 15258 | 15281.2 | 1.819 | 1.789 | 1.776 | 0.983 | 0.928 | 2.202 | -9.77 | -9.14 | -9.37 | 0.587 | 0.611 | 0.582 | 3.53 | -3.9 | 3.37 | 0.64 | 0.588 | 0.582 | 3.1 | 4.22 | -3.14 | 0.602 | 0.538 | 0.674 | 2.21 | 2.43 | 2.71 | Critical_Winding_TD_Cap | 7841.9 | 14260.6 | 1.776 | 2.202 | 9.77 | 0.674 | 4.22 | 0.8246 | 0.796 | 0.927 | 0.984 | 1 | 0.048 | 0.6522 | 0.7277 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_TV_TanDelta_pct
1717 | 935.5 | 586.4 | 107.4 | 130.4 | 19.7 | 779.8 | 5392.2 | 47.1 | 32.6 | 91.8 | 89.1 | 80.8 | 96.6 | 39.1 | 24.4 | 5308 | 5873 | 5939 | 8335.3 | 9097.6 | 9433.8 | 1.57 | 1.549 | 1.588 | 0.744 | 0.719 | 0.784 | -5.77 | 5.66 | 6.5 | 0.657 | 0.697 | 0.62 | 5.21 | -4.57 | 4.4 | 0.616 | 0.611 | 0.69 | 3.88 | 5.06 | -5.17 | 0.664 | 0.613 | 0.671 | 4.99 | 3.21 | -4.75 | Poor_Mixed | 5308 | 8335.3 | 1.549 | 0.784 | 6.5 | 0.697 | 5.21 | 0.4064 | 0.7629 | 0.537 | 0.6005 | 1 | 0.3917 | 0.522 | 0.5857 | 0.5857 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1718 | 1616.4 | 928.5 | 142 | 182.1 | 30.9 | 1245.7 | 7986.8 | 31.2 | 49.4 | 104.9 | 105.1 | 93.6 | 113 | 42.9 | 32.4 | 1257.8 | 1559.2 | 753.4 | 1410.1 | 1707.4 | 1200 | 1.121 | 1.095 | 1.593 | 0.947 | 0.949 | 0.972 | 8.89 | 9.09 | 9.18 | 0.911 | 0.826 | 0.778 | -6.38 | 4.57 | 7.59 | 0.713 | 0.862 | 0.819 | 7.45 | -6.86 | -9.84 | 0.88 | 0.71 | 0.868 | 6.54 | 6.8 | 7.07 | Very Poor_Mixed | 753.4 | 1200 | 1.095 | 0.972 | 9.18 | 0.911 | 9.84 | 0.1039 | 0.5888 | 0.1782 | 0.3059 | 1 | 0.076 | 0.2518 | 0.3457 | 0.3457 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1719 | 849.3 | 523.6 | 104.4 | 123.2 | 15.4 | 813.8 | 5685.7 | 46.8 | 30.3 | 93.2 | 91.1 | 83.4 | 99.5 | 40.3 | 25.2 | 5547.3 | 5562.2 | 6166.9 | 8508 | 8158.4 | 9729.8 | 1.534 | 1.467 | 1.578 | 0.647 | 0.73 | 0.74 | 5.03 | -5.42 | 5.56 | 0.737 | 0.706 | 0.638 | 5.9 | 6.09 | 4.53 | 0.78 | 0.75 | 0.658 | -5.27 | 4.03 | 4.99 | 0.741 | 0.737 | 0.553 | -4.62 | 5.13 | 6.52 | Poor_Mixed | 5547.3 | 8158.4 | 1.467 | 0.74 | 5.56 | 0.78 | 6.52 | 0.4489 | 0.792 | 0.4761 | 0.5725 | 1 | 0.4666 | 0.4405 | 0.5881 | 0.5881 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
1720 | 470.6 | 285.6 | 81.9 | 89.2 | 1.4 | 497.9 | 3607.9 | 34.8 | 47.4 | 79.2 | 76.4 | 72.3 | 82.1 | 36.1 | 15.3 | 5166.4 | 6637.3 | 6977.6 | 7925.2 | 10464.3 | 10879.2 | 1.534 | 1.577 | 1.559 | 0.587 | 1.019 | 0.646 | 3.81 | 4.39 | 4.51 | 0.554 | 0.524 | 0.576 | 2.31 | 3.43 | 2.23 | 0.529 | 0.567 | 0.597 | 3.13 | 2.67 | 2.92 | 0.541 | 0.576 | 0.558 | 2.11 | 2.41 | 2.1 | Critical_Oil | 5166.4 | 7925.2 | 1.534 | 1.019 | 4.51 | 0.597 | 3.43 | 0.7948 | 0.6072 | 0.8862 | 0.8855 | 1 | 0.5166 | 0.7548 | 0.7726 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | Moisture_PPM
1721 | 1561.9 | 871.4 | 127.2 | 177 | 27.4 | 1237.8 | 7410.4 | 34.6 | 44.2 | 105.2 | 106.4 | 93.7 | 113.9 | 44.4 | 32.8 | 2189.7 | 2032.2 | 1384.8 | 2602.7 | 2240.5 | 1454 | 1.189 | 1.102 | 1.05 | 0.956 | 0.965 | 0.917 | 8.53 | 9.22 | -8.42 | 0.876 | 0.773 | 0.837 | 7.3 | -8.45 | -7.79 | 0.885 | 0.709 | 0.927 | 7.09 | 8.51 | -8.35 | 0.855 | 0.855 | 0.862 | 7.47 | -6.82 | -5.85 | Very Poor_Mixed | 1384.8 | 1454 | 1.05 | 0.965 | 9.22 | 0.927 | 8.51 | 0.1545 | 0.6376 | 0.1535 | 0.2904 | 1 | 0.0995 | 0.212 | 0.3571 | 0.3571 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1722 | 386.1 | 282.9 | 86.6 | 82.7 | 11.5 | 577.1 | 4622.3 | 51.7 | 28.2 | 83.2 | 87.8 | 77.8 | 92.6 | 39 | 17.3 | 6996.3 | 7273.9 | 7582.7 | 11620.8 | 12696.4 | 12945.6 | 1.661 | 1.745 | 1.707 | 0.646 | 0.53 | 0.636 | 3.69 | 2.72 | 4.28 | 0.604 | 0.633 | 0.563 | 3.49 | 3.53 | -3.12 | 0.614 | 0.588 | 0.581 | 3.54 | 4.23 | 3.47 | 0.636 | 0.642 | 0.537 | 3.54 | 2.55 | 3.56 | Fair_Mixed | 6996.3 | 11620.8 | 1.661 | 0.646 | 4.28 | 0.642 | 4.23 | 0.6413 | 0.8207 | 0.6467 | 0.8291 | 1 | 0.6854 | 0.6404 | 0.7362 | 0.7362 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1723 | 741.1 | 442.8 | 89.8 | 86 | 11.5 | 634.7 | 4360.9 | 48.1 | 34.1 | 84.5 | 87.7 | 77.7 | 88.7 | 37.9 | 18.6 | 7157.5 | 6586.4 | 6713.8 | 12608.2 | 10740 | 11753.7 | 1.762 | 1.631 | 1.751 | 0.604 | 0.665 | 0.631 | 4.1 | 4.49 | 3.97 | 0.585 | 0.62 | 0.558 | 3.38 | 3.67 | 4.49 | 0.571 | 0.595 | 0.587 | 2.82 | 2.43 | 3.92 | 0.59 | 0.622 | 0.595 | 3.45 | -3.8 | -3.6 | Fair_Mixed | 6586.4 | 10740 | 1.631 | 0.665 | 4.49 | 0.622 | 4.49 | 0.5808 | 0.7449 | 0.6643 | 0.7902 | 1 | 0.6046 | 0.6487 | 0.702 | 0.702 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1724 | 1385.9 | 801.1 | 131.4 | 174.7 | 34.2 | 1200.9 | 7591.2 | 34.8 | 43.9 | 107.7 | 105.5 | 91.5 | 113.2 | 44.3 | 29.7 | 3394.9 | 4132.6 | 3967.1 | 4391.1 | 5466.3 | 5342.3 | 1.293 | 1.323 | 1.347 | 0.957 | 0.921 | 0.881 | -9.47 | 9.23 | 9.07 | 0.924 | 0.721 | 0.804 | 5.23 | 7.11 | -6.29 | 0.854 | 0.887 | 0.746 | 8.43 | 7.75 | 5.56 | 0.854 | 0.848 | 0.711 | -7.27 | -5.91 | 5.97 | Very Poor_Mixed | 3394.9 | 4391.1 | 1.293 | 0.957 | 9.47 | 0.924 | 8.43 | 0.1444 | 0.6406 | 0.1614 | 0.4089 | 1 | 0.0907 | 0.2668 | 0.3703 | 0.3703 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1725 | 1068.6 | 677.9 | 113.2 | 134.7 | 24.4 | 917.3 | 6825 | 57.8 | 21.8 | 79.1 | 75 | 71.7 | 82.8 | 37.1 | 10.1 | 8675.8 | 9122.9 | 9056.1 | 16865.7 | 17253.4 | 16784.7 | 1.944 | 1.891 | 1.853 | 0.519 | 0.548 | 0.54 | 2.5 | 2.06 | 2.3 | 0.568 | 0.627 | 0.588 | 3.65 | 2.56 | 3.04 | 0.587 | 0.537 | 0.582 | 3.54 | 2.57 | -2.91 | 0.615 | 0.601 | 0.546 | 2.63 | 2.48 | 3.07 | Poor_DGA | 8675.8 | 16784.7 | 1.853 | 0.548 | 2.5 | 0.627 | 3.65 | 0.3188 | 0.9331 | 0.9064 | 0.9992 | 1 | 0.8653 | 0.6893 | 0.7375 | 0.7375 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1726 | 936.5 | 573.8 | 105.6 | 126.2 | 19.5 | 881.3 | 5228.8 | 47.6 | 32.8 | 92.7 | 90.2 | 82.3 | 96.2 | 39.6 | 25.3 | 4813.2 | 5234.3 | 5590.2 | 6907.1 | 7612.9 | 8360.1 | 1.435 | 1.454 | 1.495 | 0.76 | 0.765 | 0.72 | 6.13 | 5.61 | 6.37 | 0.649 | 0.757 | 0.727 | -5.02 | 5.4 | 6.37 | 0.782 | 0.645 | 0.622 | 6.21 | -3.87 | 5.06 | 0.696 | 0.689 | 0.661 | 6.02 | 4.18 | 4.46 | Poor_Mixed | 4813.2 | 6907.1 | 1.435 | 0.765 | 6.37 | 0.782 | 6.37 | 0.4032 | 0.7605 | 0.5131 | 0.569 | 1 | 0.3888 | 0.4476 | 0.5668 | 0.5668 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1727 | 173.8 | 120 | 68.5 | 50 | 1 | 350 | 2500 | 60 | 22.1 | 75.1 | 77.2 | 70 | 81.6 | 35.3 | 11.4 | 9560.8 | 9480.7 | 9326.3 | 18386.8 | 17900.8 | 17092.5 | 1.923 | 1.888 | 1.833 | 0.5 | 0.518 | 0.528 | 2.33 | 2.97 | 3.08 | 0.53 | 0.511 | 0.5 | -2.45 | -2 | 2.35 | 0.502 | 0.507 | 0.576 | 2.17 | -2.31 | 2.21 | 0.5 | 0.516 | 0.518 | 2.11 | -2 | -2 | Good_Mixed | 9326.3 | 17092.5 | 1.833 | 0.528 | 3.08 | 0.576 | 2.45 | 0.9887 | 0.926 | 0.9566 | 0.9783 | 1 | 0.8798 | 0.898 | 0.9477 | 0.9477 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1728 | 1637.1 | 887.9 | 146 | 183.3 | 33.5 | 1277.5 | 8399.4 | 31 | 48.4 | 107.9 | 109.1 | 94.4 | 119.2 | 44.8 | 32.2 | 1797.5 | 1109.7 | 3227.2 | 2061.7 | 1200 | 4050.9 | 1.147 | 1.081 | 1.255 | 0.922 | 0.899 | 0.978 | -8.57 | 8.73 | 9.75 | 0.917 | 0.863 | 0.868 | -8.59 | -6.71 | 7.38 | 0.761 | 0.921 | 0.85 | 7.07 | 6.61 | 7.47 | 0.946 | 0.787 | 0.909 | 7.12 | -8.72 | 7.26 | Very Poor_Mixed | 1109.7 | 1200 | 1.081 | 0.978 | 9.75 | 0.946 | 8.72 | 0.0822 | 0.5979 | 0.0906 | 0.3137 | 1 | 0.0938 | 0.1896 | 0.3243 | 0.3243 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1729 | 251 | 190.7 | 65.2 | 58.7 | 40.1 | 409.7 | 3048.2 | 53.8 | 25.5 | 78.8 | 81.4 | 74.2 | 86.6 | 36.2 | 17 | 5830.3 | 7393.9 | 6933.6 | 9719.8 | 12455 | 11362.9 | 1.667 | 1.684 | 1.639 | 0.99 | 0.982 | 0.942 | 9.75 | 9.16 | -9.42 | 0.545 | 0.58 | 0.583 | 2.95 | 2.42 | 2.97 | 0.574 | 0.583 | 0.56 | 2.51 | 3.3 | 3.22 | 0.568 | 0.532 | 0.524 | -3.25 | -2.67 | -3.22 | Critical_Winding_TD_Cap | 5830.3 | 9719.8 | 1.639 | 0.99 | 9.75 | 0.583 | 3.3 | 0.6176 | 0.8617 | 0.8035 | 0.8378 | 1 | 0.0464 | 0.73 | 0.6779 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1730 | 814 | 490.5 | 99.6 | 116.4 | 17.3 | 880.8 | 4886.9 | 47.5 | 31.8 | 88.6 | 91 | 80.5 | 93.8 | 38.6 | 26.2 | 7057.6 | 7932.4 | 5667.2 | 12294.5 | 13887 | 8200.4 | 1.742 | 1.751 | 1.447 | 0.662 | 0.651 | 0.702 | 4.56 | 4.07 | 5.92 | 0.656 | 0.644 | 0.695 | 5.1 | 3.81 | 4.43 | 0.632 | 0.658 | 0.65 | 3.6 | 4.04 | 3.62 | 0.589 | 0.662 | 0.621 | 3.86 | 5 | 4.97 | Poor_Mixed | 5667.2 | 8200.4 | 1.447 | 0.702 | 5.92 | 0.695 | 5.1 | 0.4529 | 0.7728 | 0.5646 | 0.5371 | 1 | 0.5263 | 0.5381 | 0.6198 | 0.6198 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1731 | 1461 | 834.2 | 129.9 | 173.9 | 32.4 | 1126.1 | 7830.4 | 34.7 | 47.4 | 102.4 | 101.4 | 89.7 | 111.3 | 43.9 | 31.2 | 1721.9 | 3667.9 | 2246.5 | 1975.6 | 4564.4 | 2807 | 1.147 | 1.244 | 1.249 | 0.901 | 0.953 | 0.922 | 8.58 | -9.26 | 8.99 | 0.881 | 0.769 | 0.783 | -7.42 | 5.72 | 8.22 | 0.915 | 0.781 | 0.85 | 6.91 | 7.03 | 6.04 | 0.89 | 0.703 | 0.779 | -7.87 | 8.22 | 8.52 | Very Poor_Mixed | 1721.9 | 1975.6 | 1.147 | 0.953 | 9.26 | 0.915 | 8.52 | 0.1504 | 0.6072 | 0.2368 | 0.3521 | 1 | 0.1024 | 0.2423 | 0.3697 | 0.3697 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1732 | 239 | 218.5 | 72.6 | 92 | 1 | 453.9 | 4191.1 | 58.8 | 21.7 | 88.9 | 90 | 80.6 | 96.1 | 39.9 | 13.8 | 9086 | 9203 | 9080.8 | 17526.8 | 18406.1 | 17614.8 | 1.929 | 2 | 1.94 | 0.514 | 0.525 | 0.505 | -2.14 | 2 | 2.87 | 0.515 | 0.526 | 0.5 | -2 | 2.27 | 2.1 | 0.515 | 0.527 | 0.5 | -2.63 | -2 | 2.39 | 0.5 | 0.5 | 0.5 | -2 | 2.47 | 2.11 | Poor_Thermal | 9080.8 | 17526.8 | 1.929 | 0.525 | 2.87 | 0.527 | 2.63 | 0.8728 | 0.9355 | 0.5489 | 0.9244 | 1 | 0.9098 | 0.9314 | 0.8866 | 0.8866 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1733 | 1594.8 | 945.5 | 135 | 181.3 | 30.6 | 1246.9 | 8514.6 | 34 | 45.2 | 105.6 | 107.2 | 93.8 | 116.1 | 43.6 | 32.2 | 1772.9 | 1346.6 | 2569 | 2088 | 1548.7 | 2926.3 | 1.178 | 1.15 | 1.139 | 0.947 | 0.946 | 0.939 | 8.95 | 9.31 | 8.83 | 0.865 | 0.936 | 0.741 | 9.07 | 7.36 | 6.73 | 0.74 | 0.804 | 0.866 | -7.13 | -5.78 | -9.27 | 0.908 | 0.819 | 0.871 | -8.56 | -5.65 | 7.27 | Very Poor_Mixed | 1346.6 | 1548.7 | 1.139 | 0.947 | 9.31 | 0.936 | 9.27 | 0.1042 | 0.628 | 0.1411 | 0.3137 | 1 | 0.0852 | 0.2186 | 0.3425 | 0.3425 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1734 | 1648 | 891.3 | 144 | 175.1 | 30.1 | 1295.7 | 8024.6 | 53.8 | 58.3 | 80.1 | 83.4 | 75.6 | 86 | 37.2 | 18.5 | 7678.6 | 9941.2 | 8971.7 | 12879.1 | 19348.2 | 16408.7 | 1.677 | 1.946 | 1.829 | 0.569 | 0.521 | 0.542 | 3.02 | 2.24 | 3.16 | 0.595 | 0.561 | 0.562 | 2.91 | 2.3 | 2.16 | 0.587 | 0.506 | 0.554 | 3.32 | 2.96 | 2.86 | 0.581 | 0.618 | 0.63 | 3.2 | 3.08 | 3.08 | Critical_DGA | 7678.6 | 12879.1 | 1.677 | 0.569 | 3.16 | 0.63 | 3.32 | 0.1076 | 0.5833 | 0.7631 | 0.7933 | 1 | 0.8138 | 0.7094 | 0.6145 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
1735 | 1640.2 | 916.7 | 137.2 | 187 | 34.3 | 1296.8 | 8861 | 32 | 47.1 | 109.3 | 109.3 | 99.1 | 119.2 | 46.7 | 32.8 | 1155.2 | 690 | 690 | 1245.3 | 1200 | 1200 | 1.078 | 1.739 | 1.739 | 0.969 | 0.99 | 0.942 | 9.46 | 9.55 | 9.58 | 0.865 | 0.926 | 0.755 | 6.53 | -7.08 | 6.76 | 0.818 | 0.962 | 0.813 | 9.06 | -9.73 | 7.53 | 0.898 | 0.812 | 0.749 | 8.3 | 6.82 | 6.98 | Very Poor_Mixed | 690 | 1200 | 1.078 | 0.99 | 9.58 | 0.962 | 9.73 | 0.0711 | 0.61 | 0.0421 | 0.2904 | 1 | 0.0449 | 0.2065 | 0.3132 | 0.3132 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1736 | 1678.5 | 837.3 | 147.9 | 184.6 | 32.2 | 1231.1 | 8122.8 | 30.6 | 49.4 | 106.6 | 105.1 | 93.8 | 114.8 | 44.1 | 32.9 | 2001.8 | 690 | 1274 | 2416.3 | 1200 | 1494.3 | 1.207 | 1.739 | 1.173 | 0.99 | 0.934 | 0.966 | 9.34 | 8.61 | -9.61 | 0.904 | 0.846 | 0.872 | 7 | 9.06 | 5.7 | 0.928 | 0.837 | 0.713 | 7.06 | -8.46 | 8.91 | 0.881 | 0.864 | 0.866 | 7.81 | 8.42 | -6.83 | Very Poor_Mixed | 690 | 1200 | 1.173 | 0.99 | 9.61 | 0.928 | 9.06 | 0.0966 | 0.5888 | 0.1501 | 0.2865 | 1 | 0.0646 | 0.1928 | 0.3279 | 0.3279 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1737 | 661.2 | 434.6 | 100.2 | 107.7 | 15.6 | 741 | 4857.2 | 50.2 | 30.6 | 88.9 | 87.1 | 80.8 | 94.8 | 39.8 | 24.2 | 6740.6 | 7047.7 | 6278.1 | 11193.1 | 11120.6 | 10586.7 | 1.661 | 1.578 | 1.686 | 0.695 | 0.713 | 0.683 | 4.71 | 5.73 | 5.55 | 0.646 | 0.678 | 0.635 | -4.23 | 3.99 | 2.77 | 0.59 | 0.61 | 0.604 | 3.44 | 4.38 | 3.1 | 0.659 | 0.624 | 0.618 | -5.11 | -3.28 | 4.84 | Poor_Mixed | 6278.1 | 10586.7 | 1.578 | 0.713 | 5.73 | 0.678 | 5.11 | 0.5088 | 0.7881 | 0.5744 | 0.6074 | 1 | 0.4736 | 0.5751 | 0.6394 | 0.6394 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1738 | 1365.3 | 783.4 | 128.5 | 170.8 | 28.2 | 1200.2 | 7277.6 | 35.2 | 44.4 | 105.1 | 105.9 | 93 | 112.5 | 43.8 | 32 | 2245.4 | 2246.8 | 3384.4 | 2682.5 | 2744.7 | 4207.9 | 1.195 | 1.222 | 1.243 | 0.911 | 0.891 | 0.936 | -8.46 | -8.47 | 8.05 | 0.762 | 0.766 | 0.76 | 4.88 | 6.97 | 5.82 | 0.721 | 0.89 | 0.687 | 5.8 | 7.13 | -4.91 | 0.806 | 0.845 | 0.75 | -6.69 | 7.5 | -7.58 | Very Poor_Mixed | 2245.4 | 2682.5 | 1.195 | 0.936 | 8.47 | 0.89 | 7.58 | 0.1845 | 0.6357 | 0.1721 | 0.3214 | 1 | 0.1424 | 0.3136 | 0.3921 | 0.3921 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1739 | 964.4 | 523.6 | 109 | 113.8 | 16.7 | 867 | 6028.1 | 42.7 | 35.3 | 91.2 | 94.3 | 81.6 | 97.3 | 38.5 | 24.1 | 5707.6 | 5980.4 | 5825.1 | 8980 | 9954.5 | 8806 | 1.573 | 1.665 | 1.512 | 0.684 | 0.735 | 0.722 | 5.9 | 6.11 | 5.37 | 0.654 | 0.692 | 0.706 | 5.13 | 4.85 | 3.16 | 0.734 | 0.713 | 0.629 | 4.89 | -4.26 | 4.99 | 0.599 | 0.728 | 0.654 | -5.38 | 5.13 | -4.56 | Poor_Mixed | 5707.6 | 8806 | 1.512 | 0.735 | 6.11 | 0.734 | 5.38 | 0.4268 | 0.731 | 0.5023 | 0.6108 | 1 | 0.4326 | 0.4803 | 0.5822 | 0.5822 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1740 | 989.4 | 579.8 | 105.6 | 123.2 | 17.8 | 867.2 | 5682.4 | 46.7 | 35.6 | 92 | 94.3 | 83 | 96.8 | 39.6 | 22.7 | 6345 | 6389 | 6865.4 | 10721.8 | 10891.3 | 10664.7 | 1.69 | 1.705 | 1.553 | 0.71 | 0.669 | 0.731 | 5.39 | 4.38 | -4.85 | 0.776 | 0.628 | 0.634 | 4.01 | 5.06 | 4.16 | 0.654 | 0.683 | 0.7 | 5.63 | 5.68 | 4.47 | 0.639 | 0.654 | 0.731 | 3.67 | -5.07 | -4.53 | Poor_Mixed | 6345 | 10664.7 | 1.553 | 0.731 | 5.39 | 0.776 | 5.68 | 0.4086 | 0.7276 | 0.4839 | 0.6585 | 1 | 0.4942 | 0.4819 | 0.5867 | 0.5867 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1741 | 932.7 | 596 | 112.1 | 122.9 | 20.6 | 883.2 | 5343.4 | 48.1 | 32.7 | 89.2 | 91.1 | 80.6 | 95.7 | 38.7 | 24.2 | 5067.9 | 4454.9 | 5697.1 | 7463.5 | 6693.9 | 8972 | 1.473 | 1.503 | 1.575 | 0.737 | 0.718 | 0.673 | -5.35 | 5.72 | -5.24 | 0.655 | 0.707 | 0.686 | 5.77 | 5.25 | 4.44 | 0.699 | 0.612 | 0.662 | 4.54 | 5.45 | -3.51 | 0.712 | 0.629 | 0.647 | 5.92 | -3.81 | 3.61 | Poor_Mixed | 4454.9 | 6693.9 | 1.473 | 0.737 | 5.72 | 0.712 | 5.92 | 0.3916 | 0.7617 | 0.5491 | 0.6074 | 1 | 0.4566 | 0.4935 | 0.5873 | 0.5873 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1742 | 1240.8 | 779.9 | 123.7 | 168.8 | 33 | 1166.3 | 7128.7 | 34.4 | 45.3 | 101.8 | 102.5 | 90.6 | 112.9 | 44.6 | 30.8 | 1893.3 | 2424.6 | 1960.4 | 2009.8 | 2739.4 | 2398.2 | 1.062 | 1.13 | 1.223 | 0.872 | 0.887 | 0.866 | 7.03 | -7.85 | -7.85 | 0.857 | 0.875 | 0.802 | 6.48 | 7.34 | 6.39 | 0.766 | 0.81 | 0.839 | -6.54 | -8.05 | 8.57 | 0.802 | 0.766 | 0.754 | 5.51 | 6.08 | 7.43 | Very Poor_Mixed | 1893.3 | 2009.8 | 1.062 | 0.887 | 7.85 | 0.875 | 8.57 | 0.1831 | 0.627 | 0.2156 | 0.3673 | 1 | 0.2077 | 0.2618 | 0.3972 | 0.3972 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1743 | 768.9 | 497.8 | 97.8 | 106.8 | 12.2 | 852.5 | 4737.3 | 57.5 | 22.7 | 75.6 | 76.8 | 70 | 80.4 | 36 | 13.1 | 9207.7 | 9967.1 | 10000 | 18004.6 | 19397.2 | 20000 | 1.955 | 1.946 | 2 | 0.561 | 0.582 | 0.557 | 3.18 | 2.33 | -3.37 | 0.564 | 0.57 | 0.555 | 2.91 | 2.31 | 2.41 | 0.564 | 0.532 | 0.534 | 2.88 | 2.58 | -2.91 | 0.569 | 0.591 | 0.522 | 3.34 | 2.13 | -2.45 | Fair_DGA | 9207.7 | 18004.6 | 1.946 | 0.582 | 3.37 | 0.591 | 3.34 | 0.5071 | 0.9129 | 0.9553 | 0.9414 | 1 | 0.7653 | 0.7552 | 0.782 | 0.782 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1744 | 1408.4 | 835.5 | 128.1 | 169.3 | 31.6 | 1158.7 | 7731.3 | 36.1 | 45.2 | 100.7 | 103.2 | 90.4 | 110.3 | 43.7 | 28.4 | 1663.3 | 2502 | 2036.6 | 1840.1 | 2861.4 | 2379 | 1.106 | 1.144 | 1.168 | 0.866 | 0.964 | 0.941 | 7.67 | -9 | -8.38 | 0.795 | 0.736 | 0.77 | 7.14 | 7.25 | 8.1 | 0.898 | 0.827 | 0.761 | 7.43 | 8.69 | -8.54 | 0.766 | 0.923 | 0.684 | -9 | 6.89 | 6.23 | Very Poor_Mixed | 1663.3 | 1840.1 | 1.106 | 0.964 | 9 | 0.923 | 9 | 0.1605 | 0.628 | 0.2387 | 0.4572 | 1 | 0.1342 | 0.2514 | 0.3862 | 0.3862 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1745 | 1379.9 | 921.5 | 136.2 | 165.6 | 31.4 | 1219.9 | 7713.3 | 34.7 | 43.8 | 101.1 | 100.5 | 89.3 | 108.8 | 43.5 | 31.4 | 2689.8 | 3058.8 | 2274.9 | 3254.3 | 3775.9 | 2717.1 | 1.21 | 1.234 | 1.194 | 0.874 | 0.867 | 0.902 | -8 | 8.02 | 8.07 | 0.935 | 0.852 | 0.759 | -4.78 | -8.05 | 8.17 | 0.868 | 0.89 | 0.839 | -8.98 | 7.55 | 4.85 | 0.759 | 0.894 | 0.83 | -6.63 | 5.17 | 5.75 | Very Poor_Mixed | 2274.9 | 2717.1 | 1.194 | 0.902 | 8.07 | 0.935 | 8.98 | 0.1443 | 0.6415 | 0.2671 | 0.3444 | 1 | 0.1799 | 0.236 | 0.3847 | 0.3847 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1746 | 1371.5 | 811.1 | 131.9 | 172.6 | 34.3 | 1194.6 | 7294.7 | 35.5 | 42.9 | 103.9 | 100.7 | 91.7 | 111.7 | 44.2 | 31.3 | 2191.8 | 2349.3 | 4075 | 2698.2 | 2903.8 | 5777.7 | 1.231 | 1.236 | 1.418 | 0.91 | 0.901 | 0.945 | -8.11 | 8.52 | 8.86 | 0.902 | 0.834 | 0.743 | -6.21 | 6.14 | 5.65 | 0.749 | 0.926 | 0.719 | 6.5 | 7.13 | 8.54 | 0.794 | 0.846 | 0.75 | 8.17 | 8.62 | 6.2 | Very Poor_Mixed | 2191.8 | 2698.2 | 1.231 | 0.945 | 8.86 | 0.926 | 8.62 | 0.1497 | 0.6504 | 0.2167 | 0.3483 | 1 | 0.1296 | 0.2623 | 0.3799 | 0.3799 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1747 | 269.2 | 260 | 81.3 | 65.3 | 2.4 | 412.4 | 3707.9 | 54.6 | 24.3 | 79.5 | 86.8 | 74.8 | 88.5 | 37 | 15.3 | 9456.7 | 8314.8 | 8758.3 | 17907.6 | 14835.4 | 16689.2 | 1.894 | 1.784 | 1.906 | 0.743 | 0.786 | 0.819 | 6.58 | 6.84 | 7.53 | 0.505 | 0.529 | 0.5 | 2.19 | -3.29 | 3.12 | 0.577 | 0.584 | 0.501 | 2.29 | 2.67 | 2.12 | 0.543 | 0.564 | 0.522 | 3.19 | 2 | 2.78 | Poor_Winding_TD_Cap | 8314.8 | 14835.4 | 1.784 | 0.819 | 7.53 | 0.584 | 3.29 | 0.8274 | 0.8821 | 0.7381 | 0.8855 | 1 | 0.3097 | 0.822 | 0.7821 | 0.7821 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
1748 | 100 | 120 | 66.7 | 51.8 | 2.4 | 375.9 | 2500 | 60 | 20.4 | 76.2 | 76.6 | 70.6 | 84.3 | 35 | 11.7 | 8922.5 | 10000 | 9561 | 17193.7 | 20000 | 19122 | 1.927 | 2 | 2 | 0.5 | 0.5 | 0.512 | 2.33 | -2.25 | 2 | 0.528 | 0.572 | 0.522 | 2 | -3.25 | 2.47 | 0.525 | 0.526 | 0.545 | 2.87 | 2.18 | 3.49 | 0.534 | 0.517 | 0.5 | 2.17 | 2.39 | 2.54 | Good_Mixed | 8922.5 | 17193.7 | 1.927 | 0.512 | 2.33 | 0.572 | 3.49 | 0.9101 | 0.9748 | 0.9251 | 0.9724 | 1 | 0.9625 | 0.8272 | 0.9293 | 0.9293 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1749 | 374.4 | 255.4 | 73 | 64.3 | 1 | 433.6 | 3582.1 | 57.1 | 20.9 | 78.3 | 78.8 | 72.9 | 86.3 | 36.1 | 11.4 | 8310 | 8801.2 | 8753.6 | 15510.6 | 16776.2 | 16521 | 1.866 | 1.906 | 1.887 | 0.566 | 0.563 | 0.562 | 2.54 | 2 | 2.33 | 0.557 | 0.569 | 0.5 | -2.96 | -3.09 | 2.81 | 0.537 | 0.568 | 0.586 | -2.81 | 2.51 | 2.73 | 0.539 | 0.773 | 0.542 | 2.59 | 6.56 | 2.78 | Poor_Bushing_TD_Cap | 8310 | 15510.6 | 1.866 | 0.566 | 2.54 | 0.773 | 6.56 | 0.8976 | 0.9574 | 0.8435 | 0.9783 | 1 | 0.8185 | 0.7187 | 0.8765 | 0.8765 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_TV_Y_TanDelta_pct
1750 | 126.9 | 120 | 65 | 66.2 | 2.4 | 350 | 2589.5 | 56.6 | 21.6 | 75 | 76.3 | 70.5 | 80.7 | 35 | 12.9 | 9457.8 | 9802 | 10000 | 18634.6 | 19192.9 | 19588.5 | 1.97 | 1.958 | 1.959 | 0.561 | 0.524 | 0.597 | -3.15 | 2.13 | -2.69 | 0.5 | 0.518 | 0.548 | 2.36 | 2.37 | 2 | 0.505 | 0.519 | 0.543 | 3.13 | 3.1 | 2.61 | 0.535 | 0.546 | 0.566 | 2.18 | 2.35 | 2.14 | Good_Mixed | 9457.8 | 18634.6 | 1.958 | 0.597 | 3.15 | 0.566 | 3.13 | 0.8894 | 0.938 | 0.9678 | 0.9461 | 1 | 0.8001 | 0.833 | 0.901 | 0.901 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1751 | 963.5 | 531 | 105.3 | 131.1 | 22 | 921.1 | 5240.1 | 46.2 | 34.1 | 92.9 | 89 | 82.1 | 97.5 | 40.1 | 24.8 | 4917.8 | 4844 | 5710.6 | 7475.2 | 7390.4 | 8632.6 | 1.52 | 1.526 | 1.512 | 0.769 | 0.68 | 0.735 | 5.78 | -4.83 | 5.48 | 0.678 | 0.697 | 0.641 | 4.54 | 5.78 | 4.66 | 0.644 | 0.655 | 0.646 | 4.14 | 4.01 | -4.51 | 0.648 | 0.634 | 0.723 | -4.18 | 4.43 | 5.47 | Poor_Mixed | 4844 | 7390.4 | 1.512 | 0.769 | 5.78 | 0.723 | 5.78 | 0.3823 | 0.7449 | 0.5114 | 0.5865 | 1 | 0.4446 | 0.5006 | 0.5778 | 0.5778 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1752 | 1388.3 | 782.4 | 120.6 | 151.1 | 25.6 | 2641.5 | 15697 | 36.5 | 43.5 | 99.7 | 102.8 | 92.1 | 108.9 | 43.9 | 33.9 | 2273.9 | 4080.6 | 1802 | 2773.1 | 5354.9 | 2224.8 | 1.22 | 1.312 | 1.235 | 0.862 | 0.852 | 0.887 | 7.37 | 7.24 | 7.85 | 0.726 | 0.665 | 0.775 | 5.78 | 6.75 | 7.71 | 0.731 | 0.785 | 0.864 | -7.39 | -5.9 | 6.39 | 0.854 | 0.833 | 0.726 | 6.12 | 8.44 | 7.5 | Critical_Mixed | 1802 | 2224.8 | 1.22 | 0.887 | 7.85 | 0.864 | 8.44 | 0.1606 | 0.6445 | 0.2426 | 0.2473 | 1 | 0.2182 | 0.2997 | 0.3986 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | C2H2
1753 | 1085.3 | 641.7 | 114.9 | 131.6 | 19.4 | 836.6 | 6399.1 | 54.6 | 24.5 | 79 | 79.6 | 73.8 | 86.4 | 36 | 12.8 | 8507.1 | 10000 | 8075.3 | 15487.1 | 19428.1 | 14784.2 | 1.82 | 1.943 | 1.831 | 0.544 | 0.564 | 0.64 | -2.62 | 3.32 | 4.13 | 0.505 | 0.518 | 0.543 | 3.27 | 3.06 | 2.51 | 0.551 | 0.503 | 0.548 | 2.41 | 2.53 | -2.53 | 0.508 | 0.559 | 0.518 | 2.64 | -2 | 2.21 | Poor_DGA | 8075.3 | 14784.2 | 1.82 | 0.64 | 4.13 | 0.559 | 3.27 | 0.3657 | 0.8786 | 0.8221 | 0.9484 | 1 | 0.7219 | 0.8335 | 0.7376 | 0.7376 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1754 | 1766 | 944.1 | 145.7 | 197 | 34.3 | 1346.1 | 8681.8 | 57.6 | 21.4 | 81.2 | 82.1 | 75.1 | 88.1 | 37.6 | 14.3 | 8866.5 | 8969 | 9235.2 | 16993.8 | 16788.9 | 17592.1 | 1.917 | 1.872 | 1.905 | 0.662 | 0.57 | 0.671 | 4.73 | 3.73 | 3.97 | 0.636 | 0.571 | 0.593 | 20.72 | 3.58 | 2.98 | 0.552 | 0.581 | 0.576 | 3.68 | 2.4 | 4.25 | 0.63 | 0.64 | 0.61 | 3.46 | -3.72 | 2.98 | Critical_DGA | 8866.5 | 16788.9 | 1.872 | 0.671 | 4.73 | 0.64 | 20.72 | 0.0414 | 0.9432 | 0.755 | 0.9118 | 1 | 0.6093 | 0.6186 | 0.6013 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_R_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
1755 | 1560.5 | 924.6 | 142.4 | 185.6 | 32.7 | 1257.3 | 8380.2 | 56.3 | 24.2 | 122.3 | 83.8 | 78 | 90.1 | 36.9 | 18.8 | 7282 | 7181.4 | 7577.3 | 12579.9 | 13199.6 | 13200.2 | 1.728 | 1.838 | 1.742 | 0.619 | 0.584 | 0.593 | 4.45 | -3.54 | 3.93 | 0.556 | 0.5 | 0.517 | 2.47 | -2 | 2 | 0.515 | 0.528 | 0.539 | 3 | -2.57 | 2.27 | 0.511 | 0.514 | 0.511 | 2.82 | 2.33 | 2.95 | Critical_DGA | 7181.4 | 12579.9 | 1.728 | 0.619 | 4.45 | 0.556 | 3 | 0.0907 | 0.8839 | 0.5329 | 0.7841 | 1 | 0.6572 | 0.8582 | 0.6277 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature | C2H2
1756 | 882.5 | 535.8 | 107 | 129.4 | 18.9 | 824 | 5123.8 | 46 | 35.1 | 88.7 | 93 | 82.2 | 96.4 | 39.6 | 24.3 | 5308.7 | 5002.9 | 4491.1 | 8068 | 7516.1 | 6592.9 | 1.52 | 1.502 | 1.468 | 0.737 | 0.69 | 0.752 | 6.24 | 4.84 | 6.45 | 0.61 | 0.599 | 0.608 | -4.93 | -3.73 | 4.69 | 0.617 | 0.62 | 0.602 | 4.42 | -5.11 | 5.17 | 0.679 | 0.664 | 0.607 | 4.33 | 4.54 | 4.83 | Poor_Mixed | 4491.1 | 6592.9 | 1.468 | 0.752 | 6.45 | 0.679 | 5.17 | 0.4194 | 0.7333 | 0.5209 | 0.6039 | 1 | 0.4192 | 0.555 | 0.5937 | 0.5937 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1757 | 232.7 | 195 | 82.1 | 66.5 | 2 | 470.1 | 3208.9 | 59 | 22.2 | 78.8 | 80.4 | 73.2 | 84.2 | 35.8 | 17.7 | 4858.3 | 5524.3 | 5428.5 | 7406.2 | 8022.1 | 8258.6 | 1.524 | 1.452 | 1.521 | 0.598 | 0.596 | 0.618 | 3.9 | 2.64 | -3.7 | 0.572 | 0.577 | 0.547 | 3.55 | 3.06 | 3.09 | 0.523 | 0.565 | 0.536 | 3.56 | -2.28 | 2.79 | 0.522 | 0.521 | 0.53 | 2.76 | 2.71 | 2.18 | Poor_IR_PI | 4858.3 | 7406.2 | 1.452 | 0.618 | 3.9 | 0.577 | 3.56 | 0.8408 | 0.9238 | 0.8338 | 0.8173 | 1 | 0.6862 | 0.7718 | 0.8403 | 0.8403 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1758 | 1637.6 | 875.1 | 137.3 | 171.2 | 34.3 | 1309.7 | 7860.9 | 31.9 | 46.6 | 108.2 | 105.5 | 95.3 | 119.2 | 44.1 | 32.7 | 1391.1 | 1616.6 | 1090.1 | 1602.1 | 1959.6 | 1227.1 | 1.152 | 1.212 | 1.126 | 0.877 | 0.906 | 0.904 | 7.54 | 8.16 | -8.61 | 0.778 | 0.781 | 0.778 | 9.46 | 9.04 | 7.44 | 0.805 | 0.914 | 0.887 | -8.45 | 8.08 | 8.68 | 0.904 | 0.886 | 0.981 | 6.05 | 6.53 | -8.45 | Very Poor_Mixed | 1090.1 | 1227.1 | 1.126 | 0.906 | 8.61 | 0.981 | 9.46 | 0.1007 | 0.6147 | 0.1088 | 0.2943 | 1 | 0.1658 | 0.1827 | 0.3406 | 0.3406 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1759 | 291 | 195.7 | 71.9 | 157.8 | 2.5 | 505.7 | 2500 | 52.7 | 28 | 109.3 | 109.3 | 94.9 | 117.6 | 45 | 15.5 | 7721.7 | 8239.3 | 9003.5 | 13643.7 | 15036.1 | 16684.2 | 1.767 | 1.825 | 1.853 | 0.615 | 0.607 | 0.596 | 4.22 | 3.82 | 15.45 | 0.583 | 0.581 | 0.591 | 3.21 | 4.03 | 2.96 | 0.612 | 0.587 | 0.547 | 3.01 | 3.52 | 3.23 | 0.613 | 0.598 | 0.6 | -3.08 | 2.82 | 2.75 | Critical_Thermal | 7721.7 | 13643.7 | 1.767 | 0.615 | 15.45 | 0.613 | 4.03 | 0.7312 | 0.8235 | 0.0857 | 0.88 | 1 | 0.5381 | 0.6644 | 0.6891 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H4
1760 | 1640.3 | 971.6 | 141.7 | 193.4 | 33.3 | 1379 | 8250.3 | 16.4 | 24.4 | 80.4 | 80 | 74.1 | 84.2 | 36.6 | 16.5 | 7510.5 | 6956.9 | 8236.5 | 12212.2 | 11516.4 | 14410.3 | 1.626 | 1.655 | 1.75 | 0.608 | 0.576 | 0.671 | 4.54 | 3.28 | 4.61 | 0.578 | 0.629 | 0.592 | 3.07 | 3.32 | 3.2 | 0.594 | 0.589 | 0.655 | 3.48 | 2.99 | 3.1 | 0.539 | 0.64 | 0.533 | 3.2 | 3.83 | 3.28 | Critical_DGA | 6956.9 | 11516.4 | 1.626 | 0.671 | 4.61 | 0.655 | 3.83 | 0.06 | 0.297 | 0.8118 | 0.8522 | 1 | 0.6266 | 0.6585 | 0.5407 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
1761 | 159.4 | 127.4 | 68.9 | 103.8 | 1 | 350 | 2500 | 54.5 | 24.9 | 99.2 | 98.5 | 89.4 | 110.5 | 43 | 12.6 | 8814.3 | 9708.8 | 9189.7 | 15960.4 | 18729.8 | 18379.4 | 1.811 | 1.929 | 2 | 0.533 | 0.571 | 0.599 | -3.47 | 2.58 | -3.62 | 0.522 | 0.543 | 0.521 | 2.49 | 2.25 | 2.16 | 0.504 | 0.536 | 0.5 | 2.55 | 2.01 | -2.46 | 0.5 | 0.5 | 0.532 | 2.55 | 2.92 | 2.17 | Poor_Thermal | 8814.3 | 15960.4 | 1.811 | 0.599 | 3.62 | 0.543 | 2.92 | 0.915 | 0.8717 | 0.2844 | 0.953 | 1 | 0.749 | 0.8854 | 0.8337 | 0.8337 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_HV
1762 | 100 | 135.8 | 69.6 | 50 | 2.2 | 420.1 | 3014.6 | 60 | 21.1 | 76.7 | 75 | 71.1 | 80 | 35 | 13.4 | 9683.3 | 9620.4 | 9592.2 | 18155.5 | 18934.4 | 18509.4 | 1.875 | 1.968 | 1.93 | 0.503 | 0.547 | 0.53 | 2.21 | 2.34 | 2.97 | 0.509 | 0.535 | 0.511 | 2.21 | 2 | 2.35 | 0.509 | 0.545 | 0.55 | 2.83 | -2.38 | 2 | 0.5 | 0.509 | 0.501 | 2 | -2.28 | 2 | Good_Mixed | 9592.2 | 18155.5 | 1.875 | 0.547 | 2.97 | 0.55 | 2.83 | 0.9064 | 0.9514 | 0.9599 | 0.9342 | 1 | 0.8721 | 0.8865 | 0.9252 | 0.9252 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1763 | 828.8 | 507.6 | 98.4 | 115.7 | 16.9 | 839.1 | 5789.2 | 46 | 33.6 | 89.1 | 87.2 | 81.3 | 92.5 | 40.4 | 22.9 | 6465.1 | 4737.5 | 5799.9 | 10160.8 | 6826.2 | 8703.4 | 1.572 | 1.441 | 1.501 | 0.726 | 0.754 | 0.812 | 6.07 | 6.26 | 6.6 | 0.632 | 0.653 | 0.712 | 3.7 | 3.33 | 4.74 | 0.65 | 0.69 | 0.634 | 4.09 | 4.65 | 4.51 | 0.705 | 0.661 | 0.672 | -4.87 | -4.09 | 4.04 | Poor_Mixed | 4737.5 | 6826.2 | 1.441 | 0.812 | 6.6 | 0.712 | 4.87 | 0.4497 | 0.7509 | 0.5767 | 0.6518 | 1 | 0.3612 | 0.5101 | 0.5952 | 0.5952 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1764 | 1489.4 | 901.4 | 140.5 | 186.5 | 33.8 | 1236.1 | 8147.3 | 34.5 | 47.1 | 104.4 | 103.8 | 93.7 | 114.9 | 43.9 | 33.3 | 2345.5 | 1580.6 | 1423.8 | 2736.3 | 1659.6 | 1557.3 | 1.167 | 1.05 | 1.094 | 0.955 | 0.956 | 0.93 | 9.18 | -9.84 | -9.16 | 0.784 | 0.79 | 0.896 | 6.26 | 8.19 | -7.23 | 0.712 | 0.883 | 0.787 | 8.61 | 9.01 | 6.95 | 0.838 | 0.827 | 0.895 | 6.14 | -6.46 | 8.51 | Very Poor_Mixed | 1423.8 | 1557.3 | 1.05 | 0.956 | 9.84 | 0.896 | 9.01 | 0.0997 | 0.61 | 0.1711 | 0.2709 | 1 | 0.065 | 0.2302 | 0.3393 | 0.3393 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1765 | 1045.2 | 610.7 | 110.9 | 122.8 | 17.3 | 810.1 | 5699.3 | 44 | 35.2 | 93.4 | 99 | 86.9 | 103.4 | 41.2 | 26.7 | 4996.9 | 5456.6 | 5117.5 | 7454.9 | 8055.6 | 7656.9 | 1.492 | 1.476 | 1.496 | 0.761 | 0.738 | 0.712 | 6.13 | 5.89 | 5.75 | 0.73 | 0.607 | 0.701 | -3.91 | 6.71 | -4.51 | 0.637 | 0.64 | 0.699 | 5.81 | 4.39 | 4.19 | 0.759 | 0.697 | 0.682 | 4.39 | -4.6 | 4.84 | Poor_Mixed | 4996.9 | 7454.9 | 1.476 | 0.761 | 6.13 | 0.759 | 6.71 | 0.4075 | 0.7322 | 0.3793 | 0.5192 | 1 | 0.4046 | 0.4705 | 0.5549 | 0.5549 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
1766 | 1118.7 | 480.7 | 110.3 | 129.2 | 17 | 840.5 | 5626.4 | 55.2 | 23.4 | 75 | 76.5 | 70 | 80.6 | 35 | 13.6 | 9709.9 | 8802.2 | 8949.5 | 19419.9 | 16253.2 | 16689.6 | 2 | 1.846 | 1.865 | 0.566 | 0.546 | 0.541 | 2.52 | 2.67 | 3.14 | 0.544 | 0.581 | 0.569 | 2.55 | 2.77 | 2.41 | 0.56 | 0.526 | 0.539 | 2.72 | -2.83 | 2.37 | 0.5 | 0.555 | 0.575 | -2.61 | 2.92 | 2.14 | Poor_DGA | 8802.2 | 16253.2 | 1.846 | 0.566 | 3.14 | 0.581 | 2.92 | 0.4097 | 0.8988 | 0.9735 | 0.9294 | 1 | 0.801 | 0.7789 | 0.7664 | 0.7664 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1767 | 593.2 | 392 | 86.6 | 95 | 48.9 | 725.3 | 4804.9 | 30.6 | 48.1 | 82.6 | 82.8 | 72.9 | 84.9 | 37.5 | 15.6 | 3925.4 | 5530.4 | 5978.8 | 5675.3 | 8443 | 9047.3 | 1.446 | 1.527 | 1.513 | 0.69 | 0.667 | 0.662 | -5.06 | 5.17 | 4.81 | 0.537 | 0.584 | 0.58 | 3.16 | 2.87 | 3.05 | 0.51 | 0.533 | 0.581 | -3 | -2.77 | 3.42 | 0.558 | 0.55 | 0.53 | 3.1 | 3.21 | 2.67 | Critical_Oil | 3925.4 | 5675.3 | 1.446 | 0.69 | 5.17 | 0.584 | 3.42 | 0.4433 | 0.6007 | 0.7724 | 0.8773 | 1 | 0.5143 | 0.7487 | 0.6708 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1768 | 707.7 | 343.2 | 92 | 86.9 | 1 | 559.5 | 4045.7 | 57.6 | 24.5 | 85 | 84.9 | 76.3 | 91.9 | 39.2 | 14.5 | 2721.5 | 2127.3 | 2204.9 | 3068.1 | 2274.8 | 1986.8 | 1.127 | 1.069 | 0.901 | 0.703 | 0.66 | 0.716 | -5.58 | -4.53 | 5.56 | 0.553 | 0.571 | 0.54 | 3.1 | 2.46 | 2.79 | 0.516 | 0.57 | 0.569 | 2.54 | 3.54 | 2.84 | 0.513 | 0.538 | 0.541 | 2.71 | -3.12 | 3.15 | Critical_IR_PI | 2127.3 | 1986.8 | 0.901 | 0.716 | 5.58 | 0.571 | 3.54 | 0.7945 | 0.8786 | 0.6667 | 0.9067 | 0.8125 | 0.4839 | 0.7657 | 0.7516 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_TV
1769 | 968.5 | 602.5 | 111.6 | 128.4 | 18.3 | 819.3 | 5697.3 | 58.3 | 24.2 | 77.2 | 75.6 | 72.4 | 81.2 | 35.8 | 14.6 | 8803.6 | 8169 | 9252.6 | 17185.2 | 14724.2 | 17460.1 | 1.952 | 1.802 | 1.887 | 0.582 | 0.567 | 0.512 | 3.04 | 3.16 | 2 | 0.5 | 0.553 | 0.519 | 2.22 | 2.14 | 2 | 0.562 | 0.507 | 0.549 | 2.78 | 2.11 | 2.28 | 0.562 | 0.507 | 0.534 | 2.8 | 2.91 | 2.06 | Poor_DGA | 8169 | 14724.2 | 1.802 | 0.582 | 3.16 | 0.562 | 2.91 | 0.4011 | 0.8839 | 0.9213 | 0.904 | 1 | 0.8098 | 0.8373 | 0.7678 | 0.7678 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1770 | 1473.2 | 874.1 | 132.2 | 166.2 | 30.5 | 1269.7 | 7681.1 | 35.9 | 44.2 | 105.7 | 103.4 | 91.2 | 112.8 | 43.4 | 30.3 | 2976.1 | 2360.4 | 3864.3 | 3850.3 | 2667.6 | 5151.2 | 1.294 | 1.13 | 1.333 | 0.934 | 0.917 | 0.923 | 8.97 | -8.7 | -8.66 | 0.728 | 0.809 | 0.842 | 5.4 | 8.28 | 7.34 | 0.842 | 0.794 | 0.892 | 7.83 | 6.34 | -5.48 | 0.748 | 0.901 | 0.785 | 6.41 | -7.34 | 7.57 | Very Poor_Mixed | 2360.4 | 2667.6 | 1.13 | 0.934 | 8.97 | 0.901 | 8.28 | 0.1443 | 0.6376 | 0.1943 | 0.3863 | 1 | 0.1111 | 0.257 | 0.3731 | 0.3731 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1771 | 870.7 | 522.7 | 102.8 | 127 | 19 | 799.6 | 5402.6 | 46.9 | 32.1 | 92.1 | 92.4 | 84.9 | 98.5 | 40.6 | 26.4 | 5741.6 | 5275.1 | 5466.8 | 8838.4 | 7785.4 | 8438.4 | 1.539 | 1.476 | 1.544 | 0.753 | 0.773 | 0.783 | 5.35 | 6.09 | 6.04 | 0.675 | 0.746 | 0.676 | 5.8 | 6.42 | -5.63 | 0.684 | 0.644 | 0.679 | -4.1 | 4.98 | 3.67 | 0.739 | 0.702 | 0.645 | 4.91 | -4.01 | 4.95 | Poor_Mixed | 5275.1 | 7785.4 | 1.476 | 0.783 | 6.09 | 0.746 | 6.42 | 0.4267 | 0.7691 | 0.4685 | 0.5299 | 1 | 0.3823 | 0.4593 | 0.5685 | 0.5685 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1772 | 1420.1 | 832.8 | 133.6 | 171.4 | 34.1 | 1203 | 7314.3 | 34.6 | 46.6 | 100.1 | 104 | 92.1 | 112.8 | 43.2 | 30.7 | 2986.4 | 1599.5 | 1384 | 3815.5 | 1750.9 | 1703.9 | 1.278 | 1.095 | 1.231 | 0.893 | 0.946 | 0.844 | 8.46 | -8.83 | 8.42 | 0.889 | 0.856 | 0.741 | 7.7 | 5.44 | 6.38 | 0.843 | 0.706 | 0.854 | 6.14 | 6.69 | 7.67 | 0.753 | 0.874 | 0.672 | 6.78 | -6.54 | 6.34 | Very Poor_Mixed | 1384 | 1703.9 | 1.095 | 0.946 | 8.83 | 0.889 | 7.7 | 0.1431 | 0.6147 | 0.219 | 0.3711 | 1 | 0.1433 | 0.2839 | 0.3812 | 0.3812 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1773 | 915.2 | 551.8 | 97.4 | 109.8 | 15.5 | 883 | 5134.4 | 46.9 | 33.3 | 89.7 | 93.4 | 80.7 | 100.9 | 40.2 | 26.5 | 5398.9 | 5104.4 | 5385.5 | 8167.1 | 7101.9 | 8004.2 | 1.513 | 1.391 | 1.486 | 0.654 | 0.761 | 0.699 | 4.08 | 5.17 | 5.13 | 0.674 | 0.684 | 0.738 | 3.55 | 4.54 | 4.35 | 0.671 | 0.572 | 0.618 | 3.27 | 3.85 | 3.64 | 0.618 | 0.636 | 0.655 | 4.66 | -5.28 | -4.39 | Poor_Mixed | 5104.4 | 7101.9 | 1.391 | 0.761 | 5.17 | 0.738 | 5.28 | 0.4552 | 0.7544 | 0.495 | 0.5264 | 1 | 0.4989 | 0.5359 | 0.6064 | 0.6064 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1774 | 947 | 497.1 | 108.5 | 129 | 18.5 | 866.7 | 5843.6 | 44.6 | 34.7 | 89.2 | 93.9 | 79.7 | 94.4 | 40.1 | 24.2 | 5961.7 | 5392 | 5504.5 | 9535.7 | 8271.7 | 8808.5 | 1.599 | 1.534 | 1.6 | 0.708 | 0.753 | 0.758 | 5.18 | -5.79 | 5.45 | 0.679 | 0.665 | 0.69 | -4.62 | 4.14 | -4.43 | 0.624 | 0.682 | 0.67 | 4.25 | -3.39 | 4.37 | 0.607 | 0.684 | 0.682 | 4.34 | 3.51 | 4.47 | Poor_Mixed | 5392 | 8271.7 | 1.534 | 0.758 | 5.79 | 0.69 | 4.62 | 0.4076 | 0.7379 | 0.535 | 0.6074 | 1 | 0.4274 | 0.5161 | 0.587 | 0.587 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1775 | 1636.3 | 822.5 | 131.6 | 177.5 | 30.2 | 1241.6 | 7708.2 | 36.5 | 43.5 | 104.4 | 100.4 | 92.6 | 112.1 | 43.2 | 32.2 | 2270.3 | 1959.4 | 1608.7 | 2510 | 2379.8 | 1689.1 | 1.106 | 1.215 | 1.05 | 0.937 | 0.912 | 0.979 | 8.51 | 8.11 | 9.26 | 0.835 | 0.866 | 0.872 | -5.33 | 7.12 | 6.46 | 0.773 | 0.883 | 0.753 | 8.43 | 6.37 | -6.55 | 0.824 | 0.952 | 0.748 | 6.93 | 6.13 | 7.83 | Very Poor_Mixed | 1608.7 | 1689.1 | 1.05 | 0.979 | 9.26 | 0.952 | 8.43 | 0.1333 | 0.6445 | 0.2157 | 0.3137 | 1 | 0.1068 | 0.2432 | 0.3666 | 0.3666 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1776 | 100 | 147.6 | 70.1 | 59.1 | 1 | 397 | 2951.8 | 57 | 22.4 | 76.3 | 75.6 | 73.7 | 83.5 | 35 | 10.3 | 6435.4 | 6847.4 | 7076.8 | 10532.9 | 11127.8 | 12832.2 | 1.637 | 1.625 | 1.813 | 0.592 | 0.534 | 0.527 | 3.29 | -3 | 3.03 | 0.5 | 0.512 | 0.5 | 2 | 2.65 | 2 | 0.512 | 0.526 | 0.5 | 2 | 2.31 | -2 | 0.5 | 0.541 | 0.507 | 2.62 | 2.93 | 2.07 | Fair_IR_PI | 6435.4 | 10532.9 | 1.625 | 0.592 | 3.29 | 0.541 | 2.93 | 0.9609 | 0.9193 | 0.912 | 0.9968 | 1 | 0.7824 | 0.9196 | 0.9267 | 0.9267 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1777 | 297.4 | 273 | 74.8 | 64.6 | 1 | 495.6 | 3567.1 | 57 | 22.4 | 80.9 | 78.1 | 72 | 83.7 | 36.3 | 12.4 | 8991.7 | 10000 | 9910.5 | 17086.8 | 20000 | 19821 | 1.9 | 2 | 2 | 0.76 | 0.68 | 0.663 | -5.35 | 5.24 | -4.04 | 0.63 | 0.528 | 0.524 | 3.28 | -3.13 | 3.26 | 0.575 | 0.611 | 0.532 | 4.3 | 3.1 | 2.52 | 0.534 | 0.577 | 0.597 | 2.24 | -3.5 | -2.02 | Poor_Winding_TD_Cap | 8991.7 | 17086.8 | 1.9 | 0.76 | 5.35 | 0.63 | 4.3 | 0.8911 | 0.9193 | 0.8469 | 0.9575 | 1 | 0.4974 | 0.7206 | 0.825 | 0.825 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_HV_TanDelta_pct
1778 | 902.7 | 488.8 | 96.9 | 116.2 | 17.5 | 814.7 | 4977.8 | 46 | 34.6 | 92.5 | 94.4 | 82.4 | 98.9 | 40.5 | 26.9 | 5702.8 | 4919.7 | 5326.1 | 8709.4 | 7217.7 | 8077.2 | 1.527 | 1.467 | 1.517 | 0.724 | 0.693 | 0.737 | 4.94 | 5.94 | 5.67 | 0.658 | 0.678 | 0.608 | 5.71 | 4.02 | -3.55 | 0.625 | 0.581 | 0.707 | 5.61 | -4.63 | 4.54 | 0.64 | 0.683 | 0.634 | 4.38 | 3.84 | 4.7 | Poor_Mixed | 4919.7 | 7217.7 | 1.467 | 0.737 | 5.94 | 0.707 | 5.71 | 0.4542 | 0.7391 | 0.4676 | 0.512 | 1 | 0.4441 | 0.5277 | 0.5918 | 0.5918 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1779 | 1766 | 982.4 | 145.9 | 190.5 | 34.3 | 1379 | 8442 | 56.5 | 20.5 | 78.7 | 78 | 74 | 88.5 | 37 | 14.6 | 7023 | 6271.8 | 6668.5 | 12236.3 | 5721.9 | 11146.2 | 1.742 | 0.912 | 1.671 | 0.602 | 0.608 | 0.643 | 3.76 | 3.64 | 4.22 | 0.571 | 0.531 | 0.54 | 4.15 | 3.71 | 3.15 | 0.596 | 0.576 | 0.617 | 3.92 | 2.18 | 3.32 | 0.607 | 0.546 | 0.573 | 2.98 | 3.46 | 2.73 | Critical_DGA | 6271.8 | 5721.9 | 0.912 | 0.643 | 4.22 | 0.617 | 4.15 | 0.0421 | 0.9709 | 0.8227 | 0.904 | 0.8187 | 0.6407 | 0.6937 | 0.6001 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1780 | 1352.5 | 748.7 | 130 | 166.9 | 30 | 1197.1 | 6840.7 | 39.8 | 41.4 | 98.1 | 99.8 | 91.5 | 108.1 | 42.7 | 34.2 | 2696.7 | 2894.7 | 4119 | 3514 | 3616.4 | 2617.9 | 1.303 | 1.249 | 0.636 | 0.832 | 0.888 | 0.867 | 7.38 | -7.76 | 6.74 | 0.636 | 0.851 | 0.845 | -7.66 | -6.43 | 5.54 | 0.697 | 0.673 | 0.811 | 4.87 | 7.54 | 5.26 | 0.786 | 0.713 | 0.742 | -6.78 | 6.53 | 5.14 | Critical_Mixed | 2696.7 | 2617.9 | 0.636 | 0.888 | 7.76 | 0.851 | 7.66 | 0.1885 | 0.6655 | 0.2852 | 0.2355 | 0.8125 | 0.2319 | 0.3484 | 0.3925 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1781 | 894.7 | 550 | 104.5 | 112 | 17.2 | 806.9 | 5645.7 | 42.7 | 37 | 93.7 | 89 | 82.9 | 98.8 | 40.6 | 24.5 | 5516 | 4406.4 | 4901.7 | 8636.1 | 6410.5 | 7524.3 | 1.566 | 1.455 | 1.535 | 0.727 | 0.675 | 0.806 | 5.69 | 4.56 | -6.31 | 0.663 | 0.687 | 0.744 | -5.04 | 5.09 | -4.1 | 0.617 | 0.644 | 0.733 | 4.65 | -3.49 | -4.83 | 0.673 | 0.649 | 0.648 | 4.95 | 4.89 | 4.27 | Poor_Mixed | 4406.4 | 6410.5 | 1.455 | 0.806 | 6.31 | 0.744 | 5.09 | 0.4427 | 0.712 | 0.4916 | 0.597 | 1 | 0.4303 | 0.4905 | 0.5837 | 0.5837 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1782 | 947.3 | 571.3 | 103.4 | 126.9 | 24.4 | 885.2 | 5580.7 | 45.3 | 33.6 | 92.6 | 91 | 79.7 | 96.6 | 39.6 | 24.8 | 5813.6 | 4576 | 5118.4 | 8591.9 | 6511.7 | 7394.7 | 1.478 | 1.423 | 1.445 | 0.738 | 0.694 | 0.693 | 6.21 | 5.48 | -5.22 | 0.707 | 0.658 | 0.655 | 5.16 | -4.02 | -4.35 | 0.629 | 0.611 | 0.701 | -5.16 | 3.3 | -4.62 | 0.647 | 0.63 | 0.618 | 4.78 | -4.59 | -5.63 | Poor_Mixed | 4576 | 6511.7 | 1.423 | 0.738 | 6.21 | 0.707 | 5.63 | 0.3723 | 0.7509 | 0.5235 | 0.5865 | 1 | 0.4462 | 0.5178 | 0.5805 | 0.5805 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1783 | 1644.7 | 847.4 | 141.7 | 195.8 | 32.3 | 1280.7 | 7503.1 | 32.2 | 47.7 | 103.4 | 106.9 | 94.5 | 115.1 | 44.1 | 33 | 1634.8 | 1303 | 1498.6 | 1895.6 | 1458.8 | 1624.3 | 1.16 | 1.12 | 1.084 | 0.95 | 0.99 | 0.99 | 8.86 | -9.84 | 9.73 | 0.848 | 0.941 | 0.836 | 8.18 | -8.63 | 5.93 | 0.772 | 0.99 | 0.957 | 5.96 | -9.22 | -8.83 | 0.929 | 0.837 | 0.776 | 7.9 | 6.97 | -6.38 | Very Poor_Mixed | 1303 | 1458.8 | 1.084 | 0.99 | 9.84 | 0.99 | 9.22 | 0.0958 | 0.6044 | 0.1526 | 0.2826 | 1 | 0.0413 | 0.1812 | 0.3243 | 0.3243 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1784 | 495.9 | 329.9 | 92 | 85.4 | 11.4 | 632.3 | 4020.4 | 51.7 | 28.6 | 84.5 | 83 | 74.9 | 90.5 | 37.9 | 18.6 | 8264.2 | 7308.5 | 9430.3 | 15194.8 | 12733.7 | 17185.2 | 1.839 | 1.742 | 1.822 | 0.616 | 0.671 | 0.63 | 3.78 | 4.85 | 4.3 | 0.626 | 0.552 | 0.614 | 4.54 | -4.34 | 3.32 | 0.606 | 0.643 | 0.655 | -3.61 | -3.37 | -3.65 | 0.581 | 0.581 | 0.598 | 2.94 | -3.54 | 3.88 | Fair_Mixed | 7308.5 | 12733.7 | 1.742 | 0.671 | 4.85 | 0.655 | 4.54 | 0.6176 | 0.815 | 0.71 | 0.7902 | 1 | 0.5911 | 0.6189 | 0.7169 | 0.7169 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1785 | 1739.6 | 926.3 | 144.2 | 193.9 | 31.4 | 1232.4 | 8385 | 34.7 | 46.6 | 106.9 | 104.6 | 91.7 | 115.3 | 42.7 | 32.7 | 2101.2 | 1683.1 | 1458.2 | 2508.8 | 1897.8 | 1623.4 | 1.194 | 1.128 | 1.113 | 0.968 | 0.968 | 0.983 | 9.57 | 9.03 | 9.15 | 0.723 | 0.939 | 0.909 | -5.92 | 7.56 | -8.69 | 0.88 | 0.889 | 0.797 | 5.72 | -5.29 | 6.18 | 0.881 | 0.704 | 0.767 | -8.04 | -6.35 | 6.37 | Very Poor_Mixed | 1458.2 | 1623.4 | 1.113 | 0.983 | 9.57 | 0.939 | 8.69 | 0.078 | 0.6147 | 0.1706 | 0.2943 | 1 | 0.0549 | 0.2509 | 0.3379 | 0.3379 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1786 | 423.1 | 325.2 | 78.5 | 166.1 | 1.8 | 607 | 3754.3 | 56.2 | 21.7 | 104.1 | 108.4 | 91.5 | 113.1 | 43.7 | 14.2 | 7773.7 | 8162.6 | 7314.5 | 14146.1 | 6271.7 | 12081 | 1.82 | 0.768 | 1.652 | 0.603 | 0.607 | 0.607 | 4.89 | 4.22 | 3.98 | 0.535 | 0.536 | 0.5 | 2.42 | 2.11 | 2.49 | 0.529 | 0.534 | 0.525 | -2.9 | 2.25 | 2.1 | 0.536 | 0.563 | 0.536 | 2 | -2.67 | 2 | Critical_Thermal | 7314.5 | 6271.7 | 0.768 | 0.607 | 4.89 | 0.563 | 2.9 | 0.6898 | 0.9355 | 0.1702 | 0.9144 | 0.8187 | 0.6248 | 0.832 | 0.7157 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H4
1787 | 941.6 | 614.1 | 110.8 | 135.2 | 18.3 | 820.9 | 5650.9 | 45.3 | 33.8 | 92 | 92.8 | 79.3 | 99.8 | 39.9 | 24 | 5718.5 | 4720.6 | 4398.5 | 8286.3 | 7103.5 | 6793.3 | 1.449 | 1.505 | 1.544 | 0.722 | 0.766 | 0.684 | 5.12 | 6.3 | -5.72 | 0.621 | 0.712 | 0.619 | 5.06 | 5.68 | 4.21 | 0.698 | 0.715 | 0.652 | 4.83 | 5.48 | 5.97 | 0.656 | 0.678 | 0.639 | 4.86 | 5.47 | 5.34 | Poor_Mixed | 4398.5 | 6793.3 | 1.449 | 0.766 | 6.3 | 0.715 | 5.97 | 0.3964 | 0.7485 | 0.5005 | 0.6143 | 1 | 0.4284 | 0.4767 | 0.5755 | 0.5755 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1788 | 967.9 | 538.7 | 98.8 | 119.2 | 17.5 | 884.1 | 5621 | 45.6 | 34 | 89.6 | 88.1 | 81.1 | 99 | 39.6 | 24.8 | 4838.7 | 6143 | 6223.1 | 7002.4 | 9351.6 | 9239.4 | 1.447 | 1.522 | 1.485 | 0.752 | 0.727 | 0.727 | -6.41 | 6.16 | 6.55 | 0.658 | 0.766 | 0.715 | 4.93 | 4.63 | 4.32 | 0.595 | 0.691 | 0.706 | 5.36 | 5.2 | 4.96 | 0.699 | 0.704 | 0.658 | 4.41 | 5.63 | 5.26 | Poor_Mixed | 4838.7 | 7002.4 | 1.447 | 0.752 | 6.55 | 0.766 | 5.63 | 0.4241 | 0.7461 | 0.5411 | 0.5865 | 1 | 0.3814 | 0.459 | 0.575 | 0.575 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1789 | 112.8 | 120 | 65 | 69.4 | 1 | 364.7 | 2731.7 | 52.9 | 26.1 | 75.1 | 79.4 | 73.5 | 85.6 | 36.2 | 12.4 | 9285.1 | 8954.5 | 9100.2 | 18570.3 | 16761.8 | 17081.5 | 2 | 1.872 | 1.877 | 0.575 | 0.513 | 0.531 | 2.56 | 2.02 | 2.77 | 0.539 | 0.548 | 0.5 | 2 | 2 | 2.44 | 0.5 | 0.508 | 0.549 | 2.3 | 2 | 2.74 | 0.5 | 0.5 | 0.5 | -2.12 | 2 | 2.48 | Fair_Oil | 8954.5 | 16761.8 | 1.872 | 0.575 | 2.77 | 0.549 | 2.74 | 0.958 | 0.852 | 0.8754 | 0.9575 | 1 | 0.8509 | 0.9144 | 0.9209 | 0.9209 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1790 | 1305.4 | 752.5 | 125.4 | 150.3 | 25.9 | 1164.4 | 7416 | 39.3 | 42.6 | 100.5 | 103.3 | 91 | 109 | 43.4 | 31.5 | 2451.2 | 2963 | 2279.4 | 2828.5 | 3416.9 | 2815.2 | 1.154 | 1.153 | 1.235 | 0.896 | 0.86 | 0.908 | 8.01 | 8.59 | 8.47 | 0.856 | 0.821 | 0.803 | -7.63 | 5.96 | 8.14 | 0.76 | 0.848 | 0.818 | 6.54 | 8.52 | 6.19 | 0.855 | 0.756 | 0.737 | 6.09 | 6.48 | -6.89 | Very Poor_Mixed | 2279.4 | 2815.2 | 1.153 | 0.908 | 8.59 | 0.856 | 8.52 | 0.226 | 0.6534 | 0.2445 | 0.3406 | 1 | 0.1582 | 0.2636 | 0.406 | 0.406 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1791 | 247.9 | 212 | 68.1 | 70.8 | 4.1 | 541.6 | 2881.9 | 56.1 | 23.7 | 76.4 | 75 | 71.6 | 81.4 | 35 | 12.4 | 9453.4 | 9708.9 | 9801.3 | 18395.3 | 19417.8 | 19263.2 | 1.946 | 2 | 1.965 | 0.64 | 0.574 | 0.656 | 4.5 | -3.28 | 4.41 | 0.506 | 0.5 | 0.552 | 2.03 | -2 | -2.14 | 0.508 | 0.551 | 0.528 | 2 | -2.56 | 2 | 0.5 | 0.504 | 0.505 | 2.41 | -2.42 | 2 | Fair_Winding_TD_Cap | 9453.4 | 18395.3 | 1.946 | 0.656 | 4.5 | 0.552 | 2.56 | 0.7868 | 0.8931 | 0.9515 | 0.9575 | 1 | 0.6253 | 0.9011 | 0.8566 | 0.8566 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1792 | 852.5 | 445.7 | 102.9 | 124.5 | 20 | 842.9 | 5280.2 | 45.1 | 34.7 | 91.4 | 91.1 | 84.6 | 98.9 | 39.2 | 25.2 | 5794.5 | 5354.7 | 6700.4 | 9055.1 | 8372.3 | 10611.5 | 1.563 | 1.564 | 1.584 | 0.684 | 0.703 | 0.768 | -5.22 | 5.42 | -5.98 | 0.642 | 0.704 | 0.651 | 6.14 | 4.51 | 6.01 | 0.737 | 0.676 | 0.678 | 4.61 | 5.37 | 4.43 | 0.725 | 0.718 | 0.665 | 3.94 | 4.89 | 4.41 | Poor_Mixed | 5354.7 | 8372.3 | 1.563 | 0.768 | 5.98 | 0.737 | 6.14 | 0.429 | 0.7379 | 0.4902 | 0.5725 | 1 | 0.4431 | 0.4587 | 0.5781 | 0.5781 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1793 | 363.1 | 219.4 | 77.4 | 89.7 | 1 | 581.6 | 3629.3 | 13.9 | 23.5 | 83.5 | 83.6 | 75.4 | 89.1 | 37.1 | 18.2 | 1261.5 | 703.5 | 1138.1 | 1343.6 | 761.3 | 1204.4 | 1.065 | 1.082 | 1.058 | 0.664 | 0.692 | 0.736 | -5.15 | -4.52 | -5.35 | 0.563 | 0.558 | 0.604 | 2.89 | 2.73 | 2.98 | 0.536 | 0.619 | 0.563 | 2.22 | 3.1 | 2.89 | 0.556 | 0.529 | 0.578 | 2.14 | 3.17 | -3.03 | Critical_IR_PI | 703.5 | 761.3 | 1.058 | 0.736 | 5.35 | 0.619 | 3.17 | 0.8452 | 0.3136 | 0.7206 | 0.8024 | 0.925 | 0.4923 | 0.7262 | 0.7087 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
1794 | 206.2 | 120 | 70.7 | 60.3 | 6.1 | 367.1 | 2945.1 | 60 | 20 | 75 | 79.1 | 70.9 | 80.8 | 35.2 | 11.9 | 9710 | 10000 | 10000 | 18994.1 | 19778.6 | 20000 | 1.956 | 1.978 | 2 | 0.534 | 0.53 | 0.56 | 2.77 | -2.05 | 2.62 | 0.535 | 0.531 | 0.526 | 2 | 2 | -2 | 0.514 | 0.5 | 0.516 | 3.16 | -2.14 | 2.77 | 0.527 | 0.525 | 0.546 | 2 | 2 | 2 | Good_Mixed | 9710 | 18994.1 | 1.956 | 0.56 | 2.77 | 0.546 | 3.16 | 0.8194 | 1 | 0.9333 | 0.9682 | 1 | 0.8405 | 0.8622 | 0.8994 | 0.8994 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1795 | 658.9 | 482 | 102.7 | 107.5 | 16 | 721.5 | 5244.3 | 48.9 | 30.6 | 87.4 | 91.8 | 79.7 | 95.8 | 39.2 | 17.7 | 7094.7 | 7027.2 | 7296 | 12387.1 | 12847 | 11568.8 | 1.746 | 1.828 | 1.586 | 0.673 | 0.609 | 0.684 | 4.08 | -3.99 | 4.96 | 0.634 | 0.609 | 0.657 | 3.61 | 4.38 | 4.44 | 0.641 | 0.615 | 0.673 | 4.55 | -3.63 | 3.2 | 0.556 | 0.631 | 0.648 | 4.32 | 4.02 | -3.36 | Fair_Mixed | 7027.2 | 11568.8 | 1.586 | 0.684 | 4.96 | 0.673 | 4.55 | 0.4981 | 0.7881 | 0.5593 | 0.8173 | 1 | 0.5728 | 0.574 | 0.6594 | 0.6594 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1796 | 1628.8 | 873.5 | 132.9 | 182.9 | 34.3 | 1213.7 | 7944.2 | 36.9 | 43.1 | 105.1 | 106.5 | 95.6 | 115.2 | 42.8 | 32.9 | 1447.5 | 1581.1 | 2732.8 | 1707.9 | 1760.1 | 3148.8 | 1.18 | 1.113 | 1.152 | 0.894 | 0.954 | 0.931 | 8.88 | 9.02 | 8.68 | 0.795 | 0.88 | 0.858 | 9.34 | 7.67 | -6.72 | 0.806 | 0.828 | 0.825 | -4.84 | 8.26 | 5.66 | 0.859 | 0.863 | 0.734 | 8.15 | 7.03 | -5.99 | Very Poor_Mixed | 1447.5 | 1707.9 | 1.113 | 0.954 | 9.02 | 0.88 | 9.34 | 0.1047 | 0.6484 | 0.1479 | 0.2865 | 1 | 0.1059 | 0.2393 | 0.351 | 0.351 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1797 | 1441.6 | 806 | 130.7 | 175 | 29 | 1266.7 | 7569.1 | 34.9 | 43.4 | 100.9 | 102.3 | 90.5 | 110.8 | 42.8 | 31.6 | 1641.4 | 2078.3 | 2483.2 | 1934.5 | 2301.3 | 3120.8 | 1.179 | 1.107 | 1.257 | 0.866 | 0.895 | 0.923 | 8.42 | 8.4 | 8.57 | 0.758 | 0.76 | 0.841 | -8.25 | 7.84 | -6.37 | 0.746 | 0.791 | 0.737 | 8.46 | 7.48 | 5.79 | 0.845 | 0.823 | 0.744 | 8.25 | 8.46 | 5.55 | Very Poor_Mixed | 1641.4 | 1934.5 | 1.107 | 0.923 | 8.57 | 0.845 | 8.46 | 0.1565 | 0.6455 | 0.2459 | 0.3368 | 1 | 0.1481 | 0.2719 | 0.3877 | 0.3877 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1798 | 1564.5 | 894.4 | 138.9 | 180.4 | 32.9 | 1236.9 | 8142.4 | 36.2 | 44 | 105.8 | 106.4 | 93.5 | 112.8 | 42.6 | 30.7 | 923.3 | 1218.7 | 2965.4 | 1200 | 1393.8 | 3584.9 | 1.3 | 1.144 | 1.209 | 0.922 | 0.868 | 0.885 | 8.04 | 7.61 | 7.75 | 0.889 | 0.714 | 0.692 | 5.03 | 6.89 | 4.43 | 0.659 | 0.785 | 0.646 | -6.02 | 5.17 | -5.8 | 0.77 | 0.718 | 0.757 | 7.79 | 5.34 | 6.27 | Very Poor_Mixed | 923.3 | 1200 | 1.144 | 0.922 | 8.04 | 0.889 | 7.79 | 0.1052 | 0.6396 | 0.1697 | 0.3711 | 1 | 0.1843 | 0.3742 | 0.3917 | 0.3917 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1799 | 1506.5 | 886.4 | 141.1 | 177.2 | 32.2 | 1209.2 | 8438.1 | 34 | 46.8 | 103.2 | 106.2 | 92.5 | 112.6 | 43.8 | 33.3 | 1694.7 | 1720.8 | 1426.4 | 2032 | 1863.6 | 1524.1 | 1.199 | 1.083 | 1.068 | 0.913 | 0.884 | 0.872 | -8.26 | 7.94 | -8.83 | 0.8 | 0.934 | 0.881 | 7.23 | 8.25 | 5.96 | 0.698 | 0.826 | 0.896 | 7.92 | 7.03 | 8.59 | 0.858 | 0.89 | 0.893 | 6.15 | 7.65 | 9.58 | Very Poor_Mixed | 1426.4 | 1524.1 | 1.068 | 0.913 | 8.83 | 0.934 | 9.58 | 0.1134 | 0.6128 | 0.1834 | 0.2709 | 1 | 0.1577 | 0.2003 | 0.3519 | 0.3519 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1800 | 207.9 | 199.3 | 70.9 | 65.8 | 1.5 | 390.9 | 2880.7 | 57.3 | 22.6 | 85.5 | 83.6 | 76.6 | 89.7 | 36.3 | 13.6 | 4490.7 | 6014.4 | 5396.7 | 7023.8 | 9800 | 8031.1 | 1.564 | 1.629 | 1.488 | 0.65 | 0.55 | 0.599 | 4.15 | 3.7 | 3.54 | 0.596 | 0.612 | 0.597 | 3.01 | 3.29 | 3.47 | 0.585 | 0.589 | 0.624 | 3.24 | 2.51 | 4.07 | 0.606 | 0.607 | 0.567 | -3.53 | 3.54 | 3.76 | Poor_IR_PI | 4490.7 | 7023.8 | 1.488 | 0.65 | 4.15 | 0.624 | 4.07 | 0.8842 | 0.915 | 0.698 | 0.9294 | 1 | 0.6706 | 0.6422 | 0.8166 | 0.8166 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
1801 | 1435.4 | 797.1 | 134.8 | 159 | 26.2 | 1125.8 | 7499 | 36.4 | 43.2 | 104.7 | 106.2 | 92.3 | 114 | 43.9 | 30.6 | 3186.7 | 1985.4 | 1960 | 3888.6 | 2303.8 | 2433.5 | 1.22 | 1.16 | 1.242 | 0.908 | 0.908 | 0.946 | -8.33 | 7.83 | 8.95 | 0.798 | 0.796 | 0.858 | 6.32 | 6.19 | 7.66 | 0.783 | 0.676 | 0.839 | 6.39 | -7.25 | 7.27 | 0.844 | 0.829 | 0.86 | 8.48 | -7.83 | 5.81 | Very Poor_Mixed | 1960 | 2303.8 | 1.16 | 0.946 | 8.95 | 0.86 | 8.48 | 0.1984 | 0.6474 | 0.1684 | 0.3749 | 1 | 0.1347 | 0.2587 | 0.3883 | 0.3883 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1802 | 173.9 | 166.5 | 65 | 54.7 | 1 | 408.6 | 2500 | 58.6 | 21.6 | 77.6 | 75 | 72.7 | 84.7 | 35 | 12.6 | 9328 | 9960.1 | 8846.9 | 17931.5 | 18612.2 | 16829.7 | 1.922 | 1.869 | 1.902 | 0.564 | 0.508 | 0.564 | 2 | -2.67 | 2.45 | 0.63 | 0.573 | 0.58 | 2.74 | 3.36 | 2.22 | 0.527 | 0.744 | 0.518 | 2.49 | 6.18 | 2.33 | 0.5 | 0.528 | 0.583 | 2.49 | -2.34 | 2.35 | Poor_Bushing_TD_Cap | 8846.9 | 16829.7 | 1.869 | 0.564 | 2.67 | 0.744 | 6.18 | 0.9583 | 0.938 | 0.9118 | 0.953 | 1 | 0.8488 | 0.7322 | 0.9016 | 0.9016 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_LV_Y_TanDelta_pct
1803 | 1511.1 | 854.8 | 139.6 | 177.9 | 31.2 | 1244.1 | 8353.3 | 36.5 | 43.3 | 107.3 | 106.2 | 94.4 | 116.6 | 45.2 | 30.8 | 2093.3 | 1269.7 | 1723.4 | 2560.1 | 1403.9 | 2042.5 | 1.223 | 1.106 | 1.185 | 0.917 | 0.974 | 0.94 | 8.96 | -8.6 | 9.08 | 0.73 | 0.963 | 0.746 | -6.34 | -7.02 | 8.97 | 0.852 | 0.771 | 0.775 | 8.39 | 6.4 | -6.09 | 0.769 | 0.932 | 0.744 | 6.61 | 8.69 | -7.94 | Very Poor_Mixed | 1269.7 | 1403.9 | 1.106 | 0.974 | 9.08 | 0.963 | 8.97 | 0.1189 | 0.6465 | 0.1198 | 0.3673 | 1 | 0.0931 | 0.2491 | 0.3555 | 0.3555 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1804 | 652.1 | 331.6 | 95.6 | 84.7 | 12.2 | 719.2 | 4395.6 | 52.2 | 29.7 | 87.2 | 82.8 | 76.7 | 91.9 | 38.3 | 19.8 | 6953.5 | 7692.1 | 6905.8 | 12043.9 | 13935.1 | 11577.2 | 1.732 | 1.812 | 1.676 | 0.65 | 0.62 | 0.62 | 4.95 | 3.91 | 3.87 | 0.614 | 0.562 | 0.537 | -4.3 | -3.05 | 3.41 | 0.549 | 0.573 | 0.588 | 3.54 | 2.54 | 3.92 | 0.568 | 0.605 | 0.585 | 4.03 | 2.97 | 3.22 | Fair_Mixed | 6905.8 | 11577.2 | 1.676 | 0.65 | 4.95 | 0.614 | 4.3 | 0.5811 | 0.8 | 0.6695 | 0.753 | 1 | 0.6045 | 0.6801 | 0.7129 | 0.7129 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1805 | 100 | 138.9 | 70.1 | 53.6 | 1 | 350 | 2977 | 55.2 | 23.5 | 76.1 | 77.1 | 73.2 | 80.8 | 36.1 | 12.5 | 9245 | 7916.3 | 8017 | 17558.1 | 14738.9 | 14918.5 | 1.899 | 1.862 | 1.861 | 0.565 | 0.5 | 0.526 | 2.74 | -2.27 | 2.3 | 0.542 | 0.518 | 0.523 | 2 | -2.41 | 2.19 | 0.525 | 0.56 | 0.562 | 2.7 | 2 | 3.02 | 0.506 | 0.507 | 0.5 | -2.8 | 2.36 | 2 | Fair_Oil | 7916.3 | 14738.9 | 1.861 | 0.565 | 2.74 | 0.562 | 3.02 | 0.9833 | 0.8969 | 0.9093 | 0.9552 | 1 | 0.8786 | 0.8511 | 0.9284 | 0.9284 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1806 | 1550.7 | 840.7 | 136.5 | 178.9 | 32.2 | 1204.5 | 7540.6 | 35.4 | 45.9 | 102.6 | 106.7 | 91.9 | 113.6 | 42.8 | 34.1 | 1828.3 | 2315.7 | 2399.4 | 2062.1 | 2826.9 | 2733.2 | 1.128 | 1.221 | 1.139 | 0.912 | 0.99 | 0.947 | 9.34 | 9.84 | 9.36 | 0.822 | 0.907 | 0.935 | -7.99 | 7 | 8.51 | 0.737 | 0.794 | 0.89 | 7.95 | 6.61 | -6.02 | 0.895 | 0.711 | 0.959 | 6.14 | 6.35 | 6.69 | Very Poor_Mixed | 1828.3 | 2062.1 | 1.128 | 0.99 | 9.84 | 0.959 | 8.51 | 0.1296 | 0.6213 | 0.1896 | 0.2395 | 1 | 0.0575 | 0.2226 | 0.346 | 0.346 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1807 | 532.3 | 374.4 | 87.5 | 97.4 | 11.3 | 662.5 | 4314.4 | 52.8 | 28 | 84.6 | 81 | 77.6 | 90.2 | 38.1 | 17.9 | 8041.2 | 7173.6 | 6784.5 | 15045.9 | 12521.6 | 10758.4 | 1.871 | 1.746 | 1.586 | 0.71 | 0.641 | 0.686 | -4.77 | 4.31 | 4.55 | 0.547 | 0.557 | 0.541 | 4.25 | 4.59 | 3.48 | 0.543 | 0.604 | 0.622 | 3.26 | 3.85 | 3.83 | 0.61 | 0.61 | 0.582 | 3.68 | 2.17 | 3.34 | Fair_Mixed | 6784.5 | 10758.4 | 1.586 | 0.71 | 4.77 | 0.622 | 4.59 | 0.5932 | 0.8235 | 0.7059 | 0.8114 | 1 | 0.5364 | 0.6689 | 0.7138 | 0.7138 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1808 | 760.1 | 562.2 | 105.6 | 125.2 | 18.1 | 804.9 | 5535.1 | 59.9 | 22.1 | 80.1 | 83.8 | 73.5 | 84.9 | 36.3 | 10.3 | 8272.9 | 9286.9 | 9313.3 | 15617.8 | 18484.9 | 18626.7 | 1.888 | 1.99 | 2 | 0.531 | 0.537 | 0.5 | -3.03 | 2.87 | 2.55 | 0.521 | 0.602 | 0.573 | 3.62 | -2.24 | -2.28 | 0.578 | 0.573 | 0.509 | 3.24 | 2 | 2.3 | 0.557 | 0.596 | 0.552 | 2.73 | 2 | 2.63 | Fair_DGA | 8272.9 | 15617.8 | 1.888 | 0.537 | 3.03 | 0.602 | 3.62 | 0.4342 | 0.926 | 0.7866 | 0.9968 | 1 | 0.8624 | 0.7533 | 0.7645 | 0.7645 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1809 | 380.6 | 206.7 | 84.9 | 68.3 | 4.5 | 561.6 | 3693.7 | 59.6 | 21.3 | 76.7 | 81.1 | 73.1 | 82.5 | 36.8 | 12.8 | 7618.4 | 8267.7 | 8011.3 | 13812 | 15018.7 | 14801 | 1.813 | 1.817 | 1.848 | 0.73 | 0.807 | 0.744 | -5.79 | 6.96 | -6.21 | 0.544 | 0.57 | 0.593 | 2.7 | 2.32 | 2 | 0.528 | 0.5 | 0.559 | -3.06 | 2 | 3.18 | 0.537 | 0.551 | 0.547 | 2 | 2.65 | -2.3 | Poor_Winding_TD_Cap | 7618.4 | 13812 | 1.813 | 0.807 | 6.96 | 0.593 | 3.18 | 0.7537 | 0.9458 | 0.8538 | 0.9484 | 1 | 0.3638 | 0.7925 | 0.7883 | 0.7883 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1810 | 561.7 | 406.2 | 91.1 | 102.2 | 5.3 | 629.6 | 4542.6 | 49.9 | 30.4 | 83.1 | 86.8 | 77 | 90.5 | 38.4 | 11.9 | 941.4 | 904.7 | 887 | 982.1 | 960.6 | 904.7 | 1.043 | 1.062 | 1.02 | 0.677 | 0.7 | 0.652 | -3.87 | 5 | 22.25 | 0.563 | 0.548 | 0.585 | -3.07 | 2.89 | 3.69 | 0.604 | 0.587 | 0.608 | 3.42 | -3.11 | 3.13 | 0.618 | 0.581 | 0.557 | 3 | 2 | 2.49 | Critical_IR_PI | 887 | 904.7 | 1.02 | 0.7 | 22.25 | 0.618 | 3.69 | 0.6428 | 0.7907 | 0.6742 | 0.9682 | 0.775 | 0.4468 | 0.6869 | 0.6816 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1811 | 315.1 | 201.7 | 76.6 | 57.8 | 1.9 | 422.2 | 3763.2 | 42.3 | 37 | 77.5 | 75 | 73.1 | 85.5 | 36.5 | 16.3 | 7408.2 | 7151.5 | 6044.7 | 12319 | 12319 | 9696 | 1.663 | 1.723 | 1.604 | 0.622 | 0.602 | 0.639 | 4.25 | -3.5 | -4.42 | 0.503 | 0.514 | 0.528 | 3.39 | 2.3 | 2.75 | 0.584 | 0.511 | 0.529 | 2.62 | 2.22 | 2 | 0.56 | 0.547 | 0.5 | 2.22 | 2.98 | 2.49 | Poor_Oil | 6044.7 | 9696 | 1.604 | 0.639 | 4.42 | 0.584 | 3.39 | 0.8558 | 0.712 | 0.8991 | 0.8578 | 1 | 0.6258 | 0.8347 | 0.83 | 0.83 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1812 | 899.1 | 512.2 | 105.9 | 120.6 | 20.8 | 842.1 | 5749.6 | 46.2 | 33.3 | 89.3 | 87.9 | 81.7 | 94.8 | 38.8 | 23.1 | 5958.4 | 5798.4 | 5638.8 | 9422.5 | 8837.3 | 8615.2 | 1.581 | 1.524 | 1.528 | 0.709 | 0.682 | 0.759 | 5.75 | 5.39 | -6.71 | 0.732 | 0.646 | 0.718 | 6.39 | 6.11 | -5.72 | 0.708 | 0.701 | 0.673 | -6.53 | 5.5 | -4.15 | 0.71 | 0.72 | 0.628 | 5.77 | 4.53 | -4.77 | Poor_Mixed | 5638.8 | 8615.2 | 1.524 | 0.759 | 6.71 | 0.732 | 6.53 | 0.41 | 0.7544 | 0.5666 | 0.645 | 1 | 0.4219 | 0.4331 | 0.579 | 0.579 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1813 | 535.7 | 328 | 84.6 | 88.5 | 10.7 | 660.9 | 3905.9 | 50 | 28.8 | 80.1 | 84.4 | 77.2 | 86.7 | 39.1 | 16.8 | 8139.1 | 8970.1 | 7662.4 | 14962.2 | 17329.4 | 13787.3 | 1.838 | 1.932 | 1.799 | 0.61 | 0.626 | 0.668 | 3.37 | -4.18 | 4.03 | 0.639 | 0.544 | 0.635 | 2.6 | -3.7 | 3.73 | 0.683 | 0.592 | 0.634 | -4.07 | 3.68 | -4.42 | 0.644 | 0.681 | 0.641 | 3.89 | 3.22 | -2.74 | Fair_Mixed | 7662.4 | 13787.3 | 1.799 | 0.668 | 4.18 | 0.683 | 4.42 | 0.6186 | 0.8123 | 0.7293 | 0.8436 | 1 | 0.6231 | 0.5875 | 0.7202 | 0.7202 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1814 | 1114.7 | 565 | 116.7 | 127 | 25.7 | 957 | 6056 | 56.1 | 22 | 78.7 | 78.6 | 74 | 85 | 36.1 | 10 | 9068.4 | 8608.9 | 9485.5 | 16899.4 | 16418.3 | 18520.4 | 1.864 | 1.907 | 1.952 | 0.561 | 0.576 | 0.541 | -2.89 | -3.46 | 3.13 | 0.558 | 0.518 | 0.585 | 2 | 2.32 | 3.44 | 0.52 | 0.507 | 0.516 | 2.68 | 2.76 | 2.57 | 0.55 | 0.515 | 0.548 | 3.38 | 2.07 | 2.51 | Poor_DGA | 8608.9 | 16418.3 | 1.864 | 0.576 | 3.46 | 0.585 | 3.44 | 0.3298 | 0.9283 | 0.839 | 1 | 1 | 0.7623 | 0.81 | 0.7403 | 0.7403 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1815 | 797.1 | 517.8 | 102.4 | 133.2 | 18.8 | 770.3 | 5765.6 | 46.2 | 34.2 | 90.8 | 91.9 | 82 | 100.6 | 39.4 | 25.5 | 5337.1 | 6065.8 | 5932.5 | 8035.5 | 9463.9 | 8975.6 | 1.506 | 1.56 | 1.513 | 0.711 | 0.72 | 0.781 | 5.76 | 6.08 | -6.44 | 0.614 | 0.667 | 0.723 | 4.82 | 5.11 | 5.65 | 0.631 | 0.728 | 0.659 | 4.43 | 4.14 | 6.12 | 0.647 | 0.695 | 0.711 | 6.14 | -3.12 | 5.3 | Poor_Mixed | 5337.1 | 8035.5 | 1.506 | 0.781 | 6.44 | 0.728 | 6.14 | 0.4287 | 0.7438 | 0.4955 | 0.562 | 1 | 0.3955 | 0.4745 | 0.5748 | 0.5748 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1816 | 1004.1 | 550.2 | 113.9 | 129.6 | 19.7 | 883.8 | 5546.8 | 46.4 | 32.4 | 91.1 | 90.1 | 82.9 | 98.5 | 39.9 | 23.4 | 5137.5 | 6527.7 | 5546.3 | 7899.2 | 10505.6 | 8953.4 | 1.538 | 1.609 | 1.614 | 0.682 | 0.731 | 0.719 | -5.26 | 5.61 | 4.58 | 0.673 | 0.618 | 0.636 | -5.66 | 4.87 | -5.56 | 0.639 | 0.628 | 0.617 | 5.66 | -5.55 | 5.46 | 0.588 | 0.634 | 0.67 | 4.58 | 5.21 | 4.31 | Poor_Mixed | 5137.5 | 7899.2 | 1.538 | 0.731 | 5.61 | 0.673 | 5.66 | 0.3865 | 0.7654 | 0.5068 | 0.6348 | 1 | 0.4715 | 0.5185 | 0.5902 | 0.5902 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1817 | 959.8 | 584 | 104.5 | 117.2 | 19.2 | 829.9 | 5342.9 | 54.9 | 27.3 | 75.1 | 75 | 70 | 80 | 35 | 11.6 | 8602.1 | 8622.7 | 7811.1 | 16129 | 16417.1 | 14178.2 | 1.875 | 1.904 | 1.815 | 0.544 | 0.578 | 0.525 | 2.36 | 2.71 | 2.58 | 0.536 | 0.572 | 0.563 | 3.07 | 2.07 | 2.49 | 0.56 | 0.505 | 0.5 | -3.01 | -2.55 | -2.78 | 0.53 | 0.51 | 0.5 | 3.49 | 3.25 | 3.43 | Fair_DGA | 7811.1 | 14178.2 | 1.815 | 0.578 | 2.71 | 0.572 | 3.49 | 0.4167 | 0.8337 | 0.9969 | 0.9744 | 1 | 0.8228 | 0.8229 | 0.7759 | 0.7759 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1818 | 1535.5 | 978.6 | 138.7 | 181.1 | 33.5 | 1264.2 | 8057.4 | 33.2 | 47.1 | 105.6 | 103.1 | 94.9 | 114.4 | 44 | 33.7 | 742.5 | 1457.1 | 1469.4 | 1200 | 1620.6 | 1620.2 | 1.616 | 1.112 | 1.103 | 0.937 | 0.883 | 0.939 | 8.51 | 8.38 | 9.14 | 0.931 | 0.719 | 0.741 | 6.49 | 7.26 | 7.78 | 0.763 | 0.802 | 0.755 | 9.14 | -9.5 | -7.19 | 0.871 | 0.833 | 0.773 | 8.29 | 7.86 | 5.52 | Very Poor_Mixed | 742.5 | 1200 | 1.103 | 0.939 | 9.14 | 0.931 | 9.5 | 0.0932 | 0.61 | 0.1634 | 0.2552 | 1 | 0.1199 | 0.2487 | 0.3472 | 0.3472 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1819 | 1712.7 | 982.4 | 145.5 | 197 | 34.3 | 1379 | 8723.5 | 56.1 | 26 | 87.8 | 85.1 | 78.7 | 93.5 | 38.5 | 12.4 | 7534.7 | 8649 | 8144.4 | 13362 | 16146.9 | 15247 | 1.773 | 1.867 | 1.872 | 0.583 | 0.654 | 0.542 | 3.78 | 4.23 | 3.19 | 0.561 | 0.558 | 0.538 | -2.47 | 2.53 | 2.25 | 0.5 | 0.554 | 0.56 | -16.38 | 2.54 | 2.77 | 0.543 | 0.537 | 0.514 | 2.65 | 2.73 | 2.33 | Critical_DGA | 7534.7 | 13362 | 1.773 | 0.654 | 4.23 | 0.561 | 16.38 | 0.0371 | 0.8536 | 0.6248 | 0.9575 | 1 | 0.6847 | 0.7725 | 0.617 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
1820 | 261.6 | 229.6 | 76 | 62.6 | 2.2 | 480 | 2963.9 | 58.2 | 21.4 | 80.8 | 79.1 | 72.7 | 86.2 | 35.6 | 13.5 | 10000 | 8826.7 | 7795.4 | 19926.4 | 16931.3 | 14973.4 | 1.993 | 1.918 | 1.921 | 0.553 | 0.546 | 0.533 | 2.5 | 2.58 | 2.5 | 0.53 | 0.55 | 0.5 | 2.4 | 3.39 | 2.33 | 0.5 | 0.526 | 0.627 | -2.28 | 2.02 | 2.75 | 0.705 | 0.537 | 0.551 | 5.64 | -2.92 | -3.66 | Poor_Bushing_TD_Cap | 7795.4 | 14973.4 | 1.918 | 0.553 | 2.58 | 0.705 | 5.64 | 0.8373 | 0.9432 | 0.8228 | 0.9318 | 1 | 0.83 | 0.7667 | 0.8656 | 0.8656 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1821 | 100 | 123.8 | 65 | 50 | 4.2 | 350 | 2878.5 | 58.9 | 20.5 | 79.3 | 81.1 | 70.5 | 86.3 | 36.5 | 12.7 | 9452.1 | 9674 | 9373.1 | 18352.2 | 18371.7 | 17206 | 1.942 | 1.899 | 1.836 | 0.609 | 0.561 | 0.572 | 4.02 | -3.22 | 2.29 | 0.582 | 0.518 | 0.531 | -2.97 | 2 | -2.69 | 0.5 | 0.5 | 0.5 | 2.66 | 2 | 2 | 0.514 | 0.558 | 0.504 | -2.61 | 3.46 | 2.1 | Good_Mixed | 9373.1 | 17206 | 1.836 | 0.609 | 4.02 | 0.582 | 3.46 | 0.8875 | 0.9709 | 0.8353 | 0.9507 | 1 | 0.7335 | 0.8726 | 0.8892 | 0.8892 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1822 | 857 | 555.2 | 102 | 129.5 | 24.6 | 908.8 | 5430 | 45.8 | 30.4 | 87.3 | 91.6 | 80.6 | 95.5 | 39.9 | 23.5 | 6240 | 7038 | 6586.3 | 10122.4 | 11340.3 | 10364.2 | 1.622 | 1.611 | 1.574 | 0.734 | 0.736 | 0.687 | 5.47 | 4.98 | 5.25 | 0.631 | 0.722 | 0.691 | 3.54 | 4.2 | -4.75 | 0.643 | 0.677 | 0.708 | 4.02 | 4.87 | 4.28 | 0.719 | 0.653 | 0.631 | -4.2 | 4.53 | 3.32 | Poor_Mixed | 6240 | 10122.4 | 1.574 | 0.736 | 5.47 | 0.722 | 4.87 | 0.3774 | 0.7907 | 0.5524 | 0.6314 | 1 | 0.4591 | 0.503 | 0.5909 | 0.5909 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1823 | 817.2 | 457.3 | 98.9 | 118.6 | 15.7 | 763.9 | 4801.8 | 49.5 | 31 | 91 | 90.1 | 82.2 | 98.6 | 39.2 | 24.5 | 6282.8 | 6034.6 | 7577.8 | 9881.4 | 9573.4 | 13186.6 | 1.573 | 1.586 | 1.74 | 0.714 | 0.642 | 0.732 | -6.03 | 4.62 | 5.78 | 0.641 | 0.563 | 0.631 | 4.29 | 4.56 | 4.88 | 0.59 | 0.663 | 0.624 | 3.18 | 4.31 | 3.88 | 0.647 | 0.646 | 0.613 | 3.79 | -3.1 | 4.04 | Poor_Mixed | 6034.6 | 9573.4 | 1.573 | 0.732 | 6.03 | 0.663 | 4.88 | 0.4806 | 0.7829 | 0.5159 | 0.597 | 1 | 0.468 | 0.5788 | 0.6252 | 0.6252 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1824 | 881.1 | 509.4 | 105.7 | 112.4 | 17.5 | 805.5 | 4862.3 | 46.1 | 33.5 | 91.9 | 90.8 | 81.1 | 98.6 | 39.4 | 24.9 | 3895 | 6247.3 | 4997.3 | 5735.2 | 9736 | 7616.1 | 1.472 | 1.558 | 1.524 | 0.73 | 0.737 | 0.761 | 5.61 | 5.72 | 5.83 | 0.679 | 0.702 | 0.711 | 4.26 | 4.97 | -4.65 | 0.574 | 0.665 | 0.671 | -4.93 | 6.34 | 5.44 | 0.62 | 0.678 | 0.693 | 5.1 | -4.66 | 6.24 | Poor_Mixed | 3895 | 5735.2 | 1.472 | 0.761 | 5.83 | 0.711 | 6.34 | 0.4533 | 0.752 | 0.5113 | 0.5831 | 1 | 0.4108 | 0.4792 | 0.5876 | 0.5876 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1825 | 1581.9 | 896.8 | 135.9 | 182.8 | 28.9 | 1215.9 | 8068.6 | 33 | 45.5 | 102.6 | 99.8 | 89.2 | 107.3 | 43.3 | 33.5 | 1947.9 | 1317.9 | 2904.4 | 2227.6 | 1490.7 | 3718.6 | 1.144 | 1.131 | 1.28 | 0.87 | 0.904 | 0.949 | 7.95 | -8.87 | 8.65 | 0.959 | 0.713 | 0.825 | 7.89 | 6.74 | 8.11 | 0.712 | 0.777 | 0.723 | -6.15 | 6.76 | -5.61 | 0.917 | 0.758 | 0.814 | 8.35 | 4.99 | -8.34 | Very Poor_Mixed | 1317.9 | 1490.7 | 1.131 | 0.949 | 8.87 | 0.959 | 8.35 | 0.1256 | 0.6251 | 0.2721 | 0.2631 | 1 | 0.1378 | 0.2717 | 0.375 | 0.375 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1826 | 676.3 | 384.7 | 92.4 | 90.7 | 15.8 | 692.5 | 4419.9 | 51.8 | 28.6 | 88.6 | 87.2 | 77 | 92.5 | 38.1 | 23.5 | 7497.4 | 6965.4 | 8277.1 | 13267.8 | 11892.9 | 14207.6 | 1.77 | 1.707 | 1.716 | 0.654 | 0.688 | 0.63 | 4.73 | 6.55 | 4.65 | 0.643 | 0.535 | 0.6 | 3.25 | -4.15 | 3.49 | 0.641 | 0.556 | 0.547 | 3.23 | 3.9 | 3.85 | 0.673 | 0.669 | 0.629 | 4.07 | 3.3 | 3.73 | Fair_Mixed | 6965.4 | 11892.9 | 1.707 | 0.688 | 6.55 | 0.673 | 4.15 | 0.5458 | 0.815 | 0.6235 | 0.6314 | 1 | 0.5147 | 0.6193 | 0.6717 | 0.6717 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1827 | 1001.4 | 537.6 | 100.3 | 112.4 | 17.5 | 809.2 | 5032.2 | 46.2 | 33.9 | 92.8 | 90.3 | 82.6 | 99.4 | 40.1 | 24.4 | 5316.2 | 5641.2 | 6549.2 | 7450.5 | 8720.8 | 10184.8 | 1.401 | 1.546 | 1.555 | 0.763 | 0.781 | 0.715 | 5.86 | 6.48 | 5.59 | 0.724 | 0.737 | 0.692 | 4.99 | 4.03 | 5.52 | 0.674 | 0.731 | 0.64 | 4.86 | 3.17 | 4.18 | 0.705 | 0.679 | 0.709 | 6.98 | 5.31 | -5.47 | Poor_Mixed | 5316.2 | 7450.5 | 1.401 | 0.781 | 6.48 | 0.737 | 6.98 | 0.4425 | 0.7473 | 0.4907 | 0.6005 | 1 | 0.3884 | 0.446 | 0.5741 | 0.5741 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1828 | 1108.3 | 602.2 | 109.6 | 134.3 | 20.4 | 883.7 | 6430.3 | 57.6 | 22 | 79.5 | 80.2 | 72.8 | 82.7 | 35.9 | 14.7 | 7774 | 7587.7 | 7619 | 14271.9 | 13265.6 | 13598.6 | 1.836 | 1.748 | 1.785 | 0.5 | 0.544 | 0.512 | 2.52 | 2.67 | 2.67 | 0.513 | 0.516 | 0.558 | 2.79 | 2.94 | 2.77 | 0.634 | 0.611 | 0.548 | 2.73 | -2.57 | 3.08 | 0.631 | 0.556 | 0.554 | -3.16 | 3.52 | 2.72 | Poor_DGA | 7587.7 | 13265.6 | 1.748 | 0.544 | 2.67 | 0.634 | 3.52 | 0.3578 | 0.9283 | 0.8396 | 0.9014 | 1 | 0.8866 | 0.7247 | 0.7444 | 0.7444 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1829 | 1617.4 | 853.2 | 136.1 | 187.5 | 34.3 | 1230.4 | 7837.1 | 33.6 | 44.7 | 103.1 | 104.4 | 92.4 | 111.9 | 44.7 | 33.6 | 1420.3 | 2314.5 | 2320.3 | 1491.3 | 2709.7 | 2656 | 1.05 | 1.171 | 1.145 | 0.925 | 0.944 | 0.944 | 8.74 | 9.05 | -9.02 | 0.807 | 0.699 | 0.722 | -6.72 | -6.45 | 6.04 | 0.809 | 0.761 | 0.824 | 6.8 | 6.9 | 7.51 | 0.827 | 0.911 | 0.763 | 7.22 | 6.37 | 7.09 | Very Poor_Mixed | 1420.3 | 1491.3 | 1.05 | 0.944 | 9.05 | 0.911 | 7.51 | 0.1009 | 0.6328 | 0.1915 | 0.2591 | 1 | 0.0942 | 0.2837 | 0.3575 | 0.3575 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1830 | 199 | 209.6 | 74.4 | 60.1 | 1.2 | 505.7 | 2869.6 | 54.7 | 26.3 | 81.7 | 83 | 76.8 | 90.4 | 38.5 | 17.9 | 8261.2 | 8656.5 | 9297.5 | 15926.2 | 15323.3 | 17108.2 | 1.928 | 1.77 | 1.84 | 0.956 | 0.965 | 0.99 | 9.84 | -9.2 | -9.33 | 0.529 | 0.521 | 0.527 | -2 | -2.09 | -2.53 | 0.523 | 0.545 | 0.501 | -2.06 | 3.02 | 2.16 | 1.299 | 0.508 | 0.524 | 2.95 | 2 | 3.29 | Critical_Winding_TD_Cap | 8261.2 | 15323.3 | 1.77 | 0.99 | 9.84 | 1.299 | 3.29 | 0.8867 | 0.8489 | 0.7146 | 0.8114 | 1 | 0.0463 | 0.7895 | 0.7442 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_R_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_TV_TanDelta_pct
1831 | 811.1 | 500.5 | 106.7 | 118.3 | 17.8 | 837.7 | 5997.6 | 48.7 | 31.4 | 89.8 | 91.9 | 83.6 | 99.2 | 40 | 25.3 | 5091.3 | 4799.3 | 5627 | 7825.2 | 6538.5 | 8830 | 1.537 | 1.362 | 1.569 | 0.69 | 0.76 | 0.714 | -5.69 | 6.01 | -5.57 | 0.693 | 0.635 | 0.685 | -3.86 | 4.19 | 5.37 | 0.717 | 0.66 | 0.692 | 6.03 | 5.34 | -4.11 | 0.645 | 0.731 | 0.627 | 5.49 | -5.39 | 5.62 | Poor_Mixed | 4799.3 | 6538.5 | 1.362 | 0.76 | 6.01 | 0.731 | 6.03 | 0.4356 | 0.7778 | 0.4951 | 0.569 | 1 | 0.428 | 0.4698 | 0.5847 | 0.5847 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1832 | 100 | 167.2 | 70.3 | 60.6 | 2 | 350 | 2898.5 | 58.5 | 22.5 | 75 | 75.7 | 71.8 | 80 | 35.6 | 12.1 | 8995.5 | 10000 | 9538 | 17638.8 | 18986.5 | 18366 | 1.961 | 1.899 | 1.926 | 0.556 | 0.524 | 0.549 | 2.86 | 2.37 | 2.09 | 0.514 | 0.54 | 0.505 | -2.55 | 2.8 | 2 | 0.554 | 0.5 | 0.558 | -2.48 | 2.15 | 2.19 | 0.5 | 0.502 | 0.506 | -2 | -2 | 2.05 | Good_Mixed | 8995.5 | 17638.8 | 1.899 | 0.556 | 2.86 | 0.558 | 2.8 | 0.9024 | 0.9171 | 0.9635 | 0.964 | 1 | 0.8408 | 0.89 | 0.9181 | 0.9181 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1833 | 1479.3 | 883.3 | 135.8 | 163.3 | 32.3 | 1258.5 | 7912 | 33.7 | 46 | 102.6 | 109.3 | 90.9 | 113.5 | 44.3 | 31.6 | 2607 | 1579.5 | 1756 | 3259.6 | 1686.5 | 1966.5 | 1.25 | 1.068 | 1.12 | 0.929 | 0.941 | 0.902 | 8.95 | -9.21 | 9.06 | 0.807 | 0.806 | 0.909 | 5.43 | -5.98 | 6.27 | 0.814 | 0.904 | 0.867 | 7.85 | 6.12 | -7.5 | 0.895 | 0.934 | 0.716 | 7.36 | 6.13 | -6.95 | Very Poor_Mixed | 1579.5 | 1686.5 | 1.068 | 0.941 | 9.21 | 0.934 | 7.85 | 0.1327 | 0.6203 | 0.1709 | 0.3368 | 1 | 0.0967 | 0.2343 | 0.3572 | 0.3572 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1834 | 173.6 | 192.4 | 70.9 | 51.7 | 2.8 | 350 | 3323.1 | 55.8 | 24.1 | 76.2 | 75 | 70.5 | 80.7 | 35.2 | 16.5 | 8971.2 | 8143.2 | 9341 | 17399.1 | 15061.6 | 18322.7 | 1.939 | 1.85 | 1.962 | 0.548 | 0.542 | 0.546 | -2.63 | 2.61 | 3.02 | 0.537 | 0.542 | 0.539 | 3.12 | -2.57 | 2.69 | 0.5 | 0.5 | 0.5 | 3.25 | 2.6 | 3.03 | 0.505 | 0.514 | 0.581 | 2.81 | 2.65 | 2.69 | Good_Mixed | 8143.2 | 15061.6 | 1.85 | 0.548 | 3.02 | 0.581 | 3.25 | 0.8833 | 0.8857 | 0.9685 | 0.8522 | 1 | 0.8111 | 0.8484 | 0.8928 | 0.8928 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1835 | 987.5 | 523.7 | 107.1 | 130.9 | 14.1 | 837.4 | 6194.7 | 46.6 | 33.3 | 91.4 | 96.9 | 84.5 | 98.2 | 39.2 | 25.8 | 5763.6 | 6400.1 | 5251 | 8688.7 | 10235.8 | 8056.6 | 1.508 | 1.599 | 1.534 | 0.729 | 0.77 | 0.749 | 5.91 | -5.97 | 6.18 | 0.631 | 0.633 | 0.63 | 5.24 | 4.26 | 4.38 | 0.665 | 0.799 | 0.709 | 3.64 | 5.29 | -5.13 | 0.714 | 0.729 | 0.678 | -4.42 | 5.17 | 4.98 | Poor_Mixed | 5251 | 8056.6 | 1.508 | 0.77 | 6.18 | 0.799 | 5.29 | 0.4294 | 0.7544 | 0.458 | 0.5513 | 1 | 0.3887 | 0.4694 | 0.5702 | 0.5702 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1836 | 956.3 | 561.2 | 103.3 | 123.1 | 20.6 | 892.2 | 5150.5 | 59.1 | 21.8 | 77.3 | 81.7 | 74.1 | 84 | 35.7 | 12.9 | 10000 | 8559.2 | 9612.3 | 20000 | 15869.2 | 19041.8 | 2 | 1.854 | 1.981 | 0.537 | 0.533 | 0.54 | 2.35 | 2.86 | -3.05 | 0.509 | 0.5 | 0.56 | 2.3 | -2.39 | -2 | 0.543 | 0.508 | 0.5 | 2.01 | 2.27 | 2.42 | 0.5 | 0.559 | 0.5 | 2.94 | 2 | -2.5 | Poor_DGA | 8559.2 | 15869.2 | 1.854 | 0.54 | 3.05 | 0.56 | 2.94 | 0.4007 | 0.9331 | 0.832 | 0.9461 | 1 | 0.8267 | 0.8945 | 0.7794 | 0.7794 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1837 | 1449.6 | 817.8 | 128.9 | 172.4 | 31.2 | 1193.9 | 7808.1 | 35 | 45.1 | 101 | 103.6 | 90.4 | 108.1 | 42.8 | 30.5 | 690 | 1628.2 | 2563.8 | 1200 | 1749 | 3170.8 | 1.739 | 1.074 | 1.237 | 0.944 | 0.926 | 0.943 | 8.6 | 9.35 | 8.45 | 0.86 | 0.701 | 0.75 | 6.22 | -7.57 | -6.65 | 0.902 | 0.756 | 0.733 | 6.52 | 7.23 | 6.48 | 0.771 | 0.822 | 0.771 | 6.26 | 6.13 | -8.7 | Very Poor_Mixed | 690 | 1200 | 1.074 | 0.944 | 9.35 | 0.902 | 8.7 | 0.153 | 0.6289 | 0.2521 | 0.3787 | 1 | 0.1011 | 0.2878 | 0.3838 | 0.3838 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1838 | 1492.5 | 870 | 140 | 191.5 | 34.3 | 1236.6 | 8090.9 | 35.1 | 46.2 | 102.7 | 102.3 | 90.7 | 112.3 | 43.1 | 31.1 | 1302.1 | 1138.7 | 2817.7 | 1367.2 | 1228.3 | 3295.5 | 1.05 | 1.079 | 1.17 | 0.915 | 0.911 | 0.933 | 8.89 | 9.16 | -9.24 | 0.735 | 0.695 | 0.801 | 5.61 | 6.92 | -5.98 | 0.717 | 0.859 | 0.918 | 8.47 | 5.87 | 6.39 | 0.877 | 0.909 | 0.859 | 7.56 | 6.59 | 8.03 | Very Poor_Mixed | 1138.7 | 1228.3 | 1.05 | 0.933 | 9.24 | 0.918 | 8.47 | 0.0977 | 0.6184 | 0.2249 | 0.3559 | 1 | 0.0984 | 0.2584 | 0.3592 | 0.3592 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1839 | 203.4 | 144.4 | 72.9 | 56.9 | 2.6 | 374.6 | 2958.6 | 12.2 | 22.4 | 85.9 | 85.7 | 77 | 89.8 | 39 | 20.7 | 1732.9 | 690 | 690 | 1976.1 | 724.2 | 750.2 | 1.14 | 1.05 | 1.087 | 0.716 | 0.743 | 0.656 | 5.59 | 6.36 | 4.69 | 0.63 | 0.679 | 0.645 | 3.42 | 3.87 | 2.67 | 0.566 | 0.664 | 0.624 | 4.58 | 3.96 | 4.61 | 0.582 | 0.68 | 0.614 | 4.48 | -4.29 | -4.14 | Critical_IR_PI | 690 | 724.2 | 1.05 | 0.743 | 6.36 | 0.68 | 4.61 | 0.8743 | 0.336 | 0.6611 | 0.7244 | 0.85 | 0.4555 | 0.5698 | 0.6635 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
1840 | 1731.2 | 944.2 | 148.3 | 183.7 | 34.3 | 1251.7 | 8580.8 | 34.1 | 45.2 | 104.6 | 107.2 | 96 | 114.7 | 43 | 35.9 | 1647.1 | 821.7 | 1557 | 1779.6 | 1200 | 1768.2 | 1.08 | 1.46 | 1.136 | 0.931 | 0.93 | 0.921 | 9.55 | 9.2 | 8.58 | 0.816 | 0.947 | 0.798 | 6.44 | 6.7 | 6.42 | 0.785 | 0.949 | 0.899 | -9.69 | 9.62 | 6.71 | 0.843 | 0.902 | 0.967 | 6.62 | 9.77 | 8.1 | Very Poor_Mixed | 821.7 | 1200 | 1.08 | 0.931 | 9.55 | 0.967 | 9.77 | 0.0642 | 0.628 | 0.1458 | 0.1678 | 1 | 0.0926 | 0.1713 | 0.3182 | 0.3182 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1841 | 100 | 180.9 | 69.3 | 58.1 | 1.7 | 446.8 | 2770.7 | 60 | 23.1 | 75.8 | 75 | 70 | 80 | 36 | 12.8 | 8478.3 | 8139.3 | 9956.5 | 16341.6 | 15490 | 19913.1 | 1.927 | 1.903 | 2 | 0.528 | 0.542 | 0.541 | 2.7 | 3.2 | -2.52 | 0.53 | 0.528 | 0.517 | -2.5 | 2.12 | -2.53 | 0.533 | 0.51 | 0.521 | 2 | 2.28 | 2 | 0.506 | 0.5 | 0.52 | 2.29 | 2.37 | 2.47 | Good_Mixed | 8139.3 | 15490 | 1.903 | 0.542 | 3.2 | 0.533 | 2.53 | 0.8948 | 0.9047 | 0.9814 | 0.9484 | 1 | 0.8226 | 0.8757 | 0.9106 | 0.9106 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1842 | 1206.7 | 652.6 | 120.8 | 154.3 | 23.1 | 1048.1 | 6700.7 | 55.9 | 22.4 | 80.5 | 79.7 | 74.6 | 85.3 | 36.7 | 12.3 | 8192.1 | 7260.8 | 7661.8 | 14602 | 12859.5 | 13376.6 | 1.782 | 1.771 | 1.746 | 0.52 | 0.5 | 0.641 | 2 | 2.52 | 4.24 | 0.539 | 0.518 | 0.587 | 2.47 | -2.88 | -2.6 | 0.521 | 0.579 | 0.5 | 2.64 | 2.3 | -2.73 | 0.623 | 0.5 | 0.589 | 2.48 | 2.56 | -3.12 | Poor_DGA | 7260.8 | 12859.5 | 1.746 | 0.641 | 4.24 | 0.623 | 3.12 | 0.2807 | 0.9193 | 0.8037 | 0.9597 | 1 | 0.823 | 0.7913 | 0.7265 | 0.7265 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1843 | 954.9 | 615.5 | 112.5 | 118.1 | 16 | 828.8 | 5199.7 | 46.9 | 34 | 90.6 | 91.3 | 83.5 | 97.8 | 39.4 | 24.3 | 6371.3 | 6578.7 | 6827 | 10565.1 | 10705.7 | 11058.6 | 1.658 | 1.627 | 1.62 | 0.728 | 0.728 | 0.754 | 6.19 | -5.64 | 6.43 | 0.649 | 0.662 | 0.644 | 5.04 | 3.78 | 4.9 | 0.673 | 0.609 | 0.687 | -3.44 | 4.55 | -3.72 | 0.626 | 0.633 | 0.625 | -4.65 | 4.7 | 4.91 | Poor_Mixed | 6371.3 | 10565.1 | 1.62 | 0.754 | 6.43 | 0.687 | 5.04 | 0.4285 | 0.7461 | 0.5052 | 0.6039 | 1 | 0.3959 | 0.532 | 0.5886 | 0.5886 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1844 | 459.1 | 277.2 | 83.9 | 86.7 | 7 | 546.7 | 3177 | 51.3 | 29.8 | 84.4 | 83.4 | 76.1 | 90.3 | 37.4 | 17.5 | 6920.8 | 6581.1 | 8162.8 | 11622.6 | 10928.7 | 14742 | 1.679 | 1.661 | 1.806 | 0.593 | 0.656 | 0.59 | 3.83 | -3.87 | -4.01 | 0.62 | 0.57 | 0.559 | -3.17 | 3.17 | -3.55 | 0.679 | 0.571 | 0.557 | 3.6 | -3.37 | 2.88 | 0.626 | 0.583 | 0.692 | 3.25 | 3.67 | -4.09 | Fair_Mixed | 6581.1 | 10928.7 | 1.661 | 0.656 | 4.01 | 0.692 | 4.09 | 0.6905 | 0.7986 | 0.7025 | 0.8232 | 1 | 0.6453 | 0.6337 | 0.7443 | 0.7443 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1845 | 100 | 167.6 | 70.2 | 61.2 | 1 | 412.3 | 2500 | 31.8 | 48.8 | 80.6 | 80.7 | 74.3 | 87.2 | 37.1 | 13.2 | 5436.8 | 5390.6 | 5120.8 | 8399.2 | 7682.9 | 4725.1 | 1.545 | 1.425 | 0.923 | 0.622 | 0.65 | 0.643 | 4.42 | 4.02 | 4.46 | 0.556 | 0.58 | 0.597 | 3.29 | -3.69 | 3.1 | 0.552 | 0.553 | 0.554 | 3.3 | 3.51 | 2.81 | 0.616 | 0.564 | 0.556 | 2.84 | 3.26 | -3.46 | Critical_Oil | 5120.8 | 4725.1 | 0.923 | 0.65 | 4.46 | 0.616 | 3.69 | 0.9539 | 0.5942 | 0.7849 | 0.939 | 0.8125 | 0.5916 | 0.6978 | 0.7737 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
1846 | 904.6 | 577.4 | 101.3 | 119.4 | 18.6 | 809.8 | 5396.2 | 45.1 | 32.2 | 91.9 | 87.7 | 81.5 | 99.7 | 39.1 | 23.7 | 5258.1 | 5321.4 | 6665.8 | 7788.5 | 8244.7 | 10524.4 | 1.481 | 1.549 | 1.579 | 0.741 | 0.753 | 0.73 | 5.85 | 5.67 | 6.18 | 0.703 | 0.653 | 0.713 | 5.11 | -4.35 | 4.79 | 0.709 | 0.684 | 0.648 | 4.4 | 5.37 | 5.68 | 0.726 | 0.686 | 0.628 | 5.73 | 3.94 | 4.98 | Poor_Mixed | 5258.1 | 7788.5 | 1.481 | 0.753 | 6.18 | 0.726 | 5.73 | 0.4275 | 0.7678 | 0.5258 | 0.6246 | 1 | 0.402 | 0.4646 | 0.5827 | 0.5827 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1847 | 100 | 120 | 65 | 51 | 1 | 363.1 | 2500 | 60 | 20 | 76.5 | 78.9 | 70.5 | 83.2 | 35.5 | 12.4 | 6257.1 | 8172.6 | 6592.1 | 10422.1 | 14506.2 | 10577.4 | 1.666 | 1.775 | 1.605 | 0.566 | 0.626 | 0.573 | -3.24 | 3.82 | 3.34 | 0.579 | 0.531 | 0.548 | 2.33 | 2.17 | 2.73 | 0.532 | 0.542 | 0.542 | -2.11 | 2.29 | 2.59 | 0.518 | 0.559 | 0.521 | 2.28 | -2.3 | 3 | Fair_IR_PI | 6257.1 | 10422.1 | 1.605 | 0.626 | 3.82 | 0.579 | 3 | 0.9921 | 1 | 0.903 | 0.9575 | 1 | 0.703 | 0.7988 | 0.9084 | 0.9084 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1848 | 824.6 | 512.3 | 102.5 | 120.4 | 18.3 | 859.4 | 5024.2 | 56 | 25.6 | 78.3 | 78.6 | 73.8 | 85.9 | 35.6 | 12.6 | 9128.4 | 7961.5 | 8927.4 | 17127 | 14357.6 | 16764.6 | 1.876 | 1.803 | 1.878 | 0.563 | 0.59 | 0.563 | 3.1 | 3.06 | 2.53 | 0.528 | 0.568 | 0.5 | 3.19 | 2.69 | 2.61 | 0.58 | 0.584 | 0.562 | 2 | 2.45 | -2.51 | 0.579 | 0.516 | 0.538 | 2.09 | 2.25 | -2.52 | Poor_DGA | 7961.5 | 14357.6 | 1.803 | 0.59 | 3.1 | 0.584 | 3.19 | 0.4386 | 0.86 | 0.8422 | 0.953 | 1 | 0.7613 | 0.7872 | 0.753 | 0.753 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1849 | 1646 | 950.4 | 148.3 | 186.5 | 31.7 | 1315.3 | 8311.6 | 34.3 | 46.7 | 107.8 | 104.9 | 94.4 | 115.6 | 43.6 | 33.6 | 2213.4 | 2012.4 | 957.2 | 2514.3 | 2124.7 | 1200 | 1.136 | 1.056 | 1.254 | 0.99 | 0.99 | 0.958 | -9.77 | 9.84 | -9.62 | 0.849 | 0.954 | 0.804 | -7.58 | -7.28 | 8.56 | 0.798 | 0.923 | 0.713 | 6.53 | 5.56 | 7.6 | 0.784 | 0.855 | 0.829 | 6.21 | -5.97 | -5.39 | Very Poor_Mixed | 957.2 | 1200 | 1.056 | 0.99 | 9.84 | 0.954 | 8.56 | 0.0753 | 0.6137 | 0.1409 | 0.2591 | 1 | 0.0262 | 0.2452 | 0.3273 | 0.3273 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1850 | 603.2 | 356.6 | 83.9 | 83.8 | 7 | 609.1 | 3778.4 | 53.3 | 28 | 83.9 | 82.4 | 77.4 | 89.9 | 38.1 | 17.5 | 8434.8 | 6800.2 | 7703.7 | 15891.9 | 11244.9 | 13966.5 | 1.884 | 1.654 | 1.813 | 0.659 | 0.659 | 0.579 | -3.76 | 4.45 | -3.35 | 0.586 | 0.585 | 0.62 | 2.36 | 2.51 | -3.64 | 0.574 | 0.537 | 0.569 | 3.79 | 3.11 | 2.98 | 0.561 | 0.579 | 0.56 | -3.36 | 3.22 | -2.89 | Fair_Mixed | 6800.2 | 11244.9 | 1.654 | 0.659 | 4.45 | 0.62 | 3.79 | 0.6589 | 0.8235 | 0.7027 | 0.8232 | 1 | 0.6279 | 0.6966 | 0.7483 | 0.7483 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1851 | 1766 | 982.4 | 145.7 | 196.2 | 34.3 | 1379 | 8375.3 | 15.4 | 20.9 | 78.7 | 77.9 | 71.8 | 84.2 | 35.7 | 10 | 7286.7 | 6824.8 | 7261.1 | 12552.1 | 12079.5 | 12492.5 | 1.723 | 1.77 | 1.72 | 0.572 | 0.541 | 0.558 | 2.27 | -3.01 | -2.4 | 0.549 | 0.569 | 0.637 | 3.51 | 2.66 | 2.89 | 0.638 | 0.621 | 0.535 | 3.46 | 3.12 | 3.63 | 0.584 | 0.584 | 0.581 | 3.74 | -3.35 | 2.48 | Critical_DGA | 6824.8 | 12079.5 | 1.72 | 0.572 | 3.01 | 0.638 | 3.74 | 0.0385 | 0.374 | 0.8704 | 1 | 1 | 0.8079 | 0.6699 | 0.5852 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
1852 | 1409.3 | 766.8 | 131.8 | 159 | 28.3 | 1110.9 | 7371.6 | 35.7 | 42.8 | 98.3 | 98.1 | 87.2 | 108.7 | 43.2 | 35.2 | 2730.8 | 5046.1 | 2438 | 1637.3 | 7343.4 | 3061.2 | 0.6 | 1.455 | 1.256 | 0.868 | 0.908 | 0.845 | 7.92 | 8.33 | -6.41 | 0.728 | 0.755 | 0.812 | 4.76 | 6.97 | -6.58 | 0.842 | 0.788 | 0.852 | -8.13 | 7.25 | 6.08 | 0.744 | 0.754 | 0.719 | 7.5 | -5.63 | 6.07 | Critical_Mixed | 2438 | 1637.3 | 0.6 | 0.908 | 8.33 | 0.852 | 8.13 | 0.199 | 0.6514 | 0.3126 | 0.1958 | 0.8187 | 0.2105 | 0.3054 | 0.3844 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1853 | 1277.3 | 813.4 | 135.1 | 160.6 | 30.9 | 1216.4 | 7406 | 30.6 | 49.3 | 104.8 | 103.6 | 93.9 | 114.3 | 45 | 32.6 | 2716.8 | 1255.5 | 1213.7 | 3062.4 | 1406.6 | 1382.7 | 1.127 | 1.12 | 1.139 | 0.908 | 0.878 | 0.917 | 9.02 | 8.5 | 9.07 | 0.797 | 0.819 | 0.918 | 5.68 | 5.73 | -7.69 | 0.717 | 0.863 | 0.837 | 7.76 | 5.85 | -8.28 | 0.837 | 0.91 | 0.837 | 5.96 | -6.6 | 5.47 | Very Poor_Mixed | 1213.7 | 1382.7 | 1.12 | 0.917 | 9.07 | 0.918 | 8.28 | 0.1753 | 0.5897 | 0.1638 | 0.2982 | 1 | 0.1233 | 0.2479 | 0.3677 | 0.3677 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1854 | 801.6 | 487.4 | 103.3 | 109.6 | 16 | 782 | 5031.1 | 59.9 | 21.7 | 75 | 75 | 72.3 | 81.8 | 35.3 | 12.1 | 9339.7 | 9975.8 | 9234 | 17822.3 | 19682 | 17494.7 | 1.908 | 1.973 | 1.895 | 0.541 | 0.516 | 0.564 | 3.19 | 2.78 | -2 | 0.518 | 0.53 | 0.561 | 3.11 | 3.37 | -2.23 | 0.539 | 0.547 | 0.573 | -2.88 | 3.04 | 2.78 | 0.555 | 0.547 | 0.528 | 3.36 | 2.55 | 2.64 | Poor_DGA | 9234 | 17494.7 | 1.895 | 0.564 | 3.19 | 0.573 | 3.37 | 0.4777 | 0.9355 | 0.9645 | 0.964 | 1 | 0.8335 | 0.7682 | 0.7913 | 0.7913 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1855 | 1653.8 | 918.5 | 138.2 | 189.1 | 29.6 | 1235.8 | 8112.4 | 35.3 | 47.9 | 103.2 | 102.2 | 93.3 | 112 | 44.6 | 30.7 | 1117.5 | 1813.7 | 1694.7 | 1200 | 2268.6 | 1779.4 | 1.074 | 1.251 | 1.05 | 0.955 | 0.918 | 0.892 | 9.2 | -8.66 | 8.46 | 0.848 | 0.809 | 0.883 | -8.55 | 8.08 | 7.88 | 0.929 | 0.914 | 0.862 | 6.49 | 7.5 | 8.37 | 0.984 | 0.873 | 0.809 | -6.26 | 6.01 | 5.8 | Very Poor_Mixed | 1117.5 | 1200 | 1.05 | 0.955 | 9.2 | 0.984 | 8.55 | 0.1051 | 0.6025 | 0.1985 | 0.3711 | 1 | 0.1136 | 0.188 | 0.3467 | 0.3467 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1856 | 702.2 | 370.3 | 84.9 | 98.3 | 3.4 | 659.1 | 3964 | 31.8 | 49.4 | 83.1 | 84.4 | 78.2 | 91.5 | 38.6 | 13.6 | 5897.3 | 4157.1 | 4615.7 | 8988.5 | 5763.3 | 6860.3 | 1.524 | 1.386 | 1.486 | 0.663 | 0.635 | 0.624 | 4.83 | -4.48 | 4.55 | 0.511 | 0.572 | 0.564 | 3.18 | 2.89 | 3.31 | 0.54 | 0.622 | 0.548 | 2.26 | -2.82 | 3.28 | 0.525 | 0.567 | 0.544 | 2.43 | -12.8 | 2.95 | Critical_Oil | 4157.1 | 5763.3 | 1.386 | 0.663 | 4.83 | 0.622 | 12.8 | 0.6736 | 0.5888 | 0.6769 | 0.9294 | 1 | 0.5704 | 0.7221 | 0.723 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
1857 | 215.5 | 120 | 65 | 53.7 | 1 | 371.7 | 2543 | 59.8 | 20.8 | 75 | 78.2 | 70.2 | 80 | 35.7 | 14.3 | 9391.1 | 10000 | 9789.2 | 18116.1 | 18627.7 | 19578.3 | 1.929 | 1.863 | 2 | 0.553 | 0.598 | 0.506 | -2.98 | 2.86 | 2.72 | 0.559 | 0.522 | 0.526 | 2.19 | 2.03 | 2.82 | 0.521 | 0.5 | 0.558 | 2.93 | 2.12 | -2.2 | 0.503 | 0.512 | 0.504 | -2 | -3.01 | 2.41 | Good_Mixed | 9391.1 | 18116.1 | 1.863 | 0.598 | 2.98 | 0.559 | 3.01 | 0.9694 | 0.9605 | 0.9523 | 0.9118 | 1 | 0.8046 | 0.8635 | 0.9265 | 0.9265 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
1858 | 1564.8 | 961 | 137.4 | 184.8 | 33.8 | 1348.9 | 8241.9 | 33.6 | 45.3 | 109.3 | 107.2 | 95.8 | 119.2 | 45.7 | 33.9 | 1882.4 | 690 | 1297.3 | 2160.8 | 1200 | 1424.9 | 1.148 | 1.739 | 1.098 | 0.961 | 0.944 | 0.953 | 9.84 | 9.17 | 9.62 | 0.801 | 0.825 | 0.797 | -6.31 | 7.1 | 6.76 | 0.814 | 0.843 | 0.74 | -9.17 | 5.69 | 6.59 | 0.811 | 0.704 | 0.893 | 7.01 | 7.75 | 8.62 | Very Poor_Mixed | 690 | 1200 | 1.098 | 0.961 | 9.84 | 0.893 | 9.17 | 0.0781 | 0.627 | 0.079 | 0.2473 | 1 | 0.0537 | 0.2579 | 0.329 | 0.329 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1859 | 794 | 481.7 | 97.7 | 111.8 | 15.7 | 827.3 | 5529 | 46.8 | 35.1 | 89.3 | 90.8 | 85.6 | 97.7 | 40.3 | 24.7 | 6789.9 | 6787.1 | 5342.6 | 11163.1 | 10413 | 8082.4 | 1.644 | 1.534 | 1.513 | 0.743 | 0.752 | 0.744 | 4.89 | 6.06 | 6.48 | 0.638 | 0.71 | 0.651 | -4.53 | -5.39 | 4.22 | 0.718 | 0.679 | 0.705 | 5.49 | 4.05 | 4.32 | 0.791 | 0.736 | 0.763 | 5.2 | -6.54 | 5.26 | Poor_Mixed | 5342.6 | 8082.4 | 1.513 | 0.752 | 6.48 | 0.791 | 6.54 | 0.4719 | 0.7333 | 0.4988 | 0.59 | 1 | 0.4031 | 0.432 | 0.5796 | 0.5796 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1860 | 895.4 | 572.9 | 112.2 | 121.5 | 21.1 | 886.2 | 5488.2 | 57.1 | 22.9 | 80.2 | 79.4 | 74.9 | 84.5 | 35.9 | 16.1 | 9028.6 | 8379.3 | 8347.7 | 16417.9 | 16274.5 | 15663.6 | 1.818 | 1.942 | 1.876 | 0.52 | 0.523 | 0.533 | 2.57 | 2.26 | 2.97 | 0.534 | 0.648 | 0.57 | 2.59 | -2.21 | 2.91 | 0.538 | 0.564 | 0.561 | 3.09 | 3.28 | 3.11 | 0.568 | 0.599 | 0.544 | -3 | 2.75 | 2.95 | Poor_DGA | 8347.7 | 15663.6 | 1.818 | 0.533 | 2.97 | 0.648 | 3.28 | 0.3936 | 0.9088 | 0.8145 | 0.8635 | 1 | 0.8605 | 0.7188 | 0.7419 | 0.7419 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1861 | 834.7 | 534.2 | 100.3 | 122.5 | 18.5 | 791.3 | 5696 | 46.3 | 34.9 | 91.1 | 88.8 | 82.4 | 99.6 | 40 | 23.3 | 5996.7 | 5617.2 | 5615.7 | 9848.3 | 8939.4 | 8490.5 | 1.642 | 1.591 | 1.512 | 0.778 | 0.762 | 0.705 | 5.96 | -5.68 | -4.99 | 0.607 | 0.703 | 0.715 | 5.41 | 4.78 | 4.25 | 0.647 | 0.67 | 0.601 | 3.74 | 4.89 | 4.56 | 0.687 | 0.66 | 0.591 | 5.18 | -5.26 | 3.8 | Poor_Mixed | 5615.7 | 8490.5 | 1.512 | 0.778 | 5.96 | 0.715 | 5.41 | 0.4353 | 0.7356 | 0.5126 | 0.6382 | 1 | 0.4165 | 0.5147 | 0.5912 | 0.5912 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1862 | 1632.2 | 982.4 | 140 | 183.9 | 34.3 | 1310.9 | 8285.5 | 56.8 | 25.1 | 82.9 | 81.6 | 72.3 | 87.4 | 37.4 | 18.7 | 8347.1 | 7165 | 7138 | 15546 | 12558.7 | 12087.6 | 1.862 | 1.753 | 1.693 | 0.546 | 0.62 | 0.673 | -2.69 | 16.68 | -4.81 | 0.558 | 0.587 | 0.597 | 3.01 | -2.93 | -3.15 | 0.546 | 0.588 | 0.613 | 2.78 | 3.08 | 2.96 | 0.529 | 0.576 | 0.586 | 2.39 | -3.54 | 2 | Critical_DGA | 7138 | 12087.6 | 1.693 | 0.673 | 16.68 | 0.613 | 3.54 | 0.0711 | 0.8683 | 0.7729 | 0.7872 | 1 | 0.5494 | 0.7071 | 0.6028 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1863 | 289.9 | 240.9 | 81.6 | 72.2 | 2.8 | 517.9 | 3440.1 | 33.7 | 47.8 | 84.3 | 131.4 | 76.7 | 88 | 38.8 | 13.9 | 5206.5 | 6182.3 | 4376.5 | 7697.4 | 9613.5 | 6425.7 | 1.478 | 1.555 | 1.468 | 0.644 | 0.653 | 0.683 | 4.05 | 4.68 | 4.49 | 0.599 | 0.606 | 0.623 | 3.79 | 3.71 | -4.33 | 0.65 | 0.658 | 0.577 | 3.7 | -4.62 | 4.35 | 0.667 | 0.668 | 0.619 | 5 | -3.13 | -4.16 | Critical_Oil | 4376.5 | 6425.7 | 1.468 | 0.683 | 4.68 | 0.668 | 5 | 0.7933 | 0.6035 | 0.5379 | 0.9219 | 1 | 0.5628 | 0.5674 | 0.7116 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_LV>=110 C: critical LV winding temperature | Moisture_PPM
1864 | 550.7 | 300.5 | 84.2 | 88.6 | 1 | 556.9 | 3777.6 | 54.5 | 24.3 | 79.3 | 81.9 | 73.3 | 87.2 | 35.1 | 14.8 | 4557.5 | 3674.5 | 3635.3 | 6257.7 | 4988.7 | 5103.3 | 1.373 | 1.358 | 1.404 | 0.683 | 0.652 | 0.637 | 5.23 | 4.6 | -4.11 | 0.528 | 0.5 | 0.537 | 3.05 | 3.82 | 2.9 | 0.548 | 0.535 | 0.523 | 2 | 2.47 | -2.95 | 0.531 | 0.53 | 0.523 | 2.09 | 2.04 | 2.47 | Poor_IR_PI | 3635.3 | 4988.7 | 1.358 | 0.683 | 5.23 | 0.548 | 3.82 | 0.8183 | 0.8821 | 0.8037 | 0.8988 | 1 | 0.5518 | 0.8271 | 0.8219 | 0.8219 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1865 | 159 | 193.6 | 69.7 | 60.7 | 1.7 | 432.8 | 2500 | 55.1 | 27 | 76.4 | 77.4 | 71.7 | 81.7 | 36.1 | 13.5 | 8133.1 | 9032.2 | 8061.2 | 14697.5 | 17545.6 | 14676.2 | 1.807 | 1.943 | 1.821 | 0.622 | 0.588 | 0.535 | 3.4 | 2.32 | 2.26 | 0.544 | 0.5 | 0.544 | 2.34 | 2.57 | -2.05 | 0.5 | 0.504 | 0.507 | 2.16 | 3.07 | 2.71 | 0.5 | 0.5 | 0.54 | -2.52 | -2.77 | -2.54 | Fair_Oil | 8061.2 | 14676.2 | 1.807 | 0.622 | 3.4 | 0.544 | 3.07 | 0.8842 | 0.8382 | 0.9112 | 0.9318 | 1 | 0.7706 | 0.8939 | 0.8881 | 0.8881 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1866 | 754.3 | 464.3 | 97.2 | 98.2 | 14.7 | 698.7 | 4695.4 | 56.6 | 22.1 | 79 | 79.9 | 74.9 | 82.6 | 35.2 | 10 | 8890.4 | 8283.5 | 9022.7 | 16605 | 14934.2 | 17502.2 | 1.868 | 1.803 | 1.94 | 0.631 | 0.555 | 0.543 | 4.15 | 2.29 | 2.55 | 0.527 | 0.542 | 0.522 | 2.2 | 2.17 | 2.19 | 0.5 | 0.508 | 0.565 | -2 | 2 | 2.79 | 0.532 | 0.584 | 0.5 | -2.64 | 2.74 | 2 | Fair_DGA | 8283.5 | 14934.2 | 1.803 | 0.631 | 4.15 | 0.584 | 2.79 | 0.5231 | 0.926 | 0.8331 | 1 | 1 | 0.7558 | 0.8513 | 0.7943 | 0.7943 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1867 | 140 | 120 | 65 | 50 | 2.7 | 350 | 2500 | 57.7 | 20 | 75 | 78.8 | 71.7 | 81.6 | 35.6 | 12.1 | 9622.2 | 9925.4 | 9879.1 | 18667.6 | 19651.5 | 19758.3 | 1.94 | 1.98 | 2 | 0.526 | 0.558 | 0.5 | -2.4 | -2.21 | 2.28 | 0.5 | 0.533 | 0.528 | 2.14 | -2.24 | 2.15 | 0.547 | 0.538 | 0.5 | -2.85 | 2.42 | 2.07 | 0.543 | 0.525 | 0.524 | 2.77 | 2 | 2.75 | Good_Mixed | 9622.2 | 18667.6 | 1.94 | 0.558 | 2.4 | 0.547 | 2.85 | 0.9111 | 1 | 0.9225 | 0.964 | 1 | 0.8926 | 0.8525 | 0.9266 | 0.9266 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1868 | 100 | 199.3 | 73.9 | 66.3 | 1 | 469.6 | 3260.4 | 57.7 | 22.7 | 75 | 75.9 | 71.1 | 80 | 35 | 11.8 | 8581.7 | 8609.5 | 8770.1 | 16963.9 | 16652.6 | 15862 | 1.977 | 1.934 | 1.809 | 0.613 | 0.601 | 0.648 | -4.47 | 3.62 | 3.88 | 0.5 | 0.5 | 0.517 | 2.23 | 2.45 | 2.67 | 0.517 | 0.5 | 0.5 | 2.34 | 2.52 | 2.56 | 0.506 | 0.53 | 0.5 | 2 | 2.38 | -2.27 | Fair_Winding_TD_Cap | 8581.7 | 15862 | 1.809 | 0.648 | 4.47 | 0.53 | 2.67 | 0.9268 | 0.9129 | 0.9697 | 0.9703 | 1 | 0.6304 | 0.927 | 0.9019 | 0.9019 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
1869 | 876.8 | 544.6 | 102.8 | 123.5 | 20.1 | 798.1 | 5124 | 57.7 | 24 | 79.4 | 78 | 71.1 | 81.6 | 35.7 | 14.9 | 8193.2 | 9926.5 | 9021.7 | 14827.9 | 19107.9 | 16824.8 | 1.81 | 1.925 | 1.865 | 0.568 | 0.536 | 0.546 | 3.32 | -2.22 | 2.56 | 0.5 | 0.542 | 0.509 | 3.21 | 2 | -3.02 | 0.537 | 0.55 | 0.568 | -2.64 | 2.1 | 2.86 | 0.562 | 0.543 | 0.5 | 3.1 | -2.33 | 2.32 | Poor_DGA | 8193.2 | 14827.9 | 1.81 | 0.568 | 3.32 | 0.568 | 3.21 | 0.4236 | 0.8875 | 0.8829 | 0.8962 | 1 | 0.8097 | 0.8235 | 0.7671 | 0.7671 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1870 | 1483.2 | 836.8 | 127.7 | 164.7 | 26.8 | 1246.6 | 7611.1 | 33.1 | 45.8 | 102.6 | 107.9 | 93.6 | 112 | 45 | 29.8 | 1522.6 | 1471.5 | 3125.7 | 1726.7 | 1656.8 | 3606.2 | 1.134 | 1.126 | 1.154 | 0.927 | 0.954 | 0.946 | 8.71 | 8.56 | 8.65 | 0.828 | 0.786 | 0.85 | 6.12 | 6.86 | 7.36 | 0.803 | 0.805 | 0.823 | -8.02 | 6.19 | 6.21 | 0.823 | 0.696 | 0.868 | 7.27 | 7.55 | 7.59 | Very Poor_Mixed | 1471.5 | 1656.8 | 1.126 | 0.954 | 8.71 | 0.868 | 8.02 | 0.1734 | 0.6222 | 0.1656 | 0.4051 | 1 | 0.106 | 0.2581 | 0.3761 | 0.3761 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1871 | 432.1 | 237.5 | 69.8 | 67.1 | 4.9 | 516.3 | 3297.2 | 55.6 | 58 | 75 | 77.2 | 71 | 80.5 | 35.1 | 18.6 | 5672 | 6218.7 | 6889.4 | 8963 | 10321.1 | 11606.8 | 1.58 | 1.66 | 1.685 | 0.932 | 0.937 | 0.935 | 9.37 | 9.06 | -8.71 | 0.556 | 0.548 | 0.558 | 3.13 | 2.67 | 3.15 | 0.531 | 0.507 | 0.517 | -2.63 | 2.37 | 2.18 | 0.541 | 0.543 | 0.583 | -2.55 | -2.13 | 2.65 | Critical_Winding_TD_Cap | 5672 | 8963 | 1.58 | 0.937 | 9.37 | 0.583 | 3.15 | 0.76 | 0.5833 | 0.9527 | 0.7902 | 1 | 0.0907 | 0.7892 | 0.7095 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1872 | 252.8 | 179.7 | 70.5 | 70.9 | 2.7 | 520.9 | 3141.5 | 48.2 | 31.7 | 78.5 | 79.3 | 73.4 | 85.9 | 36.2 | 13 | 8124.1 | 6689.3 | 6888.3 | 14738.1 | 11060.7 | 12099 | 1.814 | 1.653 | 1.756 | 0.554 | 0.561 | 0.578 | 2.87 | -2.88 | -2.76 | 0.5 | 0.523 | 0.5 | 2.76 | 3.81 | 3.09 | 0.583 | 0.524 | 0.5 | 2.99 | 3.29 | -2.92 | 0.634 | 0.593 | 0.568 | 2.65 | 2.54 | -2.43 | Fair_Oil | 6689.3 | 11060.7 | 1.653 | 0.578 | 2.88 | 0.634 | 3.81 | 0.8163 | 0.7741 | 0.8343 | 0.9438 | 1 | 0.7758 | 0.7941 | 0.8392 | 0.8392 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1873 | 1551.7 | 953.2 | 137.6 | 178.9 | 32 | 1264.2 | 8348.1 | 35 | 45.2 | 109 | 106 | 94.9 | 115.3 | 45.6 | 32 | 690 | 953.4 | 1645 | 1200 | 1200 | 1811.6 | 1.739 | 1.259 | 1.101 | 0.957 | 0.963 | 0.981 | -9.84 | 9.52 | -9.3 | 0.869 | 0.778 | 0.85 | 6.9 | -5.86 | -8.2 | 0.79 | 0.944 | 0.829 | 7.6 | 6.1 | -9.77 | 0.733 | 0.912 | 0.81 | -7.3 | 6.41 | 8.03 | Very Poor_Mixed | 690 | 1200 | 1.101 | 0.981 | 9.84 | 0.944 | 9.77 | 0.1003 | 0.628 | 0.1124 | 0.3214 | 1 | 0.0437 | 0.2241 | 0.3342 | 0.3342 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1874 | 852.2 | 564.3 | 101.2 | 121 | 18.5 | 876.7 | 5918.1 | 44.8 | 34.1 | 91.3 | 94.9 | 79.7 | 95.7 | 40.4 | 26.7 | 6741.8 | 6466.2 | 5880.1 | 10962.7 | 10126 | 9578 | 1.626 | 1.566 | 1.629 | 0.782 | 0.717 | 0.702 | 5.84 | -5.5 | 4.51 | 0.595 | 0.698 | 0.598 | 3.52 | 4.74 | 5.21 | 0.616 | 0.684 | 0.706 | 5.1 | 5.55 | 4.5 | 0.703 | 0.659 | 0.73 | -4.03 | -4.54 | 5.13 | Poor_Mixed | 5880.1 | 9578 | 1.566 | 0.782 | 5.84 | 0.73 | 5.55 | 0.4183 | 0.7449 | 0.5065 | 0.5192 | 1 | 0.4441 | 0.498 | 0.5824 | 0.5824 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1875 | 1516.6 | 857.1 | 138.5 | 183.3 | 23.9 | 1260.9 | 8006.2 | 34 | 45.8 | 105.6 | 106.1 | 93.4 | 115 | 44.2 | 33.6 | 1169.2 | 1871.7 | 1925.4 | 1242.4 | 2089.6 | 2113.1 | 1.063 | 1.116 | 1.097 | 0.926 | 0.831 | 0.906 | -8.92 | 8.01 | 7.87 | 0.776 | 0.854 | 0.901 | 5.96 | 6.25 | 7.06 | 0.871 | 0.852 | 0.878 | 5.51 | 6.78 | 7.55 | 0.726 | 0.712 | 0.825 | 8.27 | -8.09 | 7.99 | Very Poor_Mixed | 1169.2 | 1242.4 | 1.063 | 0.926 | 8.92 | 0.901 | 8.27 | 0.1529 | 0.6222 | 0.1506 | 0.2591 | 1 | 0.1636 | 0.2467 | 0.3682 | 0.3682 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1876 | 936.9 | 612.2 | 117 | 130.9 | 22.1 | 880.9 | 5865.9 | 45.5 | 32.4 | 91.4 | 89.5 | 81.5 | 97.2 | 40 | 22.2 | 6513 | 4745.5 | 5273.2 | 10126.8 | 6761.3 | 7890.7 | 1.555 | 1.425 | 1.496 | 0.731 | 0.776 | 0.744 | 4.94 | -6.59 | 5.8 | 0.671 | 0.724 | 0.685 | -5.2 | 4.29 | 4.7 | 0.671 | 0.697 | 0.692 | 5.53 | -3.99 | 4.08 | 0.709 | 0.706 | 0.6 | 3.51 | -4.43 | 4.51 | Poor_Mixed | 4745.5 | 6761.3 | 1.425 | 0.776 | 6.59 | 0.724 | 5.53 | 0.3645 | 0.7654 | 0.5237 | 0.6753 | 1 | 0.4017 | 0.4815 | 0.572 | 0.572 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1877 | 720.2 | 480.2 | 98 | 106.2 | 18.9 | 834.1 | 4752.2 | 55.9 | 25 | 79.7 | 79.3 | 72.2 | 85.3 | 36.2 | 10.5 | 10000 | 8850.3 | 8371.7 | 20000 | 16886.1 | 16503.3 | 2 | 1.908 | 1.971 | 0.559 | 0.523 | 0.531 | 2.03 | -2.19 | 3.11 | 0.564 | 0.549 | 0.555 | 3.49 | -3.46 | -2.43 | 0.603 | 0.536 | 0.579 | 2 | 2.33 | 2.39 | 0.5 | 0.534 | 0.533 | 2.52 | 3.39 | 2.34 | Fair_DGA | 8371.7 | 16503.3 | 1.908 | 0.559 | 3.11 | 0.603 | 3.49 | 0.4701 | 0.87 | 0.8366 | 0.994 | 1 | 0.852 | 0.7752 | 0.7741 | 0.7741 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1878 | 153.5 | 225 | 70.1 | 68.7 | 1 | 357.2 | 3048.3 | 56.4 | 22.8 | 75 | 76 | 70.8 | 81.4 | 35 | 11.5 | 4272.3 | 3906.9 | 3841.3 | 6140.2 | 5279 | 5068.3 | 1.437 | 1.351 | 1.319 | 0.639 | 0.632 | 0.703 | -4.86 | 3.82 | 5.76 | 0.518 | 0.523 | 0.56 | 2.58 | -2.36 | 2.41 | 0.534 | 0.507 | 0.561 | -2.82 | 2.47 | 2.3 | 0.532 | 0.549 | 0.537 | 3.42 | 2.33 | 3.14 | Poor_IR_PI | 3841.3 | 5068.3 | 1.319 | 0.703 | 5.76 | 0.561 | 3.42 | 0.9385 | 0.9108 | 0.9646 | 0.9764 | 1 | 0.5429 | 0.8028 | 0.8697 | 0.8697 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
1879 | 954.4 | 500.2 | 108.2 | 128.9 | 19.2 | 893.7 | 5357.9 | 45.9 | 34.9 | 90.4 | 93.1 | 82.9 | 96.2 | 39.4 | 25.1 | 5680.5 | 6153.6 | 6071.2 | 8497.6 | 9807.1 | 9876.6 | 1.496 | 1.594 | 1.627 | 0.762 | 0.726 | 0.742 | 6.22 | 6.07 | 5.56 | 0.719 | 0.647 | 0.739 | 4.9 | 6 | 5.08 | 0.743 | 0.691 | 0.613 | -4.04 | 6.07 | -5.84 | 0.797 | 0.619 | 0.773 | 4.96 | 5.43 | 5.78 | Poor_Mixed | 5680.5 | 8497.6 | 1.496 | 0.762 | 6.22 | 0.797 | 6.07 | 0.4046 | 0.7356 | 0.5067 | 0.576 | 1 | 0.3976 | 0.4283 | 0.5617 | 0.5617 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1880 | 187.3 | 145.4 | 65 | 60 | 1 | 353.1 | 3109.6 | 43.8 | 34.9 | 76.6 | 78.3 | 71.2 | 81.9 | 35 | 13.2 | 7330.7 | 7352 | 5944.2 | 11612.4 | 12525.4 | 9525.7 | 1.584 | 1.704 | 1.603 | 0.546 | 0.599 | 0.621 | 2.89 | 3.57 | 3.45 | 0.584 | 0.551 | 0.561 | -4.1 | 3.11 | 3.38 | 0.577 | 0.541 | 0.523 | 3.1 | 2.83 | 2.6 | 0.631 | 0.621 | 0.5 | 2.98 | 3.05 | 2.78 | Poor_Oil | 5944.2 | 9525.7 | 1.584 | 0.621 | 3.57 | 0.631 | 4.1 | 0.9603 | 0.7356 | 0.908 | 0.939 | 1 | 0.7146 | 0.7287 | 0.8573 | 0.8573 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1881 | 454.9 | 316.3 | 89.2 | 87.4 | 73.9 | 615 | 3975.6 | 30.6 | 47.1 | 82.3 | 77.1 | 71.2 | 85.4 | 36.9 | 15.2 | 5102.2 | 4540.9 | 3860.5 | 7143.1 | 6600.3 | 5407.2 | 1.4 | 1.454 | 1.401 | 0.718 | 0.657 | 0.666 | -5.65 | 3.74 | 4.79 | 0.559 | 0.572 | 0.544 | 3.14 | 3.39 | -3.83 | 0.576 | 0.595 | 0.556 | 3.23 | 3.78 | 2.98 | 0.553 | 0.559 | 0.621 | 2.44 | 2.53 | 2.21 | Critical_Oil | 3860.5 | 5407.2 | 1.4 | 0.718 | 5.65 | 0.621 | 3.83 | 0.4929 | 0.61 | 0.8419 | 0.8882 | 1 | 0.5253 | 0.7063 | 0.6857 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1882 | 1594.3 | 960.7 | 144 | 184.8 | 31.9 | 1276.3 | 8402.1 | 54.7 | 25 | 77.6 | 75 | 70.6 | 82.8 | 36 | 12.5 | 60.1 | 8668.6 | 8570.2 | 97 | 16488.8 | 15702 | 1.614 | 1.902 | 1.832 | 0.625 | 0.616 | 0.614 | 3.71 | -4.49 | 3.99 | 0.571 | 0.566 | 0.644 | -4.19 | 2.97 | 2.33 | 0.546 | 0.55 | 0.545 | 2.77 | 2.69 | 4.15 | 0.541 | 0.595 | 0.56 | 2.62 | 4.12 | -3.78 | Critical_DGA | 60.1 | 97 | 1.614 | 0.625 | 4.49 | 0.644 | 4.19 | 0.0849 | 0.87 | 0.9378 | 0.9552 | 0.85 | 0.6279 | 0.7021 | 0.6174 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
1883 | 471.4 | 289.4 | 81.5 | 75 | 3.6 | 618.7 | 3745.7 | 25.6 | 47.2 | 85.8 | 85.9 | 76.4 | 90.2 | 37 | 10 | 5923.3 | 5686 | 5676.4 | 8983.9 | 8815.6 | 8411.8 | 1.517 | 1.55 | 1.482 | 0.646 | 0.709 | 0.719 | -4.35 | -5.15 | 5.32 | 0.555 | 0.569 | 0.576 | 2.51 | -2.84 | 2.58 | 0.556 | 0.51 | 0.564 | 3.51 | 2.79 | 2.59 | 0.558 | 0.547 | 0.552 | 2.45 | 2.87 | -3.18 | Critical_Oil | 5676.4 | 8411.8 | 1.482 | 0.719 | 5.32 | 0.576 | 3.51 | 0.7351 | 0.0257 | 0.6742 | 1 | 1 | 0.5021 | 0.7507 | 0.6697 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1884 | 1432.5 | 785.5 | 136.2 | 183.5 | 26.3 | 1162.1 | 7675.9 | 34.3 | 45.1 | 103.2 | 100.4 | 92.5 | 114.2 | 43.5 | 30.7 | 2450.7 | 1735.3 | 2611.1 | 2875.2 | 1822.1 | 3113.7 | 1.173 | 1.05 | 1.192 | 0.885 | 0.904 | 0.935 | -8.45 | 9.17 | 8.62 | 0.897 | 0.867 | 0.841 | 5.91 | -5.56 | -8.22 | 0.864 | 0.812 | 0.912 | -5.34 | 5.09 | -8.16 | 0.794 | 0.902 | 0.94 | 5.36 | -7.13 | 6.12 | Very Poor_Mixed | 1735.3 | 1822.1 | 1.05 | 0.935 | 9.17 | 0.94 | 8.22 | 0.1713 | 0.6289 | 0.2104 | 0.3711 | 1 | 0.1243 | 0.2258 | 0.3759 | 0.3759 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1885 | 352.6 | 288.5 | 74.1 | 76.8 | 5.6 | 606.7 | 3457.9 | 55.6 | 27.7 | 84.6 | 82.6 | 76.9 | 91.7 | 38.2 | 19.4 | 7221.9 | 7654.6 | 7428.6 | 12478.3 | 13758.4 | 13135.5 | 1.728 | 1.797 | 1.768 | 0.546 | 0.561 | 0.553 | 3.46 | 2.94 | 3.48 | 0.555 | 0.583 | 0.601 | 3.27 | 2.87 | 3.49 | 0.603 | 0.608 | 0.61 | -3.68 | -2.48 | 3.72 | 0.5 | 0.538 | 0.55 | 3.27 | -3.3 | -3.07 | Fair_Mixed | 7221.9 | 12478.3 | 1.728 | 0.561 | 3.48 | 0.61 | 3.72 | 0.7225 | 0.8279 | 0.6898 | 0.7656 | 1 | 0.7619 | 0.7081 | 0.7814 | 0.7814 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1886 | 1091.9 | 650.3 | 113.7 | 145.5 | 20.4 | 923.8 | 6404.2 | 59.4 | 21.9 | 76 | 78.9 | 70 | 81.2 | 35.3 | 12.1 | 9452.6 | 9407.4 | 9834.7 | 17605.6 | 18258.5 | 19669.5 | 1.863 | 1.941 | 2 | 0.547 | 0.518 | 0.5 | 2.46 | -2.6 | 2 | 0.515 | 0.5 | 0.507 | 2.05 | 2.68 | 2.18 | 0.542 | 0.531 | 0.5 | 2.45 | 3.17 | 2 | 0.513 | 0.522 | 0.582 | 2.02 | 2.1 | -2.38 | Poor_DGA | 9407.4 | 17605.6 | 1.863 | 0.547 | 2.6 | 0.582 | 3.17 | 0.3359 | 0.9307 | 0.9275 | 0.964 | 1 | 0.9017 | 0.8698 | 0.7794 | 0.7794 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1887 | 1479.1 | 885.3 | 138.5 | 175.5 | 29.6 | 1264.3 | 7553.7 | 34.8 | 44.4 | 102.7 | 103.2 | 90.1 | 109 | 43.6 | 31 | 3623.1 | 1294.8 | 2936.8 | 4650.3 | 1372.4 | 3551.6 | 1.284 | 1.06 | 1.209 | 0.865 | 0.934 | 0.936 | 8.04 | 8.86 | -8.86 | 0.752 | 0.894 | 0.836 | -7.11 | -5.97 | 6.89 | 0.849 | 0.796 | 0.768 | 7.73 | -8.98 | 5.95 | 0.829 | 0.845 | 0.864 | 7.81 | -6.3 | -6.22 | Very Poor_Mixed | 1294.8 | 1372.4 | 1.06 | 0.936 | 8.86 | 0.894 | 8.98 | 0.1362 | 0.6357 | 0.2362 | 0.3597 | 1 | 0.1302 | 0.2428 | 0.3739 | 0.3739 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1888 | 540.4 | 302.3 | 78.8 | 87.5 | 7.4 | 617.9 | 3590.9 | 54.4 | 26 | 83.7 | 83.5 | 73.9 | 90.2 | 38 | 15.6 | 9292 | 8503.6 | 7379 | 17341.5 | 15775.5 | 11981.4 | 1.866 | 1.855 | 1.624 | 0.575 | 0.623 | 0.543 | 3.41 | 4.38 | 3.48 | 0.533 | 0.546 | 0.513 | 3.44 | 3.54 | 2.68 | 0.536 | 0.572 | 0.523 | -3.46 | 3.15 | -3.98 | 0.573 | 0.592 | 0.633 | 3.32 | 2.92 | 2.32 | Fair_Mixed | 7379 | 11981.4 | 1.624 | 0.623 | 4.38 | 0.633 | 3.98 | 0.6654 | 0.8536 | 0.7209 | 0.8773 | 1 | 0.6973 | 0.7317 | 0.7741 | 0.7741 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1889 | 1574.6 | 879.5 | 144.3 | 185 | 34.3 | 1379 | 8325 | 33.2 | 45.1 | 107.5 | 109.2 | 92.2 | 116.9 | 44 | 32 | 2343.6 | 1949.9 | 2304.3 | 2633.3 | 2383.3 | 2674.8 | 1.124 | 1.222 | 1.161 | 0.877 | 0.963 | 0.891 | 7.76 | 9.08 | 8.08 | 0.769 | 0.771 | 0.722 | 6.78 | 6.47 | 7.55 | 0.689 | 0.75 | 0.799 | 7.44 | 8.21 | 6.17 | 0.83 | 0.709 | 0.911 | 7.58 | -8.17 | 7.91 | Very Poor_Mixed | 1949.9 | 2383.3 | 1.124 | 0.963 | 9.08 | 0.911 | 8.21 | 0.0741 | 0.6289 | 0.122 | 0.3214 | 1 | 0.1455 | 0.2846 | 0.3539 | 0.3539 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1890 | 1441.9 | 808.7 | 129.3 | 170.8 | 28.4 | 1185.6 | 7802 | 35.4 | 43.4 | 105.2 | 106.7 | 93.3 | 112.3 | 43.8 | 29.4 | 2488.6 | 3323.5 | 2654.6 | 2798.9 | 4088.5 | 3261.6 | 1.125 | 1.23 | 1.229 | 0.894 | 0.919 | 0.929 | 8.43 | -8.62 | 8.88 | 0.868 | 0.826 | 0.903 | 6.62 | 6.75 | 7.02 | 0.836 | 0.738 | 0.693 | 6.03 | -6.97 | 7.15 | 0.893 | 0.775 | 0.815 | 7.51 | 5.09 | 7.29 | Very Poor_Mixed | 2488.6 | 2798.9 | 1.125 | 0.929 | 8.88 | 0.903 | 7.51 | 0.1696 | 0.6455 | 0.1665 | 0.4201 | 1 | 0.1253 | 0.2629 | 0.3824 | 0.3824 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1891 | 851.3 | 540 | 115.5 | 117.1 | 18 | 821.3 | 5723.5 | 47.2 | 32.6 | 94.5 | 95.5 | 83 | 100.3 | 40.5 | 26.4 | 5688.5 | 5981 | 5883 | 8881.3 | 8119.8 | 8733.2 | 1.561 | 1.358 | 1.484 | 0.783 | 0.755 | 0.747 | -6.48 | 5.58 | 7.02 | 0.656 | 0.708 | 0.612 | 5.96 | 3.08 | 4.77 | 0.662 | 0.703 | 0.706 | 4.35 | 4.13 | 4.68 | 0.626 | 0.703 | 0.715 | -5.13 | -4.02 | 5.25 | Poor_Mixed | 5688.5 | 8119.8 | 1.358 | 0.783 | 7.02 | 0.715 | 5.96 | 0.4265 | 0.7629 | 0.4375 | 0.5299 | 1 | 0.3601 | 0.4862 | 0.5663 | 0.5663 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1892 | 890.1 | 590.1 | 105.4 | 132.9 | 19.4 | 861.7 | 5935.3 | 44 | 35.3 | 88.7 | 92.7 | 82.9 | 98 | 39.6 | 27.1 | 5494.1 | 5414.7 | 4605 | 8627.1 | 8315.7 | 6550.6 | 1.57 | 1.536 | 1.422 | 0.706 | 0.734 | 0.727 | -5.81 | 6.18 | 6.18 | 0.683 | 0.678 | 0.706 | 4.58 | 4.55 | 4.98 | 0.681 | 0.761 | 0.673 | -5.21 | -4.13 | 4.1 | 0.69 | 0.734 | 0.597 | 4.55 | 5.12 | 5.72 | Poor_Mixed | 4605 | 6550.6 | 1.422 | 0.734 | 6.18 | 0.761 | 5.72 | 0.3944 | 0.731 | 0.5103 | 0.5047 | 1 | 0.41 | 0.4646 | 0.5636 | 0.5636 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1893 | 429.1 | 303.2 | 85.3 | 84.9 | 8.2 | 600 | 3958.4 | 50.1 | 29.3 | 83 | 79.1 | 78.3 | 89.1 | 38.8 | 18.8 | 7175.6 | 6987.7 | 7139.2 | 12287.5 | 11526.4 | 12341 | 1.712 | 1.65 | 1.729 | 0.685 | 0.674 | 0.639 | 4.44 | -4.73 | 4.78 | 0.601 | 0.596 | 0.592 | 2.96 | 3.87 | 3.53 | 0.618 | 0.615 | 0.587 | 3.45 | 3.5 | 2.75 | 0.608 | 0.599 | 0.568 | 3.71 | -3.58 | 3.73 | Fair_Mixed | 6987.7 | 11526.4 | 1.65 | 0.685 | 4.78 | 0.618 | 3.87 | 0.6653 | 0.8054 | 0.731 | 0.7841 | 1 | 0.5426 | 0.6385 | 0.7262 | 0.7262 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1894 | 565.9 | 273.7 | 76.1 | 67.6 | 3.4 | 507.7 | 3184.4 | 34.9 | 79.7 | 79 | 78.1 | 71.7 | 84.9 | 36.5 | 14.1 | 5158.3 | 5450.8 | 5220 | 7636.5 | 8048.2 | 7836.9 | 1.48 | 1.477 | 1.501 | 0.651 | 0.674 | 0.677 | -4.29 | -4.2 | 3.98 | 0.503 | 0.527 | 0.565 | 3.03 | 3.92 | 3.45 | 0.599 | 0.595 | 0.621 | 3.37 | 3.36 | 2.93 | 0.575 | 0.563 | 0.568 | 3.8 | 2.09 | -3.84 | Critical_Oil | 5158.3 | 7636.5 | 1.477 | 0.677 | 4.29 | 0.621 | 3.92 | 0.7656 | 0.5833 | 0.8593 | 0.9169 | 1 | 0.5701 | 0.7083 | 0.7605 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1895 | 965.5 | 608.1 | 104.7 | 122.9 | 21.3 | 811.8 | 5617.6 | 45.8 | 34.6 | 93.2 | 94.1 | 84.3 | 102.9 | 40.9 | 24.4 | 5197.8 | 4950.6 | 6106.7 | 7785.4 | 7505.9 | 9756.1 | 1.498 | 1.516 | 1.598 | 0.734 | 0.736 | 0.687 | 6.35 | -5.73 | 4.68 | 0.728 | 0.659 | 0.719 | 4.96 | 4.83 | 4.84 | 0.686 | 0.727 | 0.683 | 6.83 | 3.72 | 5.69 | 0.733 | 0.671 | 0.685 | 5.14 | 6.14 | 5.36 | Poor_Mixed | 4950.6 | 7505.9 | 1.498 | 0.736 | 6.35 | 0.733 | 6.83 | 0.3951 | 0.7391 | 0.4305 | 0.6005 | 1 | 0.4398 | 0.433 | 0.5601 | 0.5601 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1896 | 1576.2 | 871.1 | 132.7 | 171.8 | 34.3 | 1215.7 | 7941.3 | 33.6 | 45.8 | 104.1 | 106.3 | 95.3 | 116.5 | 43.8 | 32.8 | 2781.3 | 1464.1 | 2390.2 | 3448.8 | 1698.2 | 2912.8 | 1.24 | 1.16 | 1.219 | 0.895 | 0.99 | 0.947 | 8.32 | 9.28 | 8.93 | 0.806 | 0.709 | 0.815 | 6.9 | 8.39 | 8.74 | 0.841 | 0.735 | 0.849 | -8.69 | 8.7 | 5.12 | 0.775 | 0.783 | 0.719 | 6.19 | 6.3 | 5.82 | Very Poor_Mixed | 1464.1 | 1698.2 | 1.16 | 0.99 | 9.28 | 0.849 | 8.74 | 0.1179 | 0.6222 | 0.1427 | 0.2904 | 1 | 0.0951 | 0.2802 | 0.3567 | 0.3567 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1897 | 288.9 | 218.1 | 73.4 | 116.7 | 1 | 476.3 | 2627.1 | 59.3 | 23.5 | 97.6 | 97.5 | 86.2 | 104.8 | 41 | 12 | 9402.8 | 9149.5 | 9922.2 | 18395 | 17770.6 | 18883.3 | 1.956 | 1.942 | 1.903 | 0.527 | 0.529 | 0.506 | 2.82 | -2 | -2 | 0.583 | 0.52 | 0.599 | 2 | -2.47 | 2.85 | 0.532 | 0.512 | 0.527 | 3.74 | 2.92 | 2.7 | 0.511 | 0.5 | 0.538 | 2.98 | 3.38 | 3.06 | Poor_Thermal | 9149.5 | 17770.6 | 1.903 | 0.529 | 2.82 | 0.599 | 3.74 | 0.8486 | 0.8969 | 0.361 | 0.9661 | 1 | 0.9018 | 0.8042 | 0.8352 | 0.8352 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1898 | 138.8 | 180.7 | 71.5 | 50 | 1 | 395.2 | 2712.9 | 57.9 | 20.9 | 78.1 | 79.9 | 73.1 | 83.3 | 36.7 | 12.3 | 9598.8 | 8711.8 | 8711.4 | 18263.5 | 15931.4 | 16243.5 | 1.903 | 1.829 | 1.865 | 0.764 | 0.737 | 0.793 | 7.32 | 5.63 | -6.98 | 0.553 | 0.502 | 0.509 | 3.32 | 2.06 | 2 | 0.54 | 0.515 | 0.581 | 2.4 | 2.81 | 2.8 | 0.5 | 0.555 | 0.529 | -2.91 | 3.44 | 2.63 | Poor_Winding_TD_Cap | 8711.4 | 15931.4 | 1.829 | 0.793 | 7.32 | 0.581 | 3.44 | 0.9714 | 0.9574 | 0.8458 | 0.9597 | 1 | 0.3427 | 0.8256 | 0.8469 | 0.8469 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
1899 | 349.2 | 268 | 76.8 | 71.5 | 4.9 | 442.2 | 3605.8 | 55.4 | 24.2 | 76 | 75 | 70.3 | 81.9 | 36.1 | 15.7 | 8991.6 | 8815.3 | 8986.9 | 16801.2 | 17137.9 | 17412.1 | 1.869 | 1.944 | 1.937 | 0.558 | 0.571 | 0.577 | 2.84 | 3.08 | 2.78 | 0.543 | 0.56 | 0.528 | 2.45 | 2.46 | 2.11 | 0.534 | 0.536 | 0.731 | -2.04 | -2.75 | -4.62 | 0.585 | 0.508 | 0.58 | -3.26 | 2.12 | 2.75 | Poor_Bushing_TD_Cap | 8815.3 | 16801.2 | 1.869 | 0.577 | 3.08 | 0.731 | 4.62 | 0.764 | 0.8839 | 0.9638 | 0.8746 | 1 | 0.7651 | 0.7463 | 0.8386 | 0.8386 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1900 | 390.4 | 300.1 | 80.7 | 142.2 | 1.8 | 616.9 | 3748.8 | 53 | 29.6 | 108.8 | 109.3 | 97.1 | 119 | 44.9 | 15.1 | 9045.8 | 8383.1 | 9811.1 | 17774.1 | 16087.4 | 9107.2 | 1.965 | 1.919 | 0.928 | 0.607 | 0.634 | 0.629 | -3.6 | -3.36 | 4.31 | 0.585 | 0.644 | 0.622 | -3.83 | 3.74 | 2.99 | 0.587 | 0.575 | 0.586 | 2.66 | -2.61 | 2.49 | 0.546 | 0.646 | 0.611 | 3.08 | 3.36 | 3.62 | Critical_Thermal | 8383.1 | 9107.2 | 0.928 | 0.634 | 4.31 | 0.646 | 3.83 | 0.7139 | 0.8013 | 0.0701 | 0.8908 | 0.8125 | 0.6414 | 0.6517 | 0.6633 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_TV
1901 | 1656.5 | 918.3 | 143.9 | 181.4 | 34.3 | 1367.4 | 8546.4 | 33.4 | 49.4 | 109.3 | 107.3 | 93.5 | 117.5 | 44.1 | 34.8 | 1579.8 | 1081.2 | 1589.7 | 1891.3 | 1200 | 1669.2 | 1.197 | 1.11 | 1.05 | 0.98 | 0.988 | 0.956 | 9.51 | -9.8 | 9.24 | 0.909 | 0.945 | 0.899 | -7.24 | 5.51 | -7.34 | 0.808 | 0.875 | 0.793 | -7.73 | -7.19 | -8.6 | 0.866 | 0.779 | 0.87 | -5.52 | -8.64 | 6.88 | Very Poor_Mixed | 1081.2 | 1200 | 1.05 | 0.988 | 9.8 | 0.945 | 8.64 | 0.0657 | 0.5888 | 0.1115 | 0.2118 | 1 | 0.0405 | 0.2057 | 0.3115 | 0.3115 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1902 | 1484.2 | 867.8 | 136.1 | 175.3 | 28.5 | 1338.4 | 7922.9 | 57.3 | 61.1 | 85.7 | 80.8 | 76.1 | 89.3 | 37.4 | 15.2 | 8568.3 | 8401 | 8494.2 | 15680.4 | 16016.9 | 15190.9 | 1.83 | 1.907 | 1.788 | 0.587 | 0.543 | 0.542 | 2.72 | 2.49 | 3.45 | 0.602 | 0.61 | 0.652 | 3.85 | 4.23 | -4.15 | 0.667 | 0.603 | 0.587 | 4.18 | -3.13 | 3.77 | 0.608 | 0.653 | 0.543 | 3.93 | 3.68 | 4.01 | Critical_DGA | 8401 | 15190.9 | 1.788 | 0.587 | 3.45 | 0.667 | 4.23 | 0.1322 | 0.5833 | 0.7188 | 0.8882 | 1 | 0.7854 | 0.6002 | 0.5973 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
1903 | 778.8 | 413.2 | 87.9 | 100.8 | 13.3 | 752.4 | 4685.6 | 57.3 | 22.9 | 78 | 77.3 | 70.8 | 81.9 | 36.2 | 11.8 | 9039 | 9725.2 | 9456.7 | 17162.2 | 19032.2 | 18913.3 | 1.899 | 1.957 | 2 | 0.518 | 0.511 | 0.547 | -2.44 | 2 | 2.44 | 0.531 | 0.504 | 0.503 | -2.57 | 2.41 | 2.34 | 0.533 | 0.547 | 0.571 | -2.03 | 2.86 | -2.66 | 0.546 | 0.532 | 0.5 | 2.82 | 2.03 | -2.52 | Fair_DGA | 9039 | 17162.2 | 1.899 | 0.547 | 2.44 | 0.571 | 2.86 | 0.5337 | 0.9088 | 0.9026 | 0.9703 | 1 | 0.8881 | 0.8399 | 0.8168 | 0.8168 | Good | 1 | 1 | DGA | 0 |  | C2H2
1904 | 517.9 | 313 | 81.3 | 78.6 | 1 | 614.3 | 4374.3 | 31.9 | 46.5 | 84.9 | 83.8 | 104.7 | 89.5 | 37.5 | 15 | 5869.6 | 5110.6 | 4881 | 9279.7 | 7481.2 | 7346.9 | 1.581 | 1.464 | 1.505 | 0.634 | 0.65 | 0.674 | 4.48 | 4.64 | 4.32 | 0.5 | 0.514 | 0.522 | 3.1 | 2 | -2.03 | 0.534 | 0.5 | 0.5 | 2 | 2 | 2.13 | 0.588 | 0.539 | 0.53 | 2.57 | 2.95 | 2.99 | Critical_Oil | 4881 | 7346.9 | 1.464 | 0.674 | 4.64 | 0.588 | 3.1 | 0.82 | 0.6156 | 0.5551 | 0.8935 | 1 | 0.5659 | 0.8671 | 0.7744 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Moisture_PPM
1905 | 943.5 | 545.7 | 100.1 | 121.5 | 16.5 | 746.6 | 5450.1 | 46.7 | 35.8 | 96 | 90.8 | 84.5 | 101.7 | 38.5 | 25.1 | 6131 | 5983.4 | 6491.3 | 9019.8 | 9502.9 | 10217.4 | 1.471 | 1.588 | 1.574 | 0.708 | 0.715 | 0.761 | 5.73 | 5.71 | 6.2 | 0.723 | 0.65 | 0.702 | 5.88 | 4.92 | 3.48 | 0.688 | 0.76 | 0.624 | 3.85 | -5.75 | 4.87 | 0.681 | 0.729 | 0.669 | 4.62 | 6.17 | 5.18 | Poor_Mixed | 5983.4 | 9019.8 | 1.471 | 0.761 | 6.2 | 0.76 | 6.17 | 0.4475 | 0.7253 | 0.4541 | 0.576 | 1 | 0.415 | 0.4542 | 0.573 | 0.573 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1906 | 545.1 | 291.7 | 86.5 | 88.4 | 1 | 608 | 4189.1 | 30.6 | 49.4 | 75.5 | 75.3 | 70.8 | 80 | 35.2 | 17.8 | 6310.7 | 4196.4 | 4743.6 | 9824.6 | 6023.2 | 7054.2 | 1.557 | 1.435 | 1.487 | 0.616 | 0.674 | 0.689 | -3.65 | 5.07 | -5.15 | 0.522 | 0.541 | 0.507 | -2.5 | -2 | 2.55 | 0.536 | 0.561 | 0.551 | 2.43 | 2 | -2 | 0.514 | 1.115 | 0.502 | 2.51 | 2.5 | 2.07 | Critical_Oil | 4196.4 | 6023.2 | 1.435 | 0.689 | 5.15 | 1.115 | 2.55 | 0.8078 | 0.5888 | 0.9711 | 0.8143 | 1 | 0.5522 | 0.7828 | 0.7886 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
1907 | 1582.6 | 907.9 | 142.7 | 184.6 | 34.3 | 1310.5 | 8132.9 | 54.1 | 22.9 | 86 | 83.1 | 75.1 | 88.9 | 36.9 | 10.5 | 9062.8 | 10000 | 8105.5 | 17370.4 | 19325.5 | 4609.6 | 1.917 | 1.933 | 0.569 | 0.643 | 0.631 | 0.592 | 4.52 | 3.94 | -2.54 | 0.593 | 0.609 | 0.632 | 3.26 | 3.78 | -3.42 | 0.549 | 0.539 | 0.637 | 4.01 | 4.39 | 3.15 | 0.62 | 0.578 | 0.639 | 3.15 | 4.44 | -4.06 | Critical_DGA | 8105.5 | 4609.6 | 0.569 | 0.643 | 4.52 | 0.639 | 4.44 | 0.082 | 0.9088 | 0.7103 | 0.994 | 0.8125 | 0.6511 | 0.6292 | 0.5847 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
1908 | 562.6 | 366.9 | 87.8 | 93.7 | 2.2 | 649.6 | 3912.1 | 28.2 | 22.2 | 80.5 | 83.9 | 75.1 | 87.1 | 37 | 14.6 | 6407.8 | 7746.1 | 7050.4 | 10724.3 | 13443.6 | 12224.2 | 1.674 | 1.736 | 1.734 | 0.91 | 0.974 | 0.954 | 9.12 | -9.51 | 9.49 | 0.621 | 0.59 | 0.546 | 2.54 | 4.13 | 3.75 | 0.587 | 0.564 | 0.548 | -2.7 | 2.11 | 3.04 | 0.645 | 0.57 | 0.597 | 4.36 | -3.55 | -2.57 | Critical_Winding_TD_Cap | 6407.8 | 10724.3 | 1.674 | 0.974 | 9.51 | 0.645 | 4.36 | 0.7163 | 0.3404 | 0.7552 | 0.904 | 1 | 0.0668 | 0.6764 | 0.6318 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
1909 | 669.5 | 417.2 | 92 | 149.1 | 1.2 | 704.7 | 4381.7 | 59.7 | 50.4 | 109.3 | 108.4 | 96.2 | 119.2 | 45.7 | 16.6 | 8972.5 | 9343 | 9179.3 | 17381.2 | 18054.5 | 18279.2 | 1.937 | 1.932 | 1.991 | 0.577 | 0.625 | 0.547 | 3.24 | 3.34 | 3.28 | 0.637 | 0.589 | 0.643 | -4.07 | 4.23 | 3.85 | 0.622 | 0.617 | 0.652 | 3.74 | 4.66 | 3.65 | 0.641 | 0.593 | 0.588 | 3.72 | 4.25 | 4.23 | Critical_Thermal | 8972.5 | 17381.2 | 1.932 | 0.625 | 3.34 | 0.652 | 4.66 | 0.6729 | 0.5833 | 0.0702 | 0.8493 | 1 | 0.7227 | 0.5814 | 0.6536 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1910 | 317.6 | 185 | 65 | 50 | 1.5 | 384.4 | 2574.4 | 60 | 20 | 79 | 75.5 | 70 | 84.4 | 36.4 | 11.8 | 9530.4 | 9959.8 | 9555.3 | 18660.7 | 19919.7 | 18430.3 | 1.958 | 2 | 1.929 | 0.573 | 0.502 | 0.544 | 2.44 | 2.53 | -2.93 | 0.5 | 0.508 | 0.533 | 2.23 | -2 | 2.29 | 0.5 | 0.5 | 0.5 | 2.49 | 2.06 | 2 | 0.502 | 0.533 | 0.5 | -2 | 2.38 | 2.23 | Good_Mixed | 9530.4 | 18430.3 | 1.929 | 0.573 | 2.93 | 0.533 | 2.49 | 0.91 | 1 | 0.9127 | 0.9703 | 1 | 0.8423 | 0.94 | 0.9344 | 0.9344 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1911 | 943.8 | 597.6 | 103 | 133.4 | 17.9 | 939.2 | 5909.1 | 42.5 | 35.9 | 91.5 | 90 | 80.1 | 97.2 | 39.4 | 26.6 | 6041.1 | 5768.4 | 5786.8 | 9218.7 | 9273.8 | 9561.7 | 1.526 | 1.608 | 1.652 | 0.78 | 0.731 | 0.772 | 5.59 | 5.4 | 6.27 | 0.69 | 0.686 | 0.628 | 4.95 | 5.45 | -5.14 | 0.665 | 0.709 | 0.704 | 4.45 | 5.89 | 4.49 | 0.684 | 0.625 | 0.757 | -4.46 | 4.62 | 5.46 | Poor_Mixed | 5768.4 | 9218.7 | 1.526 | 0.78 | 6.27 | 0.757 | 5.89 | 0.3907 | 0.7242 | 0.5327 | 0.5228 | 1 | 0.3938 | 0.4632 | 0.5625 | 0.5625 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1912 | 1452.7 | 800.4 | 132.7 | 175.1 | 28.5 | 1204.1 | 7525.3 | 34.7 | 44 | 106.7 | 101 | 90.9 | 112.7 | 44.9 | 29.3 | 1765.1 | 1897.3 | 2659.5 | 2029.4 | 2296.6 | 3191 | 1.15 | 1.21 | 1.2 | 0.896 | 0.958 | 0.931 | 8.35 | -8.79 | -8.78 | 0.743 | 0.759 | 0.841 | 5.13 | -8.03 | -7.84 | 0.779 | 0.883 | 0.738 | -6.43 | 7.46 | 5.02 | 0.818 | 0.869 | 0.808 | -6.71 | 6.85 | 6.05 | Very Poor_Mixed | 1765.1 | 2029.4 | 1.15 | 0.958 | 8.79 | 0.883 | 8.03 | 0.1644 | 0.6396 | 0.1938 | 0.4238 | 1 | 0.1157 | 0.2768 | 0.3845 | 0.3845 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1913 | 119.2 | 174.1 | 67.4 | 54.4 | 2.3 | 387.4 | 3054.9 | 58.5 | 21.7 | 75.6 | 77.9 | 70 | 81.2 | 35.7 | 10 | 9388.1 | 9608.6 | 9313.1 | 18585.9 | 19076.1 | 17303.3 | 1.98 | 1.985 | 1.858 | 0.527 | 0.603 | 0.5 | 2.86 | 3.49 | 2.47 | 0.556 | 0.5 | 0.541 | 2.7 | -2.29 | 2.18 | 0.522 | 0.5 | 0.532 | -2 | 3.03 | 2.29 | 0.5 | 0.535 | 0.598 | 2.16 | 2 | 2 | Good_Mixed | 9313.1 | 17303.3 | 1.858 | 0.603 | 3.49 | 0.598 | 3.03 | 0.8917 | 0.9355 | 0.941 | 1 | 1 | 0.8256 | 0.8572 | 0.9092 | 0.9092 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1914 | 1150.6 | 584.1 | 113.1 | 142.3 | 19.1 | 867.1 | 6364.7 | 59.4 | 21.2 | 79.9 | 77.6 | 72.4 | 82.5 | 35.3 | 14.8 | 8965.2 | 8689.2 | 9692.1 | 16989.7 | 16170.1 | 18907.3 | 1.895 | 1.861 | 1.951 | 0.574 | 0.573 | 0.569 | -3.28 | 3.18 | 2.5 | 0.511 | 0.536 | 0.54 | 2.79 | 2.66 | 2.35 | 0.5 | 0.515 | 0.546 | 2.16 | -3.01 | -2.59 | 0.505 | 0.537 | 0.534 | -2.91 | 2 | 3.06 | Poor_DGA | 8689.2 | 16170.1 | 1.861 | 0.574 | 3.28 | 0.546 | 3.06 | 0.3571 | 0.9486 | 0.8673 | 0.8988 | 1 | 0.7549 | 0.8411 | 0.7519 | 0.7519 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1915 | 111.5 | 138.1 | 74.2 | 91.2 | 1.6 | 375.3 | 2500 | 56.5 | 24 | 83.6 | 86.1 | 77.6 | 89.2 | 38.1 | 13.4 | 8499.9 | 10000 | 10000 | 15277.3 | 19734.9 | 19668.5 | 1.797 | 1.973 | 1.967 | 0.532 | 0.5 | 0.5 | 3.24 | -2 | 2 | 0.5 | 0.5 | 0.5 | 2 | 2 | 2.08 | 0.517 | 0.5 | 0.505 | 2.42 | -2.35 | 2.24 | 0.518 | 0.535 | 0.514 | 2.28 | 2.31 | 2.58 | Fair_Thermal | 8499.9 | 15277.3 | 1.797 | 0.532 | 3.24 | 0.535 | 2.58 | 0.871 | 0.8875 | 0.6793 | 0.9342 | 1 | 0.934 | 0.9227 | 0.8958 | 0.8958 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
1916 | 100 | 120 | 66.9 | 51.2 | 1 | 350 | 2549.3 | 58.1 | 22.9 | 75.9 | 79.8 | 70.3 | 82 | 35.2 | 14.4 | 9862.8 | 10000 | 10000 | 19725.6 | 19422.1 | 20000 | 2 | 1.942 | 2 | 0.5 | 0.533 | 0.5 | 2 | -2.33 | 2 | 0.533 | 0.554 | 0.567 | 3.37 | 3.15 | -2 | 0.543 | 0.506 | 0.5 | 2.68 | 2 | 2.6 | 0.5 | 0.5 | 0.538 | 2.63 | 2.89 | 2.59 | Good_Mixed | 9862.8 | 19422.1 | 1.942 | 0.533 | 2.33 | 0.567 | 3.37 | 0.9949 | 0.9088 | 0.912 | 0.9092 | 1 | 0.9547 | 0.8498 | 0.9411 | 0.9411 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1917 | 1097.3 | 630.9 | 105.7 | 130 | 23.3 | 894.8 | 6186.3 | 59.9 | 20 | 79.7 | 80.9 | 73 | 87.1 | 36.2 | 13.4 | 9243 | 9775.6 | 10000 | 17267.7 | 18867.8 | 19476.2 | 1.868 | 1.93 | 1.948 | 0.53 | 0.568 | 0.546 | 3.15 | -3.26 | 2.45 | 0.5 | 0.523 | 0.5 | -2.1 | 2 | -2.09 | 0.537 | 0.557 | 0.5 | 2.39 | 2.54 | -2 | 0.511 | 0.523 | 0.528 | 2.04 | 2.37 | 2.65 | Poor_DGA | 9243 | 17267.7 | 1.868 | 0.568 | 3.26 | 0.557 | 2.65 | 0.3476 | 1 | 0.8067 | 0.9342 | 1 | 0.795 | 0.8872 | 0.7653 | 0.7653 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1918 | 238.8 | 154.7 | 65.2 | 55.3 | 2.6 | 452.1 | 3491.8 | 56.7 | 22.2 | 78.7 | 75.2 | 71.3 | 80.6 | 35 | 16.5 | 10000 | 8700 | 9756.7 | 19440.7 | 16359.1 | 18893.5 | 1.944 | 1.88 | 1.936 | 0.54 | 0.5 | 0.548 | 2.61 | -2 | 3.03 | 0.517 | 0.5 | 0.553 | 2.11 | 2 | -2.06 | 0.504 | 0.579 | 0.531 | 2.03 | 2.71 | 2.4 | 0.5 | 0.548 | 0.5 | 2.1 | 2.08 | 2 | Good_Mixed | 8700 | 16359.1 | 1.88 | 0.548 | 3.03 | 0.579 | 2.71 | 0.8578 | 0.9238 | 0.9292 | 0.8522 | 1 | 0.8725 | 0.8815 | 0.9017 | 0.9017 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1919 | 364.6 | 240.1 | 75.7 | 68.1 | 74.7 | 543.6 | 3559.8 | 30.9 | 49.4 | 78.4 | 80.2 | 74 | 82.4 | 37.2 | 17.9 | 4834.3 | 5740.5 | 5194.1 | 7328.3 | 8692 | 8174 | 1.516 | 1.514 | 1.574 | 0.671 | 0.696 | 0.643 | 4.79 | -5.23 | 5.26 | 0.584 | 0.569 | 0.53 | 4.65 | 3.19 | 4.67 | 0.582 | 0.663 | 0.614 | 2.82 | 3.61 | -3.06 | 0.616 | 0.578 | 0.596 | -3.95 | 4.41 | 3.29 | Critical_Oil | 4834.3 | 7328.3 | 1.514 | 0.696 | 5.26 | 0.663 | 4.67 | 0.5559 | 0.5888 | 0.8348 | 0.8114 | 1 | 0.5132 | 0.6412 | 0.6809 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1920 | 311.6 | 227.6 | 81.2 | 75 | 1 | 547.6 | 3749.6 | 58.5 | 23 | 75 | 76 | 72.7 | 81.7 | 35 | 16.1 | 9293 | 8851.6 | 8449.5 | 18358 | 15446.8 | 16304.2 | 1.975 | 1.745 | 1.93 | 0.687 | 0.732 | 0.717 | 4.81 | 5.65 | -5.71 | 0.504 | 0.5 | 0.552 | 2 | 2.81 | -2 | 0.526 | 0.566 | 0.5 | -2.31 | 2.25 | 2 | 0.511 | 0.516 | 0.517 | 2.17 | -2.8 | 2 | Poor_Winding_TD_Cap | 8449.5 | 15446.8 | 1.745 | 0.732 | 5.71 | 0.566 | 2.81 | 0.868 | 0.9067 | 0.945 | 0.8635 | 1 | 0.4566 | 0.8812 | 0.846 | 0.846 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
1921 | 1708.4 | 954.5 | 138.9 | 197 | 34.3 | 1216.4 | 7977.1 | 36.4 | 43.3 | 106.5 | 105.7 | 94.2 | 115.9 | 45.1 | 33.9 | 2393.7 | 3206.6 | 2233.9 | 2818.3 | 4086.1 | 2680.9 | 1.177 | 1.274 | 1.2 | 0.974 | 0.989 | 0.956 | -9.84 | 9.66 | -9.13 | 0.881 | 0.78 | 0.761 | 4.99 | 5.58 | 7.38 | 0.885 | 0.947 | 0.741 | -5.91 | 6.98 | 7.41 | 0.871 | 0.886 | 0.836 | 6.76 | 6.23 | -6.48 | Very Poor_Mixed | 2233.9 | 2680.9 | 1.177 | 0.989 | 9.84 | 0.947 | 7.41 | 0.0733 | 0.6465 | 0.1323 | 0.2473 | 1 | 0.0403 | 0.2476 | 0.3317 | 0.3317 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1922 | 842.6 | 507.6 | 100.4 | 115.6 | 16.3 | 838 | 5249.5 | 46.3 | 35.3 | 90.4 | 92.3 | 82.8 | 97.3 | 41.5 | 25.7 | 4126.1 | 4484.4 | 4909.5 | 5711.4 | 6591.7 | 7444 | 1.384 | 1.47 | 1.516 | 0.764 | 0.77 | 0.716 | 5.94 | 6.37 | 5.47 | 0.716 | 0.68 | 0.646 | -5.29 | 4.5 | 4.4 | 0.723 | 0.643 | 0.584 | -5.37 | 4.67 | -4.71 | 0.694 | 0.762 | 0.618 | 4.27 | 5.32 | -4.49 | Poor_Mixed | 4126.1 | 5711.4 | 1.384 | 0.77 | 6.37 | 0.762 | 5.37 | 0.457 | 0.731 | 0.4932 | 0.5549 | 1 | 0.3936 | 0.4846 | 0.5814 | 0.5814 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1923 | 941.3 | 539.5 | 104.8 | 119.4 | 22.6 | 841.3 | 5524.7 | 46.4 | 34.5 | 91.9 | 90.2 | 82.3 | 99.7 | 40.2 | 24.5 | 5919.5 | 6561.9 | 5331.7 | 9073.5 | 9997.3 | 8261.5 | 1.533 | 1.524 | 1.55 | 0.712 | 0.718 | 0.771 | 5.23 | 5.02 | 6.44 | 0.678 | 0.608 | 0.671 | 5.52 | -3.14 | 4.72 | 0.651 | 0.642 | 0.569 | 4.73 | 4.84 | 4.63 | 0.612 | 0.609 | 0.676 | -4.02 | 4.25 | 4.89 | Poor_Mixed | 5331.7 | 8261.5 | 1.524 | 0.771 | 6.44 | 0.678 | 5.52 | 0.3981 | 0.7403 | 0.4969 | 0.597 | 1 | 0.4281 | 0.5437 | 0.5857 | 0.5857 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1924 | 869.1 | 538.3 | 103 | 125.8 | 16.6 | 805.7 | 5357.7 | 44.6 | 33.6 | 92.7 | 90.3 | 84.5 | 101.6 | 39 | 25.6 | 5829.6 | 4095.8 | 6220.3 | 9031.5 | 6253.4 | 9647.4 | 1.549 | 1.527 | 1.551 | 0.729 | 0.722 | 0.755 | 5.82 | -5.7 | 5.56 | 0.675 | 0.656 | 0.656 | 4.17 | 5.76 | 5.54 | 0.695 | 0.685 | 0.737 | -4.35 | 4.29 | -4.48 | 0.611 | 0.685 | 0.74 | 4.83 | 3.93 | 4.55 | Poor_Mixed | 4095.8 | 6253.4 | 1.527 | 0.755 | 5.82 | 0.74 | 5.76 | 0.4407 | 0.7509 | 0.4754 | 0.5584 | 1 | 0.4186 | 0.4768 | 0.5802 | 0.5802 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1925 | 796.1 | 501.7 | 97.4 | 113.8 | 13.2 | 692.4 | 5347.8 | 56.9 | 22 | 75 | 75 | 73.1 | 82.4 | 35 | 13.8 | 8047 | 9125.6 | 8239.4 | 14628.7 | 17086.3 | 14572.5 | 1.818 | 1.872 | 1.769 | 0.529 | 0.56 | 0.554 | 2.58 | 3.43 | 2.92 | 0.507 | 0.551 | 0.642 | 2.64 | 3.59 | 3.06 | 0.582 | 0.551 | 0.564 | -3.28 | 2.94 | -2.95 | 0.535 | 0.617 | 0.54 | 3.14 | 2.09 | -2.54 | Poor_DGA | 8047 | 14572.5 | 1.769 | 0.56 | 3.43 | 0.642 | 3.59 | 0.5046 | 0.9283 | 0.9555 | 0.9244 | 1 | 0.7936 | 0.7313 | 0.7821 | 0.7821 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1926 | 962 | 510.7 | 106 | 124 | 17.7 | 854 | 5252.9 | 47.8 | 34.6 | 90.5 | 92.4 | 82.6 | 99.6 | 40 | 25.6 | 5859 | 6973.3 | 6094.6 | 9171.3 | 10766.1 | 9451.5 | 1.565 | 1.544 | 1.551 | 0.782 | 0.79 | 0.749 | 6.06 | 6.91 | 5.46 | 0.578 | 0.627 | 0.69 | -4.78 | -5.02 | 5 | 0.59 | 0.628 | 0.63 | -4.97 | -4.91 | 4.13 | 0.564 | 0.608 | 0.705 | 3.71 | 3.64 | -5.19 | Poor_Mixed | 5859 | 9171.3 | 1.544 | 0.79 | 6.91 | 0.705 | 5.19 | 0.4241 | 0.7391 | 0.4916 | 0.5584 | 1 | 0.362 | 0.558 | 0.5829 | 0.5829 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1927 | 210.2 | 195.1 | 70.7 | 55.7 | 2.9 | 399.9 | 2887.8 | 57.1 | 24.6 | 77.3 | 78.2 | 71.6 | 83.8 | 36.9 | 13.3 | 9426.8 | 9140.5 | 9737.6 | 17927.2 | 16633.5 | 18308.2 | 1.902 | 1.82 | 1.88 | 0.5 | 0.526 | 0.508 | 2.54 | 2 | 2.32 | 0.5 | 0.5 | 0.55 | 2.32 | 2.12 | 2.53 | 0.513 | 0.526 | 0.515 | 2.42 | -2.64 | 2.01 | 0.514 | 0.5 | 0.5 | 2.06 | -2.13 | 2 | Good_Mixed | 9140.5 | 16633.5 | 1.82 | 0.526 | 2.54 | 0.55 | 2.64 | 0.8591 | 0.8768 | 0.8794 | 0.9367 | 1 | 0.9291 | 0.913 | 0.9092 | 0.9092 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1928 | 990.9 | 600.3 | 112.1 | 125.6 | 21.4 | 944.2 | 5682.4 | 46.1 | 33.6 | 91 | 90.3 | 83.2 | 101 | 38.8 | 26 | 4153.7 | 5461.2 | 5145.5 | 5955.8 | 8166.1 | 7818.4 | 1.434 | 1.495 | 1.519 | 0.752 | 0.763 | 0.722 | 5.16 | 6.17 | -5.32 | 0.555 | 0.723 | 0.623 | 5.09 | -5.05 | 4.42 | 0.617 | 0.668 | 0.586 | -4.73 | 5.09 | -4.07 | 0.621 | 0.717 | 0.635 | -4.86 | 4.79 | 4.66 | Poor_Mixed | 4153.7 | 5955.8 | 1.434 | 0.763 | 6.17 | 0.723 | 5.09 | 0.3686 | 0.7509 | 0.4987 | 0.5442 | 1 | 0.418 | 0.5336 | 0.5739 | 0.5739 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1929 | 435.8 | 224.5 | 71.2 | 70 | 72.8 | 471.2 | 3293.2 | 54.4 | 24.3 | 81 | 78.8 | 72.5 | 85.2 | 37.3 | 16.4 | 9357.7 | 8241.1 | 8558 | 17473 | 15020.2 | 15895.1 | 1.867 | 1.823 | 1.857 | 0.862 | 0.862 | 0.869 | -7.46 | 7.97 | 7.73 | 0.539 | 0.636 | 0.514 | 2.17 | 3.05 | 2.16 | 0.514 | 0.531 | 0.603 | 3.76 | 3.22 | 2.95 | 0.582 | 0.605 | 0.593 | -2.53 | -2.89 | -3.83 | Critical_Winding_TD_Cap | 8241.1 | 15020.2 | 1.823 | 0.869 | 7.97 | 0.636 | 3.83 | 0.5645 | 0.8821 | 0.8222 | 0.855 | 1 | 0.2079 | 0.7263 | 0.6918 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1930 | 584.7 | 451.3 | 94.6 | 97.5 | 11.9 | 725.6 | 4692.8 | 52.1 | 24.8 | 83.7 | 81.3 | 78.6 | 89.4 | 38.1 | 20.1 | 7481.9 | 6810.5 | 6206.2 | 12501.4 | 10826.7 | 10126.7 | 1.671 | 1.59 | 1.632 | 0.585 | 0.576 | 0.611 | 3.41 | -3.33 | 3.12 | 0.696 | 0.605 | 0.654 | 4.13 | 4.75 | 4.03 | 0.626 | 0.604 | 0.63 | 4.35 | 3.9 | -4.21 | 0.643 | 0.654 | 0.574 | 4.17 | 4.66 | 4.62 | Fair_Mixed | 6206.2 | 10126.7 | 1.59 | 0.611 | 3.41 | 0.696 | 4.75 | 0.5584 | 0.8734 | 0.7072 | 0.7436 | 1 | 0.7101 | 0.5555 | 0.7117 | 0.7117 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1931 | 858.1 | 523.3 | 105.5 | 109.2 | 15 | 822.5 | 5106 | 45.3 | 33.3 | 93.5 | 93.8 | 84.4 | 98.1 | 40.2 | 25 | 5174 | 5620 | 5448.7 | 7508.2 | 8742.2 | 8193.6 | 1.451 | 1.556 | 1.504 | 0.674 | 0.753 | 0.728 | 4.93 | -5.97 | 5.05 | 0.677 | 0.612 | 0.735 | 4.15 | -4.62 | 3.34 | 0.658 | 0.685 | 0.67 | 4.52 | 4.54 | 4.86 | 0.631 | 0.709 | 0.655 | 4.28 | 6.51 | 5.19 | Poor_Mixed | 5174 | 7508.2 | 1.451 | 0.753 | 5.97 | 0.735 | 6.51 | 0.4689 | 0.7544 | 0.4584 | 0.5796 | 1 | 0.4557 | 0.4914 | 0.5948 | 0.5948 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1932 | 395.7 | 195.2 | 82.3 | 77.1 | 1 | 551.9 | 3193.5 | 53 | 27.7 | 80.9 | 79.3 | 71.5 | 83.9 | 36.5 | 10 | 690 | 1191.9 | 2244.8 | 705.8 | 1250.4 | 2815.4 | 1.023 | 1.049 | 1.254 | 0.672 | 0.683 | 0.693 | 5.05 | 5.16 | 24.43 | 0.547 | 0.513 | 0.55 | 2.61 | 2.28 | -2.24 | 0.521 | 0.525 | 0.577 | 2 | 2.08 | 2.6 | 0.516 | 0.5 | 0.504 | 4.05 | 2.51 | 2.22 | Critical_IR_PI | 690 | 705.8 | 1.023 | 0.693 | 24.43 | 0.577 | 4.05 | 0.8641 | 0.8279 | 0.8383 | 1 | 0.925 | 0.4141 | 0.8425 | 0.8068 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | Winding_TV_CapChange_pct
1933 | 1476.8 | 877.4 | 145.2 | 190.1 | 34.3 | 1263.2 | 8661.1 | 36.4 | 43.7 | 105.3 | 105.1 | 91 | 114.6 | 45.3 | 31.1 | 1758.6 | 2505.2 | 1850.8 | 2053.3 | 3079.5 | 2042.4 | 1.168 | 1.229 | 1.104 | 0.942 | 0.861 | 0.941 | 8.97 | -7.29 | 9.48 | 0.805 | 0.85 | 0.883 | 6.93 | 7.68 | 8.06 | 0.727 | 0.775 | 0.753 | 8.2 | 4.73 | 6.36 | 0.769 | 0.794 | 0.693 | 4.98 | -5.88 | 8.55 | Very Poor_Mixed | 1758.6 | 2042.4 | 1.104 | 0.942 | 9.48 | 0.883 | 8.55 | 0.0846 | 0.6425 | 0.1653 | 0.3559 | 1 | 0.129 | 0.2917 | 0.3631 | 0.3631 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1934 | 436.7 | 259.3 | 77.7 | 71.5 | 2.1 | 3462.8 | 10486.2 | 58.3 | 21.5 | 81.1 | 83.2 | 73.4 | 86.7 | 36.4 | 13.4 | 8863.9 | 8940.3 | 9717.2 | 17040.7 | 17328.9 | 18377.3 | 1.922 | 1.938 | 1.891 | 0.977 | 0.99 | 0.99 | 9.84 | 9.51 | 9.6 | 0.583 | 0.527 | 0.583 | -2.61 | 2.81 | 2.7 | 0.533 | 0.56 | 0.567 | 2.63 | 3.74 | -2.54 | 0.56 | 0.514 | 0.59 | 2.78 | 3.15 | -3.38 | Critical_Winding_TD_Cap | 8863.9 | 17040.7 | 1.891 | 0.99 | 9.84 | 0.59 | 3.74 | 0.6149 | 0.9406 | 0.774 | 0.9342 | 1 | 0.0266 | 0.7408 | 0.6878 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
1935 | 1259 | 676.2 | 113 | 139.6 | 18 | 936.7 | 6398 | 56.9 | 22.2 | 81 | 77.1 | 74.7 | 86.3 | 35.5 | 11.2 | 8946.7 | 8792.1 | 8271.3 | 16738.4 | 15810.5 | 15555 | 1.871 | 1.798 | 1.881 | 0.557 | 0.556 | 0.57 | 3.71 | 3.37 | 3.01 | 0.525 | 0.528 | 0.537 | 2.91 | 3.24 | 2.49 | 0.5 | 0.567 | 0.5 | 2.98 | 2 | -2 | 0.5 | 0.506 | 0.524 | 2.33 | 2.67 | 2.69 | Poor_DGA | 8271.3 | 15555 | 1.798 | 0.57 | 3.71 | 0.567 | 3.24 | 0.3392 | 0.9238 | 0.8245 | 0.9821 | 1 | 0.7457 | 0.8683 | 0.7479 | 0.7479 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1936 | 557.5 | 367.6 | 92.6 | 93.3 | 9.7 | 617 | 4585.9 | 51.7 | 27.1 | 86.6 | 86.7 | 76.5 | 87 | 36.9 | 19.2 | 7184.3 | 6449.5 | 7774.7 | 12137.5 | 10120.4 | 13618 | 1.689 | 1.569 | 1.752 | 0.629 | 0.646 | 0.679 | -4.49 | 4.68 | 5 | 0.61 | 0.576 | 0.583 | 2.73 | -2.92 | 3.91 | 0.59 | 0.559 | 0.622 | 3.56 | 3.98 | 2.57 | 0.59 | 0.626 | 0.581 | 3.4 | 3.94 | 3.56 | Fair_Mixed | 6449.5 | 10120.4 | 1.569 | 0.679 | 5 | 0.626 | 3.98 | 0.6104 | 0.8367 | 0.6787 | 0.7718 | 1 | 0.5533 | 0.6508 | 0.7141 | 0.7141 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1937 | 124.5 | 140.6 | 67.8 | 55.3 | 2 | 350 | 2500 | 59.6 | 20 | 78 | 75.8 | 70 | 80 | 35.9 | 16.4 | 10000 | 9635.5 | 8649.6 | 20000 | 19271 | 16152.6 | 2 | 2 | 1.867 | 0.556 | 0.523 | 0.543 | 2.47 | 2.85 | -2.66 | 0.5 | 0.542 | 0.5 | 3.13 | 2.6 | 2.86 | 0.5 | 0.52 | 0.543 | 2.59 | 2.63 | -2.61 | 0.509 | 0.545 | 0.506 | 2.73 | 2.66 | 2.67 | Good_Mixed | 8649.6 | 16152.6 | 1.867 | 0.556 | 2.85 | 0.545 | 3.13 | 0.9137 | 1 | 0.9423 | 0.855 | 1 | 0.8274 | 0.8671 | 0.9173 | 0.9173 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1938 | 260.1 | 319.2 | 78.2 | 70.9 | 1.6 | 480.3 | 4010.7 | 45.9 | 36.2 | 78.2 | 82 | 75.3 | 83.5 | 36.6 | 15.8 | 6976.4 | 7137.9 | 8028.1 | 12414.3 | 12319.7 | 14631 | 1.779 | 1.726 | 1.822 | 0.574 | 0.612 | 0.593 | 2.67 | 3.51 | -4.07 | 0.559 | 0.552 | 0.555 | -2.45 | 3.16 | -2.65 | 0.609 | 0.57 | 0.554 | 2.96 | 2.97 | -2.09 | 0.566 | 0.583 | 0.535 | 2.93 | 3.12 | 2.31 | Poor_Oil | 6976.4 | 12319.7 | 1.726 | 0.612 | 4.07 | 0.609 | 3.16 | 0.8257 | 0.7208 | 0.8094 | 0.8718 | 1 | 0.7 | 0.7316 | 0.8071 | 0.8071 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1939 | 609.8 | 354.9 | 85.1 | 87.7 | 10.2 | 548.1 | 4492.2 | 52.2 | 30.1 | 82.2 | 86.3 | 74.4 | 88 | 37.1 | 20.7 | 7629.9 | 6948.8 | 7878.6 | 12938.3 | 12234.7 | 13703.6 | 1.696 | 1.761 | 1.739 | 0.634 | 0.572 | 0.629 | 4.7 | 3.3 | -4.63 | 0.577 | 0.605 | 0.583 | 3.4 | 3.05 | 2.82 | 0.55 | 0.631 | 0.646 | 3.75 | 3.23 | 3.76 | 0.644 | 0.577 | 0.634 | 3.27 | 3.15 | -4.01 | Fair_Mixed | 6948.8 | 12234.7 | 1.696 | 0.634 | 4.7 | 0.646 | 4.01 | 0.625 | 0.7947 | 0.724 | 0.7244 | 1 | 0.6293 | 0.6336 | 0.7224 | 0.7224 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1940 | 352.2 | 215.5 | 76.4 | 75 | 2.3 | 434.5 | 3073.4 | 55.8 | 20.1 | 87.7 | 90.4 | 79.5 | 93.2 | 39 | 10.8 | 10000 | 10000 | 10000 | 19651.2 | 19875 | 20000 | 1.965 | 1.988 | 2 | 0.526 | 0.505 | 0.57 | 2.04 | -2.65 | 2.92 | 0.534 | 0.529 | 0.52 | 2.3 | 2 | 2 | 0.5 | 0.523 | 0.524 | -2 | 2 | 3.14 | 0.509 | 0.507 | 0.5 | -2.21 | 2.6 | 2.12 | Fair_Thermal | 10000 | 19651.2 | 1.965 | 0.57 | 2.92 | 0.534 | 3.14 | 0.8177 | 0.9898 | 0.5819 | 0.9892 | 1 | 0.8589 | 0.8913 | 0.8715 | 0.8715 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1941 | 882.5 | 526.7 | 105.9 | 120.5 | 22.6 | 855.3 | 5505 | 48.2 | 35 | 95.1 | 93.5 | 82.9 | 101.1 | 40.5 | 25.4 | 5930.2 | 5005.1 | 5734.3 | 8505.1 | 7625.4 | 8799.4 | 1.434 | 1.524 | 1.535 | 0.728 | 0.723 | 0.786 | -5.85 | 6.04 | 6.35 | 0.692 | 0.598 | 0.704 | 4.33 | -4.14 | 4.72 | 0.646 | 0.671 | 0.606 | 4.59 | 5.23 | 4.7 | 0.678 | 0.62 | 0.639 | 4.05 | 4.44 | -4.29 | Poor_Mixed | 5005.1 | 7625.4 | 1.434 | 0.786 | 6.35 | 0.704 | 5.23 | 0.4007 | 0.7345 | 0.4428 | 0.5655 | 1 | 0.3889 | 0.5229 | 0.5694 | 0.5694 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1942 | 627.2 | 368.7 | 92.6 | 90.4 | 55.1 | 652.4 | 4349.1 | 50 | 30.5 | 80 | 79.5 | 76.4 | 86.9 | 37.5 | 18.6 | 6752.1 | 7714.3 | 7466.8 | 11512.3 | 13506.3 | 12887.5 | 1.705 | 1.751 | 1.726 | 0.914 | 0.99 | 0.99 | 9.26 | -9.69 | 9.32 | 0.568 | 0.557 | 0.561 | 2.64 | 4.22 | 3.41 | 0.565 | 0.519 | 0.556 | 2.99 | 2.25 | -2.86 | 0.633 | 0.587 | 0.622 | 2.54 | 2.32 | -2.15 | Critical_Winding_TD_Cap | 6752.1 | 11512.3 | 1.705 | 0.99 | 9.69 | 0.633 | 4.22 | 0.4581 | 0.7894 | 0.784 | 0.7902 | 1 | 0.052 | 0.715 | 0.6231 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1943 | 788.4 | 468.5 | 102.8 | 130.1 | 17.9 | 853.2 | 4900.9 | 47 | 32 | 92.7 | 88.6 | 84 | 99.5 | 39.8 | 27 | 5907.5 | 4852.4 | 6473.1 | 9226.7 | 7670.7 | 10043.5 | 1.562 | 1.581 | 1.552 | 0.785 | 0.729 | 0.727 | 6.68 | 6.21 | -5.66 | 0.697 | 0.574 | 0.735 | -3.5 | 5.21 | 3.73 | 0.641 | 0.672 | 0.649 | -5.81 | 6.1 | -3.5 | 0.66 | 0.721 | 0.699 | 6.54 | 3.81 | 5.43 | Poor_Mixed | 4852.4 | 7670.7 | 1.552 | 0.785 | 6.68 | 0.735 | 6.54 | 0.4415 | 0.7703 | 0.4954 | 0.5083 | 1 | 0.3822 | 0.4853 | 0.5786 | 0.5786 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1944 | 100 | 120 | 65 | 51.5 | 2.3 | 350 | 2500 | 57.9 | 20 | 76.6 | 75 | 71 | 80.4 | 35.9 | 11.5 | 9744.9 | 10000 | 10000 | 19489.8 | 19527.2 | 20000 | 2 | 1.953 | 2 | 0.502 | 0.5 | 0.541 | 2.34 | 2 | 2 | 0.507 | 0.547 | 0.517 | 2 | -2 | -2.52 | 0.5 | 0.511 | 0.5 | 2 | -2.54 | 2.07 | 0.537 | 0.521 | 0.516 | 2 | 2 | -2.23 | Good_Mixed | 9744.9 | 19489.8 | 1.953 | 0.541 | 2.34 | 0.547 | 2.54 | 0.9213 | 1 | 0.9567 | 0.9764 | 1 | 0.9431 | 0.8955 | 0.948 | 0.948 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1945 | 484 | 237 | 80.5 | 78.3 | 2.6 | 601.9 | 3818.3 | 58.2 | 21.3 | 119.5 | 84 | 73.7 | 88.2 | 37.2 | 12.7 | 767.7 | 929.5 | 1497.8 | 829.3 | 960.3 | 1621.5 | 1.08 | 1.033 | 1.083 | 0.679 | 0.736 | 0.768 | 4.86 | 5.47 | 5.23 | 0.552 | 0.5 | 0.555 | -3.01 | -2.83 | -2.32 | 0.51 | 0.521 | 0.5 | 2 | -2.73 | 2.71 | 0.504 | 0.564 | 0.557 | 2.12 | 2.79 | 2.45 | Critical_IR_PI | 767.7 | 829.3 | 1.033 | 0.768 | 5.47 | 0.564 | 3.01 | 0.7583 | 0.9458 | 0.5712 | 0.9507 | 0.85 | 0.4547 | 0.8439 | 0.7593 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature; IR_Min_10min<1000 Mohm: critical insulation resistance | WTI_HV
1946 | 910.2 | 496.7 | 107.1 | 124.3 | 19.2 | 854.6 | 5434.9 | 44.8 | 33.8 | 90.3 | 90.7 | 81.6 | 100 | 38.8 | 24.3 | 5860.1 | 5801.9 | 4996.6 | 9337 | 9257.8 | 7743.6 | 1.593 | 1.596 | 1.55 | 0.668 | 0.717 | 0.723 | 4.67 | 5.56 | 5.34 | 0.721 | 0.701 | 0.683 | 4.73 | 5.24 | -4.15 | 0.667 | 0.693 | 0.705 | 4.73 | 4.77 | 4.02 | 0.682 | 0.671 | 0.67 | 4.03 | 4.25 | -4.13 | Poor_Mixed | 4996.6 | 7743.6 | 1.55 | 0.723 | 5.56 | 0.721 | 5.24 | 0.4176 | 0.7485 | 0.5158 | 0.6039 | 1 | 0.4766 | 0.4754 | 0.5883 | 0.5883 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1947 | 343.4 | 235.7 | 79.7 | 84.3 | 1.3 | 2408.2 | 23414.1 | 31.8 | 48.1 | 78.1 | 80 | 71.9 | 83.6 | 37.2 | 17.5 | 5442.6 | 5379.9 | 4801.1 | 8197.7 | 8469.4 | 6771.6 | 1.506 | 1.574 | 1.41 | 0.657 | 0.68 | 0.684 | 4.73 | 4.76 | 4.99 | 0.523 | 0.57 | 0.561 | 3.3 | 2.57 | 2.64 | 0.544 | 0.572 | 0.586 | 2.75 | -2 | 2.63 | 0.511 | 0.54 | 0.513 | 3.86 | 2.2 | 2 | Critical_Oil | 4801.1 | 6771.6 | 1.41 | 0.684 | 4.99 | 0.586 | 3.86 | 0.6397 | 0.6007 | 0.8513 | 0.8232 | 1 | 0.5244 | 0.781 | 0.7323 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | Moisture_PPM
1948 | 328.7 | 202.1 | 78.3 | 149.7 | 1 | 513 | 3739.1 | 58 | 21.8 | 107.4 | 105.8 | 96.7 | 119.2 | 44.5 | 13.4 | 7554.7 | 8489.5 | 6980.2 | 13452.9 | 5397.6 | 11874.3 | 1.781 | 0.636 | 1.701 | 0.605 | 0.615 | 0.627 | -3.8 | -3.74 | 4.1 | 0.52 | 0.589 | 0.578 | -3.37 | 3.25 | 3.21 | 0.637 | 0.567 | 0.586 | -3.35 | -3.84 | 3.36 | 0.548 | 0.599 | 0.59 | -3.66 | 3 | -3.25 | Critical_Thermal | 6980.2 | 5397.6 | 0.636 | 0.627 | 4.1 | 0.637 | 3.84 | 0.8006 | 0.9331 | 0.1009 | 0.9342 | 0.8187 | 0.6421 | 0.6788 | 0.712 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H4
1949 | 100 | 120 | 65 | 50 | 1.5 | 350 | 2500 | 60 | 20 | 75 | 79.7 | 70 | 82 | 35 | 10.7 | 9217.8 | 9838.7 | 10000 | 17822.4 | 19421.9 | 19574.6 | 1.933 | 1.974 | 1.957 | 0.529 | 0.504 | 0.5 | 2 | -2.01 | -2 | 0.549 | 0.5 | 0.5 | 2.13 | 2.32 | -2 | 0.518 | 0.52 | 0.5 | 2 | 2 | 2 | 0.5 | 0.5 | 0.5 | 2.11 | 2 | 2.55 | Good_Mixed | 9217.8 | 17822.4 | 1.933 | 0.529 | 2.01 | 0.549 | 2.55 | 0.9521 | 1 | 0.9345 | 0.9909 | 1 | 0.9573 | 0.9438 | 0.9649 | 0.9649 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1950 | 1543.3 | 854.1 | 136.4 | 177.1 | 34.3 | 1232.5 | 7858.9 | 36 | 45 | 102.7 | 104.3 | 93 | 111.8 | 42.9 | 31.3 | 1770.8 | 2064.6 | 2025.6 | 2074.6 | 2356.9 | 2338.9 | 1.172 | 1.142 | 1.155 | 0.904 | 0.927 | 0.943 | 8.28 | -8.72 | 9.58 | 0.851 | 0.703 | 0.712 | 5.41 | -5.54 | 7.78 | 0.892 | 0.83 | 0.795 | 7.36 | 5.02 | -5.32 | 0.91 | 0.741 | 0.882 | 5.2 | -6.69 | 6.87 | Very Poor_Mixed | 1770.8 | 2074.6 | 1.142 | 0.943 | 9.58 | 0.91 | 7.78 | 0.1139 | 0.6299 | 0.2044 | 0.3483 | 1 | 0.1071 | 0.287 | 0.3686 | 0.3686 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1951 | 387.3 | 302.6 | 77.2 | 65.1 | 3.5 | 590.1 | 3916.1 | 55.7 | 25.6 | 75 | 76 | 71.5 | 80 | 35.1 | 13.9 | 9369 | 8077 | 8592.1 | 17665.2 | 14621.5 | 15927.6 | 1.885 | 1.81 | 1.854 | 0.525 | 0.554 | 0.563 | 2.29 | 2.99 | -2.5 | 0.582 | 0.558 | 0.579 | 2.79 | -3.71 | 2.6 | 0.562 | 0.6 | 0.776 | 3.96 | -2 | 7.14 | 0.5 | 0.55 | 0.536 | -3.54 | 2.59 | 2.47 | Poor_Bushing_TD_Cap | 8077 | 14621.5 | 1.81 | 0.563 | 2.99 | 0.776 | 7.14 | 0.7613 | 0.86 | 0.9642 | 0.9219 | 1 | 0.8218 | 0.6963 | 0.8364 | 0.8364 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1952 | 100 | 120 | 70.5 | 54.6 | 2.2 | 431 | 2500 | 57.8 | 22.9 | 77.3 | 77.3 | 70.5 | 80 | 35.4 | 14.9 | 2833.8 | 5220.2 | 2512.6 | 3657.4 | 7423.5 | 3091.5 | 1.291 | 1.422 | 1.23 | 0.592 | 0.555 | 0.635 | 4 | 3.24 | 5.26 | 0.549 | 0.5 | 0.552 | -2 | -3.1 | -2.06 | 0.541 | 0.5 | 0.555 | -2.63 | 2 | 2.03 | 0.5 | 0.517 | 0.53 | 2.36 | 2.17 | 2.42 | Poor_IR_PI | 2512.6 | 3091.5 | 1.23 | 0.635 | 5.26 | 0.555 | 3.1 | 0.8966 | 0.9088 | 0.9263 | 0.8962 | 1 | 0.6549 | 0.8648 | 0.878 | 0.878 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1953 | 646.6 | 483.6 | 106.8 | 109.9 | 15.5 | 765.3 | 4767.4 | 48 | 31.2 | 82.6 | 85.7 | 76.8 | 90 | 38.1 | 22.4 | 7014.6 | 6950.9 | 7823.1 | 11545 | 11441.4 | 14034.3 | 1.646 | 1.646 | 1.794 | 0.671 | 0.649 | 0.68 | 4.64 | 4.7 | -5.03 | 0.713 | 0.61 | 0.59 | 5.16 | 3.75 | -4.51 | 0.622 | 0.602 | 0.596 | -5.32 | 3.44 | -3.99 | 0.595 | 0.633 | 0.609 | 3.78 | 5.56 | 3.87 | Fair_Mixed | 6950.9 | 11441.4 | 1.646 | 0.68 | 5.03 | 0.713 | 5.56 | 0.4959 | 0.7804 | 0.6916 | 0.6686 | 1 | 0.5335 | 0.5725 | 0.658 | 0.658 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1954 | 217 | 151.4 | 65 | 52.1 | 2.5 | 406.4 | 3092.3 | 57.3 | 21.6 | 75 | 75 | 70 | 80 | 35.6 | 14.8 | 10000 | 8999.4 | 9617.5 | 19781.4 | 16836.2 | 18987.9 | 1.978 | 1.871 | 1.974 | 0.5 | 0.5 | 0.507 | 2 | 2 | -2.86 | 0.5 | 0.566 | 0.5 | 3.1 | 2.29 | 3.05 | 0.509 | 0.51 | 0.547 | 2 | 2 | -2.94 | 0.5 | 0.547 | 0.5 | 2.28 | 2 | 2.87 | Good_Mixed | 8999.4 | 16836.2 | 1.871 | 0.507 | 2.86 | 0.566 | 3.1 | 0.8802 | 0.938 | 0.9979 | 0.8988 | 1 | 0.963 | 0.8848 | 0.9314 | 0.9314 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1955 | 1679.2 | 925.1 | 137.9 | 191 | 34.3 | 1234.4 | 8402.5 | 33.7 | 46.9 | 104.7 | 104.3 | 92.9 | 114.9 | 45.3 | 33.8 | 1949.9 | 1718.6 | 2791 | 2369.6 | 1934.5 | 3337.5 | 1.215 | 1.126 | 1.196 | 0.912 | 0.88 | 0.92 | 9.17 | 8.67 | 9.3 | 0.707 | 0.873 | 0.753 | 7.84 | 8.77 | 5.62 | 0.855 | 0.918 | 0.794 | -8.91 | -8.36 | 6.47 | 0.836 | 0.917 | 0.908 | 7.63 | 7.33 | 5.86 | Very Poor_Mixed | 1718.6 | 1934.5 | 1.126 | 0.92 | 9.3 | 0.918 | 8.91 | 0.0766 | 0.6119 | 0.1608 | 0.2513 | 1 | 0.1119 | 0.2181 | 0.3362 | 0.3362 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1956 | 1507.2 | 866.8 | 131.1 | 183.5 | 29 | 1241.8 | 8214.3 | 34.1 | 43.1 | 108.4 | 109.1 | 94.4 | 117.7 | 44.4 | 33.3 | 1903.4 | 1330.2 | 1040.6 | 2337.1 | 1396.7 | 1200 | 1.228 | 1.05 | 1.153 | 0.917 | 0.901 | 0.858 | 7.49 | -7.84 | -8.05 | 0.837 | 0.788 | 0.944 | 6.84 | -6.96 | 4.39 | 0.73 | 0.79 | 0.905 | 6.27 | 7.23 | 7.06 | 0.799 | 0.909 | 0.71 | -9.09 | 6 | 9.15 | Very Poor_Mixed | 1040.6 | 1200 | 1.05 | 0.917 | 8.05 | 0.944 | 9.15 | 0.1322 | 0.6484 | 0.0984 | 0.2709 | 1 | 0.1844 | 0.2483 | 0.3648 | 0.3648 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1957 | 892.8 | 528.6 | 111.4 | 111.2 | 16.7 | 824.6 | 5301.6 | 46.9 | 34.8 | 91 | 89.6 | 82 | 97.3 | 39.8 | 24.8 | 4600 | 5305.9 | 4704.6 | 6943.5 | 8264.6 | 7328.7 | 1.509 | 1.558 | 1.558 | 0.738 | 0.728 | 0.718 | 5.72 | 6.21 | 5.8 | 0.781 | 0.741 | 0.689 | 5.15 | 4.66 | 5.57 | 0.675 | 0.708 | 0.704 | 3.93 | 5.13 | 5.33 | 0.639 | 0.75 | 0.568 | 4.1 | -5.24 | -4.33 | Poor_Mixed | 4600 | 6943.5 | 1.509 | 0.738 | 6.21 | 0.781 | 5.57 | 0.4456 | 0.7368 | 0.5232 | 0.5865 | 1 | 0.413 | 0.4589 | 0.5819 | 0.5819 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1958 | 119.8 | 150.1 | 70.4 | 50 | 4.7 | 350 | 2940.1 | 59 | 21.1 | 79 | 75.6 | 71.1 | 83.4 | 35.3 | 13.5 | 9472.6 | 9763.5 | 9445 | 18461.3 | 18759.8 | 18702.5 | 1.949 | 1.921 | 1.98 | 0.517 | 0.515 | 0.539 | 2 | 2 | 2.33 | 0.5 | 0.5 | 0.521 | 2.35 | 2.08 | -2.31 | 0.516 | 0.522 | 0.504 | 2.91 | 2.77 | 3.02 | 0.5 | 0.535 | 0.539 | 2.67 | 2.6 | -2.81 | Good_Mixed | 9445 | 18461.3 | 1.921 | 0.539 | 2.33 | 0.539 | 3.02 | 0.8706 | 0.9514 | 0.9069 | 0.9318 | 1 | 0.9058 | 0.8806 | 0.9144 | 0.9144 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1959 | 100 | 128.3 | 67.8 | 50 | 2.4 | 352.1 | 2588.2 | 60 | 21.8 | 76.1 | 78.6 | 70 | 82.4 | 35.2 | 10 | 9697.6 | 10000 | 10000 | 18572.5 | 19736.7 | 20000 | 1.915 | 1.974 | 2 | 0.536 | 0.534 | 0.509 | 2.7 | -2 | -2.29 | 0.531 | 0.525 | 0.511 | 2 | 2.64 | 2.06 | 0.5 | 0.5 | 0.554 | -2 | 2.26 | 2.7 | 0.5 | 0.512 | 0.528 | 2 | 2.77 | 2 | Good_Mixed | 9697.6 | 18572.5 | 1.915 | 0.536 | 2.7 | 0.554 | 2.77 | 0.9203 | 0.9331 | 0.9234 | 1 | 1 | 0.8828 | 0.8927 | 0.9287 | 0.9287 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1960 | 898.7 | 598.4 | 104.5 | 135.4 | 20.9 | 887.6 | 5854.8 | 59 | 21.9 | 76.6 | 76.4 | 70 | 82.2 | 35 | 10.8 | 9899 | 9195.4 | 10000 | 18382.8 | 17733.5 | 19653.8 | 1.857 | 1.929 | 1.965 | 0.537 | 0.576 | 0.589 | 3.15 | -3.44 | 3.09 | 0.564 | 0.521 | 0.563 | 2.36 | 2.41 | 2 | 0.536 | 0.604 | 0.508 | 2.23 | -2.98 | 3.37 | 0.523 | 0.555 | 0.55 | 2.26 | -2.72 | 2.93 | Poor_DGA | 9195.4 | 17733.5 | 1.857 | 0.589 | 3.44 | 0.604 | 3.37 | 0.3802 | 0.9307 | 0.9419 | 0.9892 | 1 | 0.7473 | 0.7828 | 0.7559 | 0.7559 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1961 | 678.5 | 406.6 | 105.6 | 109.5 | 14.3 | 699.2 | 4901.4 | 60 | 21 | 77.4 | 75.4 | 71.1 | 81.6 | 35.6 | 14 | 8808 | 9910.2 | 10000 | 16460 | 19242.1 | 20000 | 1.869 | 1.942 | 2 | 0.574 | 0.579 | 0.549 | 3.36 | -3.2 | 3.34 | 0.554 | 0.54 | 0.594 | 2.89 | 2.28 | 2.28 | 0.525 | 0.539 | 0.557 | 2.65 | 2.63 | 2.37 | 0.536 | 0.5 | 0.53 | -2.87 | -2.9 | -2.47 | Poor_DGA | 8808 | 16460 | 1.869 | 0.579 | 3.36 | 0.594 | 2.9 | 0.5189 | 0.9543 | 0.9335 | 0.9194 | 1 | 0.7408 | 0.7973 | 0.7908 | 0.7908 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1962 | 452.4 | 298.7 | 77 | 74 | 3 | 522.1 | 3662.7 | 58.5 | 20.8 | 79.3 | 80.7 | 71.2 | 82.3 | 36.5 | 21.1 | 363.9 | 7803 | 7419.9 | 642.7 | 13757.8 | 12932.4 | 1.766 | 1.763 | 1.743 | 0.982 | 0.933 | 0.99 | 9.55 | 9.84 | -9.84 | 0.545 | 0.628 | 0.627 | 3.38 | 4.02 | -3.5 | 0.555 | 0.563 | 0.584 | 3.52 | 2.65 | 3.6 | 0.661 | 0.579 | 0.584 | 3.25 | 3.16 | 2.98 | Critical_Winding_TD_Cap | 363.9 | 642.7 | 1.743 | 0.99 | 9.84 | 0.661 | 4.02 | 0.7656 | 0.9605 | 0.851 | 0.7114 | 0.85 | 0.0335 | 0.6584 | 0.6865 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_TV_TanDelta_pct
1963 | 1619.4 | 894.3 | 132 | 187.5 | 73.8 | 1303.3 | 7430.5 | 55.3 | 21.9 | 77.1 | 78 | 73.5 | 83.5 | 37 | 12.6 | 9329.6 | 9482.9 | 8283.1 | 17613.6 | 18025.7 | 14450.9 | 1.888 | 1.901 | 1.745 | 0.508 | 0.586 | 0.569 | 2 | 3.34 | -3.22 | 0.607 | 0.635 | 0.582 | -3.33 | 3.4 | 3.72 | 0.616 | 0.559 | 0.572 | 3.18 | -3.33 | -4.06 | 0.612 | 0.581 | 0.624 | 3.61 | 4.11 | 3.42 | Critical_DGA | 8283.1 | 14450.9 | 1.745 | 0.586 | 3.34 | 0.635 | 4.11 | 0.0937 | 0.9307 | 0.8678 | 0.953 | 1 | 0.8034 | 0.6341 | 0.6561 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1964 | 124.5 | 174.7 | 72.3 | 53.6 | 2.8 | 390.9 | 2824.1 | 59 | 20.5 | 79.8 | 75.4 | 71 | 80.7 | 35.3 | 13.4 | 10000 | 10000 | 9611.7 | 19265.3 | 19454 | 19223.5 | 1.927 | 1.945 | 2 | 0.515 | 0.5 | 0.59 | 2 | 2 | -2.65 | 0.515 | 0.507 | 0.502 | -2.3 | -2 | 2 | 0.514 | 0.517 | 0.505 | 2.18 | 2.19 | -2.13 | 0.516 | 0.528 | 0.5 | -2.18 | 2 | -2.31 | Good_Mixed | 9611.7 | 19223.5 | 1.927 | 0.59 | 2.65 | 0.528 | 2.31 | 0.8789 | 0.9709 | 0.9173 | 0.9342 | 1 | 0.8961 | 0.9097 | 0.9239 | 0.9239 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1965 | 201.7 | 220.2 | 72 | 69.4 | 2.3 | 3336.3 | 10549.4 | 32.3 | 48.6 | 75.9 | 78.2 | 70.2 | 80 | 36.6 | 18.9 | 4674.9 | 4631.5 | 4216.2 | 6571.5 | 6603.6 | 6092.9 | 1.406 | 1.426 | 1.445 | 0.649 | 0.712 | 0.642 | 4.56 | 4.95 | 3.71 | 0.541 | 0.566 | 0.59 | 3.24 | -3.02 | 2.74 | 0.545 | 0.5 | 0.557 | -2.79 | 2.96 | 2.5 | 0.551 | 0.577 | 0.544 | 2.99 | 3.15 | 2.1 | Critical_Oil | 4216.2 | 6092.9 | 1.406 | 0.712 | 4.95 | 0.59 | 3.24 | 0.643 | 0.5961 | 0.9319 | 0.7811 | 1 | 0.5563 | 0.7617 | 0.7395 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | Moisture_PPM
1966 | 1618.8 | 941.6 | 141.1 | 188.4 | 31.5 | 1295.2 | 8607.5 | 32.3 | 46.2 | 104.7 | 104.6 | 94.4 | 114.8 | 45 | 32.2 | 2250.6 | 1573.1 | 2071 | 2534.8 | 1651.8 | 2447.6 | 1.126 | 1.05 | 1.182 | 0.877 | 0.875 | 0.912 | 8.66 | 8.14 | 8.28 | 0.929 | 0.865 | 0.762 | 8.98 | 8.69 | -6.72 | 0.87 | 0.892 | 0.9 | -7.55 | 8.43 | 8.25 | 0.868 | 0.943 | 0.83 | 7.84 | -8.18 | -8.83 | Very Poor_Mixed | 1573.1 | 1651.8 | 1.05 | 0.912 | 8.66 | 0.943 | 8.98 | 0.0816 | 0.6184 | 0.1535 | 0.3137 | 1 | 0.158 | 0.1622 | 0.337 | 0.337 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1967 | 428.3 | 351.4 | 84.1 | 76.9 | 1.9 | 656.1 | 3646.5 | 52.7 | 24.5 | 78.7 | 77.9 | 70.6 | 86.3 | 35 | 14 | 726.1 | 991.1 | 1170.3 | 753.4 | 1108.6 | 1283.6 | 1.038 | 1.119 | 1.097 | 1.827 | 0.667 | 0.701 | 5.03 | -5.43 | -5.13 | 0.517 | 0.56 | 0.598 | 3.01 | 3.95 | 3.44 | 0.599 | 0.634 | 0.577 | 3.7 | 3.64 | 3.7 | 0.597 | 0.535 | 0.569 | -3.53 | 3.41 | 3.25 | Critical_IR_PI | 726.1 | 753.4 | 1.038 | 1.827 | 5.43 | 0.634 | 3.95 | 0.7614 | 0.8786 | 0.8748 | 0.9194 | 0.925 | 0.4127 | 0.6797 | 0.7574 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_HV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_HV_TanDelta_pct
1968 | 333.3 | 177.4 | 75.3 | 159 | 72.8 | 468.4 | 3051.2 | 53 | 27.6 | 105.2 | 106.8 | 91.6 | 113.4 | 44.2 | 12.9 | 8204.2 | 8794.9 | 7351.2 | 14618.9 | 16328 | 13281.1 | 1.782 | 1.857 | 1.807 | 0.537 | 0.557 | 0.546 | -2.85 | 3.09 | 2.02 | 0.514 | 0.587 | 0.569 | 2.18 | 2.4 | 2.93 | 0.572 | 0.548 | 0.519 | -2.91 | 3.38 | 4.15 | 0.586 | 0.5 | 0.576 | 3.55 | 2.81 | 2.95 | Critical_Thermal | 7351.2 | 13281.1 | 1.782 | 0.557 | 3.09 | 0.587 | 4.15 | 0.4886 | 0.8293 | 0.1671 | 0.9461 | 1 | 0.819 | 0.7583 | 0.6969 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1969 | 949.7 | 564.4 | 107 | 121.1 | 15.2 | 786.3 | 5249 | 46.1 | 33.9 | 91.7 | 88 | 81.7 | 95.4 | 39.3 | 26 | 6071.6 | 6994.6 | 6322.2 | 9533.4 | 11951.2 | 10215.6 | 1.57 | 1.709 | 1.616 | 0.77 | 0.803 | 0.781 | -5.93 | 6.42 | -6.2 | 0.645 | 0.666 | 0.69 | 4.96 | 5.87 | 3.75 | 0.734 | 0.769 | 0.687 | 2.51 | 4.57 | 4.28 | 0.663 | 0.613 | 0.682 | 5.13 | 5.44 | -5.37 | Poor_Mixed | 6071.6 | 9533.4 | 1.57 | 0.803 | 6.42 | 0.769 | 5.87 | 0.446 | 0.7473 | 0.544 | 0.5442 | 1 | 0.3505 | 0.4775 | 0.5778 | 0.5778 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1970 | 720.3 | 458 | 96.6 | 101.2 | 12 | 748.1 | 4537.6 | 49.5 | 31.3 | 90 | 86.7 | 80.5 | 97.5 | 39.2 | 22.6 | 7136.1 | 7084.1 | 5344.5 | 12180.4 | 11962.1 | 8422.2 | 1.707 | 1.689 | 1.576 | 0.656 | 0.708 | 0.686 | -5.15 | 5.53 | 5.03 | 0.603 | 0.565 | 0.626 | -4.55 | -4.04 | 4.7 | 0.566 | 0.673 | 0.574 | 3.92 | 5.2 | 3.56 | 0.643 | 0.581 | 0.683 | 3.52 | -3.52 | 5.14 | Poor_Mixed | 5344.5 | 8422.2 | 1.576 | 0.708 | 5.53 | 0.683 | 5.2 | 0.5388 | 0.7791 | 0.5621 | 0.6619 | 1 | 0.492 | 0.5895 | 0.6525 | 0.6525 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
1971 | 335 | 199.7 | 80.7 | 76.4 | 3.6 | 499.9 | 3607.6 | 40.1 | 39.2 | 81.6 | 80.9 | 74.1 | 85.8 | 36.4 | 15.3 | 6723.3 | 7899.4 | 5813.9 | 11744.3 | 13002.4 | 9348.1 | 1.747 | 1.646 | 1.608 | 0.637 | 0.606 | 0.616 | -4.62 | 3.57 | 3.7 | 0.566 | 0.542 | 0.561 | 2.86 | 2.82 | 2.5 | 0.5 | 0.562 | 0.5 | 2.14 | 2.09 | 3.02 | 0.562 | 0.5 | 0.532 | 2 | -3.38 | -2.43 | Poor_Oil | 5813.9 | 9348.1 | 1.608 | 0.637 | 4.62 | 0.566 | 3.38 | 0.7755 | 0.6883 | 0.7872 | 0.8855 | 1 | 0.633 | 0.8289 | 0.7973 | 0.7973 | Fair | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1972 | 527 | 285.6 | 81.7 | 77.1 | 9.6 | 665.5 | 4370.5 | 52.2 | 27.1 | 83.4 | 81.7 | 75 | 89.2 | 37 | 16.4 | 7633.8 | 8426.7 | 8642.5 | 13204.5 | 14820.5 | 15260.2 | 1.73 | 1.759 | 1.766 | 0.642 | 0.654 | 0.557 | 4.18 | 4.34 | 3.43 | 0.523 | 0.547 | 0.544 | 2.41 | 2.92 | 3.73 | 0.585 | 0.615 | 0.577 | 3.65 | 3.45 | 2.61 | 0.567 | 0.555 | 0.586 | 3.48 | 3.59 | -3.68 | Fair_Mixed | 7633.8 | 13204.5 | 1.73 | 0.654 | 4.34 | 0.615 | 3.73 | 0.6445 | 0.8367 | 0.7393 | 0.855 | 1 | 0.638 | 0.7056 | 0.7545 | 0.7545 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
1973 | 1442.5 | 885.9 | 129.8 | 165.8 | 29.1 | 1215.5 | 8045.6 | 36.1 | 46.2 | 105.7 | 103.6 | 94.9 | 114.6 | 44.9 | 31.7 | 2350.9 | 2625.3 | 1449 | 2673.6 | 3022.1 | 1588.6 | 1.137 | 1.151 | 1.096 | 0.914 | 0.975 | 0.86 | 8.35 | -9.84 | -7.96 | 0.784 | 0.794 | 0.696 | 6.61 | -5.5 | -5.86 | 0.763 | 0.769 | 0.812 | 5.85 | 8.11 | 6.07 | 0.822 | 0.867 | 0.913 | 5.63 | 6.83 | 7.89 | Very Poor_Mixed | 1449 | 1588.6 | 1.096 | 0.975 | 9.84 | 0.913 | 8.11 | 0.1553 | 0.6184 | 0.1525 | 0.3329 | 1 | 0.121 | 0.2837 | 0.3729 | 0.3729 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1974 | 477 | 316.8 | 86.8 | 129 | 68.7 | 652.8 | 3624.9 | 58.9 | 21.4 | 107.8 | 109.3 | 95.5 | 117.8 | 45.8 | 15.8 | 8056.6 | 7512.1 | 7606.1 | 14731.8 | 13172.9 | 13528.3 | 1.829 | 1.754 | 1.779 | 0.529 | 0.564 | 0.597 | 2.76 | -2.89 | 3.09 | 0.666 | 0.591 | 0.52 | 3.46 | 2.32 | -2.81 | 0.573 | 0.533 | 0.542 | -2.79 | -2.77 | 2.32 | 0.537 | 0.556 | 0.509 | 2.91 | 3 | 2.81 | Critical_Thermal | 7512.1 | 13172.9 | 1.754 | 0.597 | 3.09 | 0.666 | 3.46 | 0.4476 | 0.9432 | 0.0836 | 0.8718 | 1 | 0.7756 | 0.7523 | 0.681 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
1975 | 1049.1 | 570.1 | 104.4 | 127.9 | 19.2 | 849.6 | 6001.3 | 44.9 | 32.8 | 91.2 | 89 | 83.7 | 98.2 | 38.8 | 27.2 | 5285.9 | 5524.3 | 4239.9 | 7915.7 | 8289.6 | 5672.6 | 1.498 | 1.501 | 1.338 | 0.745 | 0.767 | 0.732 | 6.1 | -5.74 | 5.64 | 0.673 | 0.669 | 0.599 | 3.33 | 4.34 | 4.05 | 0.607 | 0.679 | 0.666 | 5.2 | 4.28 | 5.3 | 0.648 | 0.643 | 0.666 | -4.25 | 5.52 | -4.86 | Poor_Mixed | 4239.9 | 5672.6 | 1.338 | 0.767 | 6.1 | 0.679 | 5.52 | 0.3917 | 0.7605 | 0.5169 | 0.5011 | 1 | 0.4004 | 0.5204 | 0.5756 | 0.5756 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1976 | 195.6 | 213.6 | 68.6 | 54.3 | 1.9 | 424.8 | 3173.3 | 60 | 20 | 82 | 81.2 | 74.1 | 85.9 | 36.8 | 12.1 | 5985.6 | 5755.3 | 5366 | 9046.5 | 8702.8 | 8426.6 | 1.511 | 1.512 | 1.57 | 0.652 | 0.631 | 0.647 | 4.51 | 4.28 | 4.63 | 0.554 | 0.53 | 0.531 | 2.41 | 2.76 | 3.04 | 0.563 | 0.501 | 0.511 | 2 | 2.1 | -2.33 | 0.547 | 0.528 | 0.53 | -2.89 | 2.2 | 2 | Poor_IR_PI | 5366 | 8426.6 | 1.511 | 0.652 | 4.63 | 0.563 | 3.04 | 0.8808 | 1 | 0.7789 | 0.964 | 1 | 0.5758 | 0.8273 | 0.8558 | 0.8558 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1977 | 1290.3 | 845.7 | 128.1 | 170.6 | 32.6 | 1125.9 | 7383.7 | 39.5 | 40 | 102.8 | 105.5 | 89.3 | 111 | 42.7 | 34.7 | 3781.4 | 2885.8 | 3081.2 | 4689.6 | 3645.8 | 4161.9 | 1.24 | 1.263 | 1.351 | 0.836 | 0.818 | 0.846 | 8.05 | -12.2 | 7.69 | 0.844 | 0.754 | 0.698 | 7.52 | 6.48 | 5.09 | 0.728 | 0.738 | 0.769 | 4.89 | 6.68 | -5.63 | 0.72 | 0.714 | 0.79 | -6.05 | -5.38 | 5.94 | Critical_Mixed | 2885.8 | 3645.8 | 1.24 | 0.846 | 12.2 | 0.844 | 7.52 | 0.1705 | 0.6799 | 0.2237 | 0.2157 | 1 | 0.1874 | 0.3524 | 0.407 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
1978 | 1529.6 | 853.7 | 142.4 | 172.8 | 29 | 1254.2 | 8253.8 | 34.7 | 46.6 | 104.9 | 105.2 | 90.1 | 114.4 | 44.2 | 31.9 | 2932.8 | 1207.1 | 2452.2 | 3492.8 | 1373.5 | 3137.3 | 1.191 | 1.138 | 1.279 | 0.91 | 0.888 | 0.951 | 8.44 | 7.95 | 8.77 | 0.805 | 0.764 | 0.799 | 8.18 | 6.51 | 8.65 | 0.808 | 0.73 | 0.876 | 6.36 | 5.78 | 5.57 | 0.734 | 0.811 | 0.702 | 5.6 | -5.1 | 4.77 | Very Poor_Mixed | 1207.1 | 1373.5 | 1.138 | 0.951 | 8.77 | 0.876 | 8.65 | 0.1301 | 0.6147 | 0.1812 | 0.3252 | 1 | 0.1369 | 0.3115 | 0.3759 | 0.3759 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
1979 | 866.5 | 525.8 | 100 | 107.5 | 18.4 | 752.7 | 5865.9 | 58.1 | 21.6 | 75.5 | 76.7 | 72.2 | 80 | 35 | 10.7 | 9534.3 | 10000 | 9424.4 | 18408.3 | 19601.5 | 17374.9 | 1.931 | 1.96 | 1.844 | 0.604 | 0.559 | 0.563 | 3.8 | 2.36 | 3.3 | 0.514 | 0.5 | 0.564 | -2.01 | 2.37 | -2 | 0.547 | 0.542 | 0.5 | 2.8 | 2.63 | 2.92 | 0.522 | 0.553 | 0.502 | 2.29 | -2.05 | 2.57 | Poor_DGA | 9424.4 | 17374.9 | 1.844 | 0.604 | 3.8 | 0.564 | 2.92 | 0.4525 | 0.938 | 0.9391 | 0.9909 | 1 | 0.7417 | 0.8571 | 0.7872 | 0.7872 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1980 | 1729.5 | 895.2 | 136.1 | 161.7 | 31.2 | 1294.1 | 7981.4 | 33.1 | 48.3 | 109.3 | 105.8 | 96.8 | 118.2 | 45.3 | 33.5 | 2094.4 | 1483.1 | 1064.6 | 2415.8 | 1566 | 1200 | 1.153 | 1.056 | 1.127 | 0.984 | 0.947 | 0.99 | -9.84 | 9.5 | 9.84 | 0.819 | 0.945 | 0.721 | -8.37 | -8.28 | 9.75 | 0.855 | 0.865 | 0.938 | 6.88 | 9.02 | -5.51 | 0.834 | 0.805 | 0.829 | -7.6 | 8.31 | -6.14 | Very Poor_Mixed | 1064.6 | 1200 | 1.056 | 0.99 | 9.84 | 0.945 | 9.75 | 0.1148 | 0.5988 | 0.0892 | 0.2631 | 1 | 0.0307 | 0.2014 | 0.3232 | 0.3232 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1981 | 221.8 | 206 | 76.7 | 69.4 | 1.5 | 475.4 | 3763.8 | 58.6 | 21.2 | 78.5 | 78.3 | 70.2 | 80 | 35.6 | 15 | 5453.1 | 5075.2 | 6498.9 | 8893.4 | 7366.3 | 10481.9 | 1.631 | 1.451 | 1.613 | 0.559 | 0.64 | 0.549 | 3.33 | -3.48 | 3.06 | 0.54 | 0.515 | 0.537 | 2.32 | 2.04 | 2.6 | 0.514 | 0.5 | 0.539 | 2.74 | 2 | 2 | 0.554 | 0.502 | 0.57 | -2.81 | -2 | 2 | Poor_IR_PI | 5075.2 | 7366.3 | 1.451 | 0.64 | 3.48 | 0.57 | 2.81 | 0.8528 | 0.9486 | 0.9073 | 0.8935 | 1 | 0.7246 | 0.8502 | 0.8769 | 0.8769 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1982 | 185.8 | 189.5 | 69.4 | 71.3 | 4.1 | 420.5 | 2500 | 50.2 | 27.9 | 76.9 | 76.7 | 72.7 | 82.4 | 35 | 12.2 | 8960.6 | 7984.2 | 6764.6 | 16677.9 | 14270.4 | 11556.9 | 1.861 | 1.787 | 1.708 | 0.541 | 0.583 | 0.517 | 2 | 3.52 | 2.52 | 0.554 | 0.527 | 0.535 | 2 | 2.18 | 2.37 | 0.518 | 0.5 | 0.5 | 2 | 2 | 2.69 | 0.545 | 0.5 | 0.5 | 2.87 | -2.03 | 2 | Fair_Oil | 6764.6 | 11556.9 | 1.708 | 0.583 | 3.52 | 0.554 | 2.87 | 0.8159 | 0.825 | 0.9049 | 0.9618 | 1 | 0.823 | 0.8951 | 0.8779 | 0.8779 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1983 | 138.6 | 212.5 | 67 | 56.7 | 4 | 409.1 | 2592.4 | 56.4 | 24.7 | 78.5 | 77.3 | 71.7 | 84.6 | 36 | 12.2 | 10000 | 9488.3 | 9440.8 | 20000 | 18187.9 | 17800.4 | 2 | 1.917 | 1.885 | 0.515 | 0.506 | 0.5 | 2.33 | 2 | 2.86 | 0.561 | 0.538 | 0.5 | -3.09 | -2.43 | 2.41 | 0.506 | 0.533 | 0.546 | 2.16 | 2.35 | -2.24 | 0.501 | 0.508 | 0.551 | 2.18 | 2.24 | 2.15 | Good_Mixed | 9440.8 | 17800.4 | 1.885 | 0.515 | 2.86 | 0.561 | 3.09 | 0.8447 | 0.8751 | 0.8761 | 0.9618 | 1 | 0.9321 | 0.8545 | 0.8962 | 0.8962 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1984 | 1392.3 | 798.8 | 131.7 | 154.5 | 32.7 | 1154.2 | 7149.1 | 34.5 | 43.2 | 103.7 | 105.6 | 94.9 | 115.1 | 43.1 | 32.7 | 2395.4 | 2351.7 | 837.9 | 2975.5 | 2888.1 | 1200 | 1.242 | 1.228 | 1.432 | 0.913 | 0.883 | 0.894 | 8.31 | 8.26 | 9.24 | 0.791 | 0.757 | 0.791 | -6.65 | 6.29 | 7.55 | 0.824 | 0.763 | 0.781 | 8.04 | 8.55 | 5.88 | 0.873 | 0.901 | 0.867 | 6.76 | 8.64 | -7.5 | Very Poor_Mixed | 837.9 | 1200 | 1.228 | 0.913 | 9.24 | 0.901 | 8.64 | 0.1784 | 0.6474 | 0.163 | 0.2943 | 1 | 0.1395 | 0.2415 | 0.3763 | 0.3763 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1985 | 577.9 | 388.6 | 76.9 | 86.7 | 1.2 | 536.6 | 3506.9 | 54.2 | 22.8 | 80 | 76.2 | 72.2 | 85.8 | 36.7 | 16.7 | 919.4 | 1123.6 | 1975.9 | 984.2 | 1259 | 2350.2 | 1.07 | 1.121 | 1.189 | 0.701 | 0.696 | 0.664 | 5.16 | 4.48 | 4.49 | 0.5 | 0.535 | 0.502 | 3.19 | -3.25 | -2.53 | 0.554 | 1.556 | 0.56 | 2.53 | 3.1 | 2.41 | 0.555 | 0.556 | 0.521 | 2.06 | -2.55 | 2.36 | Critical_IR_PI | 919.4 | 984.2 | 1.07 | 0.701 | 5.16 | 1.556 | 3.25 | 0.7859 | 0.9108 | 0.8609 | 0.8465 | 0.925 | 0.5185 | 0.7536 | 0.7904 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_LV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Winding_HV_TanDelta_pct
1986 | 212.3 | 192.7 | 70.9 | 71.4 | 1 | 365.7 | 2500 | 56.1 | 23 | 80.7 | 83.5 | 72.7 | 88 | 36.3 | 12.8 | 9667.1 | 8947.8 | 10000 | 18633 | 17434.9 | 19301.2 | 1.927 | 1.949 | 1.93 | 0.566 | 0.588 | 0.554 | 3.44 | 3.49 | -2.94 | 0.544 | 0.506 | 0.806 | -3.45 | 3.84 | 6.29 | 0.554 | 0.547 | 0.627 | 2 | 2.49 | 2 | 0.5 | 0.5 | 0.56 | 2.82 | 2.52 | 3.13 | Poor_Bushing_TD_Cap | 8947.8 | 17434.9 | 1.927 | 0.588 | 3.49 | 0.806 | 6.29 | 0.932 | 0.9067 | 0.775 | 0.9484 | 1 | 0.7389 | 0.7498 | 0.8651 | 0.8651 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
1987 | 401.4 | 230.5 | 83.5 | 76 | 2.3 | 554.4 | 3693.8 | 52.7 | 60 | 81.9 | 82.5 | 73.8 | 89.5 | 36.3 | 14.6 | 7682.9 | 7997.3 | 8259.1 | 13337.3 | 14100.6 | 14200.8 | 1.736 | 1.763 | 1.719 | 0.609 | 0.577 | 0.633 | 3.49 | 2.04 | -3.86 | 0.847 | 0.592 | 0.606 | 8.27 | 4.03 | 3.26 | 0.538 | 0.584 | 0.604 | 2.77 | 2.13 | -2.86 | 0.551 | 0.62 | 0.582 | 2.9 | -2.13 | 3.69 | Critical_Bushing_TD_Cap | 7682.9 | 13337.3 | 1.719 | 0.633 | 3.86 | 0.847 | 8.27 | 0.7824 | 0.5833 | 0.7562 | 0.904 | 1 | 0.706 | 0.6306 | 0.7588 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
1988 | 1458.8 | 882.5 | 132.4 | 187.7 | 34.3 | 1217 | 7988.5 | 37.3 | 41.6 | 103.3 | 103 | 92.6 | 113.1 | 44.2 | 29.5 | 781.1 | 1533.1 | 2315.6 | 1200 | 1817.1 | 2675.2 | 1.536 | 1.185 | 1.155 | 0.952 | 0.893 | 0.935 | -9.75 | 8.25 | 8.41 | 0.899 | 0.729 | 0.837 | -7.6 | 6.68 | 5.51 | 0.704 | 0.752 | 0.784 | 6.63 | 5.75 | -7.74 | 0.71 | 0.629 | 0.739 | -6.88 | 7.78 | 7.77 | Very Poor_Mixed | 781.1 | 1200 | 1.155 | 0.952 | 9.75 | 0.899 | 7.78 | 0.1114 | 0.6634 | 0.1948 | 0.4164 | 1 | 0.1088 | 0.3201 | 0.3806 | 0.3806 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1989 | 828.2 | 513.8 | 110.8 | 124.7 | 21.7 | 883.9 | 6110.9 | 58.7 | 21.7 | 80.5 | 80 | 73.4 | 86.1 | 37.7 | 14.1 | 10000 | 8157.2 | 9294.2 | 18877.8 | 14654.3 | 18108 | 1.888 | 1.796 | 1.948 | 0.501 | 0.556 | 0.514 | 2.05 | 2.77 | -2.33 | 0.539 | 0.5 | 0.55 | 2.87 | -2.31 | 3.33 | 0.515 | 0.528 | 0.613 | -2.77 | 2.27 | 2.94 | 0.562 | 0.526 | 0.592 | 2.8 | 2.94 | -3.31 | Poor_DGA | 8157.2 | 14654.3 | 1.796 | 0.556 | 2.77 | 0.613 | 3.33 | 0.3937 | 0.9355 | 0.8012 | 0.9169 | 1 | 0.8933 | 0.7782 | 0.7618 | 0.7618 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1990 | 1766 | 982.4 | 148.3 | 197 | 34.3 | 1627.1 | 20945.9 | 52 | 29 | 81 | 86.4 | 75.9 | 87.8 | 36.6 | 18.1 | 8140 | 8543.1 | 7761.4 | 14894.4 | 16203.9 | 14067 | 1.83 | 1.897 | 1.812 | 0.579 | 0.601 | 0.612 | 3.28 | -3.17 | 4.11 | 0.561 | 0.597 | 0.608 | -2.61 | -3.85 | 3.75 | 0.582 | 0.618 | 0.533 | 3.25 | -4.13 | 2.86 | 0.628 | 0.597 | 0.645 | -3.38 | 2.75 | 3.34 | Critical_DGA | 7761.4 | 14067 | 1.812 | 0.612 | 4.11 | 0.645 | 4.13 | 0.0111 | 0.8095 | 0.7253 | 0.8054 | 1 | 0.6872 | 0.6511 | 0.5861 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | C2H2
1991 | 433.7 | 324.7 | 89.3 | 91.3 | 10.9 | 659.1 | 4122.6 | 59.4 | 21.8 | 83.6 | 80.8 | 73.9 | 87 | 36.6 | 12.5 | 9485.3 | 9028.3 | 9199.1 | 17974.7 | 16832.9 | 17480.5 | 1.895 | 1.864 | 1.9 | 0.511 | 0.5 | 0.541 | 2.22 | 2.88 | 2.42 | 0.554 | 0.511 | 0.524 | 2.85 | -2.67 | 2.1 | 0.563 | 0.512 | 0.514 | 2.2 | 3.32 | 2.04 | 0.506 | 0.548 | 0.568 | 2.87 | 3.42 | 2.37 | Fair_DGA | 9028.3 | 16832.9 | 1.864 | 0.541 | 2.88 | 0.568 | 3.42 | 0.6184 | 0.9331 | 0.7669 | 0.9552 | 1 | 0.8985 | 0.8149 | 0.8235 | 0.8235 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1992 | 176 | 172.1 | 74.3 | 50 | 1.1 | 452.9 | 2954.6 | 60 | 20 | 76.7 | 77.7 | 73.6 | 84.4 | 35.9 | 12.4 | 10000 | 9607.2 | 8591.5 | 19820.1 | 18112.3 | 16429.8 | 1.982 | 1.885 | 1.912 | 0.501 | 0.501 | 0.517 | 2 | 2.07 | 3.27 | 0.5 | 0.543 | 0.5 | 2.29 | 3.09 | 2.18 | 0.553 | 0.514 | 0.5 | -2 | 2.42 | 2.41 | 0.531 | 0.565 | 0.527 | -2.69 | -2.36 | 2.71 | Good_Mixed | 8591.5 | 16429.8 | 1.885 | 0.517 | 3.27 | 0.565 | 3.09 | 0.9316 | 1 | 0.8754 | 0.9575 | 1 | 0.9328 | 0.8593 | 0.9336 | 0.9336 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1993 | 1539.1 | 799 | 137.2 | 164 | 27 | 1167.4 | 7821.5 | 35.9 | 43.1 | 106.3 | 107.6 | 94.5 | 118 | 44 | 31 | 2784.7 | 2159.6 | 2411.5 | 3475.5 | 2589.2 | 2794.8 | 1.248 | 1.199 | 1.159 | 0.89 | 0.899 | 0.89 | 8.6 | 8.93 | 8.03 | 0.855 | 0.81 | 0.926 | -7.11 | 7.16 | 7.32 | 0.769 | 0.74 | 0.83 | 6 | 5.03 | -5.46 | 0.844 | 0.773 | 0.86 | 6.56 | 6.56 | 6.17 | Very Poor_Mixed | 2159.6 | 2589.2 | 1.159 | 0.899 | 8.93 | 0.926 | 7.32 | 0.1718 | 0.6484 | 0.1188 | 0.3597 | 1 | 0.1463 | 0.2668 | 0.3791 | 0.3791 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
1994 | 920 | 497.3 | 100.9 | 126.3 | 20.8 | 864.6 | 5387.8 | 48.9 | 30.6 | 91.9 | 89 | 81.6 | 96.5 | 38.8 | 24 | 6670.5 | 6456 | 5674.7 | 10811.7 | 10326.3 | 8632.9 | 1.621 | 1.599 | 1.521 | 0.71 | 0.685 | 0.77 | 5.86 | 4.7 | 6.35 | 0.62 | 0.734 | 0.736 | -5 | 4.55 | -5.1 | 0.648 | 0.633 | 0.644 | 4.17 | -4.68 | 4.97 | 0.613 | 0.657 | 0.667 | -3.82 | 5.43 | 3.53 | Poor_Mixed | 5674.7 | 8632.9 | 1.521 | 0.77 | 6.35 | 0.736 | 5.43 | 0.4092 | 0.7881 | 0.5342 | 0.6143 | 1 | 0.4352 | 0.5063 | 0.5931 | 0.5931 | Poor | 0 | 1 | DGA | 0 |  | C2H2
1995 | 223.7 | 186.2 | 73.3 | 65.6 | 1.9 | 362.1 | 3318.7 | 57.2 | 23.5 | 77.5 | 77 | 71.4 | 82.8 | 35.3 | 11.8 | 9218.3 | 9417.7 | 9353.6 | 17416 | 18088.5 | 17924.4 | 1.889 | 1.921 | 1.916 | 0.5 | 0.553 | 0.5 | 2.52 | 2.79 | 2 | 0.579 | 0.5 | 0.515 | 3.1 | 3.13 | 2.76 | 0.582 | 0.571 | 0.529 | 2.03 | 2.4 | -2 | 0.585 | 0.536 | 0.535 | 2.11 | 2.87 | -2.88 | Good_Mixed | 9218.3 | 17416 | 1.889 | 0.553 | 2.79 | 0.585 | 3.13 | 0.8725 | 0.8969 | 0.9041 | 0.9703 | 1 | 0.9168 | 0.7885 | 0.895 | 0.895 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
1996 | 1401.1 | 837.5 | 131.3 | 167.9 | 31.2 | 1181.2 | 7632.8 | 34.3 | 45.7 | 105.7 | 104.1 | 92.2 | 113.9 | 43.3 | 32.8 | 2565.9 | 2169.1 | 2334.8 | 3222.5 | 2580.5 | 2745.9 | 1.256 | 1.19 | 1.176 | 0.957 | 0.911 | 0.918 | -8.97 | 8.64 | 8.37 | 0.728 | 0.879 | 0.879 | 8.35 | -6.71 | 8.56 | 0.843 | 0.743 | 0.813 | -7.85 | 6.25 | -9.11 | 0.89 | 0.857 | 0.894 | 8.76 | 7.48 | 6.69 | Very Poor_Mixed | 2169.1 | 2580.5 | 1.176 | 0.957 | 8.97 | 0.894 | 9.11 | 0.16 | 0.6232 | 0.1799 | 0.2904 | 1 | 0.1144 | 0.2098 | 0.3611 | 0.3611 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1997 | 1470.2 | 838.3 | 127.1 | 171 | 34.3 | 1115.6 | 7679.7 | 32.7 | 45.4 | 104.3 | 104.2 | 92.8 | 110.7 | 43.6 | 30.1 | 2454.1 | 2619.3 | 2068.2 | 2994.3 | 3077.8 | 2463.7 | 1.22 | 1.175 | 1.191 | 0.885 | 0.908 | 0.946 | 8.12 | 8.35 | -8.57 | 0.706 | 0.949 | 0.955 | -6.7 | 8.25 | 8.4 | 0.728 | 0.734 | 0.802 | -6.9 | 7.23 | 5.78 | 0.774 | 0.748 | 0.785 | 6.11 | 8.12 | 8.17 | Very Poor_Mixed | 2068.2 | 2463.7 | 1.175 | 0.946 | 8.57 | 0.955 | 8.4 | 0.1487 | 0.6261 | 0.1976 | 0.3938 | 1 | 0.1412 | 0.2634 | 0.3789 | 0.3789 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
1998 | 1207.9 | 702.1 | 116.4 | 142.6 | 24.6 | 1046.6 | 6500.3 | 55.9 | 25.5 | 76.9 | 77.1 | 71.9 | 81.4 | 35 | 12 | 8881.6 | 8350.2 | 9262.3 | 16954.3 | 15515.8 | 18491 | 1.909 | 1.858 | 1.996 | 0.5 | 0.532 | 0.506 | 2.09 | 2.03 | 2.73 | 0.528 | 0.5 | 0.504 | 2.9 | 2.84 | 2 | 0.533 | 0.504 | 0.559 | 2.45 | 2.73 | 2.61 | 0.512 | 0.546 | 0.531 | 2.87 | 2.65 | 2.26 | Poor_DGA | 8350.2 | 15515.8 | 1.858 | 0.532 | 2.73 | 0.559 | 2.9 | 0.2835 | 0.8617 | 0.9126 | 0.9661 | 1 | 0.9281 | 0.8478 | 0.7564 | 0.7564 | Fair | 1 | 1 | DGA | 0 |  | C2H2
1999 | 895.1 | 516.3 | 107.9 | 106.5 | 18.6 | 779.7 | 5541.2 | 49 | 31.4 | 88.2 | 89.9 | 80.3 | 95.9 | 40.4 | 21.4 | 6948.5 | 6680.3 | 7656.1 | 11048 | 11142.1 | 12694.1 | 1.59 | 1.668 | 1.658 | 0.74 | 0.695 | 0.717 | 5.95 | 4.32 | 5.52 | 0.625 | 0.687 | 0.657 | 4.52 | 4.82 | 4.38 | 0.687 | 0.68 | 0.655 | 4.41 | 5.09 | 4.53 | 0.713 | 0.709 | 0.676 | 4.3 | 4.68 | 3.45 | Poor_Mixed | 6680.3 | 11048 | 1.59 | 0.74 | 5.95 | 0.713 | 5.09 | 0.4454 | 0.7778 | 0.554 | 0.7016 | 1 | 0.4593 | 0.4896 | 0.6076 | 0.6076 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2000 | 1546.3 | 878.1 | 133.9 | 177.5 | 26.7 | 1279.2 | 7978.3 | 32.5 | 48.4 | 103.5 | 104.6 | 92.9 | 113.9 | 44.6 | 33.6 | 2026.4 | 1695.4 | 1423.7 | 2127.7 | 1976 | 1494.9 | 1.05 | 1.166 | 1.05 | 0.968 | 0.951 | 0.981 | 8.81 | 9.29 | 9.84 | 0.917 | 0.808 | 0.837 | 6.63 | 6.73 | 7.76 | 0.768 | 0.928 | 0.695 | -5.18 | 6.71 | 6.2 | 0.743 | 0.668 | 0.792 | 5.39 | 7.13 | 6.02 | Very Poor_Mixed | 1423.7 | 1494.9 | 1.05 | 0.981 | 9.84 | 0.928 | 7.76 | 0.141 | 0.5979 | 0.1761 | 0.2591 | 1 | 0.056 | 0.2956 | 0.3586 | 0.3586 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2001 | 1539.9 | 794.2 | 129.6 | 177.9 | 33.3 | 1220.1 | 7465.7 | 33.4 | 46.8 | 105.1 | 104 | 92.6 | 115 | 42.8 | 33.2 | 690 | 1899.4 | 3012.8 | 1200 | 2160 | 3744.5 | 1.739 | 1.137 | 1.243 | 0.901 | 0.891 | 0.924 | 8.36 | 8.32 | 9.35 | 0.779 | 0.791 | 0.81 | 9.33 | 5.84 | 6.52 | 0.77 | 0.673 | 0.893 | -5.96 | 7.55 | 7.81 | 0.773 | 0.743 | 0.745 | -7.69 | 5.97 | 7.67 | Very Poor_Mixed | 690 | 1200 | 1.137 | 0.924 | 9.35 | 0.893 | 9.33 | 0.1361 | 0.6128 | 0.1796 | 0.2748 | 1 | 0.1297 | 0.2884 | 0.3693 | 0.3693 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2002 | 336.6 | 245.6 | 82.7 | 85.7 | 2.9 | 603.3 | 3953.6 | 55.5 | 20.8 | 77.6 | 78.4 | 71.2 | 84.1 | 35.8 | 12.5 | 8026.8 | 8913.3 | 9291.2 | 14471.7 | 17188.8 | 18471.1 | 1.803 | 1.928 | 1.988 | 0.764 | 0.768 | 0.796 | -5.96 | -5.01 | 6.51 | 0.574 | 0.561 | 0.562 | 2.75 | -2.04 | 2.63 | 0.597 | 0.56 | 0.567 | 2.87 | 3.42 | 3.83 | 0.581 | 0.543 | 0.572 | 3.3 | 2.88 | 3.88 | Poor_Winding_TD_Cap | 8026.8 | 14471.7 | 1.803 | 0.796 | 6.51 | 0.597 | 3.88 | 0.7527 | 0.9605 | 0.8822 | 0.9552 | 1 | 0.3774 | 0.7085 | 0.7798 | 0.7798 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2003 | 501 | 267.8 | 80.6 | 76.7 | 1 | 565.1 | 4339.9 | 59.6 | 50.3 | 76 | 78.8 | 70.7 | 80.5 | 35.8 | 10 | 1052.7 | 1210.8 | 1031.1 | 1131.3 | 1235 | 1074.7 | 1.075 | 1.02 | 1.042 | 0.759 | 0.745 | 0.694 | 6.29 | -5.54 | 4.21 | 0.628 | 0.587 | 0.554 | 2.98 | -3.68 | 3.65 | 0.598 | 0.64 | 0.616 | 3.23 | 3.93 | -2.5 | 0.586 | 0.554 | 0.624 | 4.33 | -3.15 | 3.86 | Critical_IR_PI | 1031.1 | 1074.7 | 1.02 | 0.759 | 6.29 | 0.64 | 4.33 | 0.8369 | 0.5833 | 0.92 | 1 | 1 | 0.4417 | 0.6401 | 0.7583 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2004 | 1650.3 | 927.6 | 141.2 | 186 | 31.4 | 1216.5 | 8722.8 | 36.5 | 45.4 | 108.2 | 109 | 94.2 | 116.5 | 44 | 32.9 | 1609.7 | 690 | 1516.3 | 1806.1 | 1200 | 1692.5 | 1.122 | 1.739 | 1.116 | 0.939 | 0.911 | 0.924 | 8.7 | 9.13 | 8.75 | 0.86 | 0.756 | 0.734 | -8.22 | 6.53 | 8.55 | 0.74 | 0.717 | 0.837 | 7.09 | 9.26 | -8.94 | 0.78 | 0.799 | 0.766 | 8.9 | 6.42 | -6.26 | Very Poor_Mixed | 690 | 1200 | 1.116 | 0.939 | 9.13 | 0.86 | 9.26 | 0.0903 | 0.6261 | 0.11 | 0.2865 | 1 | 0.1069 | 0.2651 | 0.3457 | 0.3457 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2005 | 1624.4 | 910.5 | 142.7 | 192.7 | 34 | 1303.6 | 7910.3 | 31.5 | 47.7 | 107.3 | 104.7 | 94.3 | 115.6 | 44.3 | 31.6 | 1083.3 | 1291.4 | 1063.7 | 1200 | 1355.9 | 1200 | 1.108 | 1.05 | 1.128 | 0.952 | 0.935 | 0.922 | 9.25 | -9.16 | 9.51 | 0.912 | 0.798 | 0.919 | 7.74 | -9.58 | 6.93 | 0.806 | 0.731 | 0.918 | 7.08 | -6.36 | 6.88 | 0.79 | 0.871 | 0.769 | 8.8 | -8.64 | 8.63 | Very Poor_Mixed | 1063.7 | 1200 | 1.05 | 0.952 | 9.51 | 0.919 | 9.58 | 0.077 | 0.6044 | 0.1403 | 0.3368 | 1 | 0.0765 | 0.2084 | 0.3309 | 0.3309 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2006 | 569.3 | 372.6 | 91.5 | 121.1 | 15.1 | 767.2 | 4305.6 | 59.7 | 22.1 | 78.8 | 79.9 | 74.6 | 84.6 | 36.7 | 11.2 | 9605.4 | 9316.8 | 10000 | 18813.1 | 17473.1 | 20000 | 1.959 | 1.875 | 2 | 0.546 | 0.527 | 0.57 | -2.69 | -2.12 | -2.54 | 0.539 | 0.547 | 0.522 | 2.41 | 2 | 2.72 | 0.56 | 0.536 | 0.57 | 2.47 | 2.75 | -2.37 | 0.517 | 0.555 | 0.53 | -2.67 | 3.17 | 2.57 | Fair_DGA | 9316.8 | 17473.1 | 1.875 | 0.57 | 2.69 | 0.57 | 3.17 | 0.5215 | 0.926 | 0.8205 | 0.9821 | 1 | 0.8322 | 0.79 | 0.7914 | 0.7914 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2007 | 901 | 477.9 | 102 | 117.7 | 19 | 826.6 | 5599.8 | 44.2 | 35.3 | 92.1 | 90.1 | 82.4 | 101.7 | 40.9 | 25.6 | 5829.5 | 6777.6 | 5695.6 | 9398.5 | 10705.9 | 8598.4 | 1.612 | 1.58 | 1.51 | 0.764 | 0.755 | 0.711 | 6.2 | -5.48 | 5.76 | 0.753 | 0.62 | 0.683 | 4.07 | 4.54 | 4.05 | 0.716 | 0.688 | 0.678 | 4.45 | 4.62 | 3.82 | 0.702 | 0.687 | 0.642 | -3.84 | 4.16 | 4.23 | Poor_Mixed | 5695.6 | 8598.4 | 1.51 | 0.764 | 6.2 | 0.753 | 4.62 | 0.4334 | 0.731 | 0.481 | 0.5584 | 1 | 0.4054 | 0.4898 | 0.577 | 0.577 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2008 | 1592.9 | 868.2 | 131.6 | 193.9 | 31.5 | 1309.3 | 7872.3 | 30.6 | 46.7 | 105.1 | 107.5 | 94.1 | 117.7 | 44.9 | 35.1 | 876.9 | 799.7 | 690 | 1200 | 1200 | 1200 | 1.368 | 1.501 | 1.739 | 0.934 | 0.99 | 0.985 | 9.27 | 9.64 | 8.9 | 0.955 | 0.793 | 0.832 | 6 | 8.99 | 7.72 | 0.943 | 0.906 | 0.917 | 8.87 | 6.74 | 7.39 | 0.894 | 0.755 | 0.748 | 8.53 | 7.91 | -8.74 | Very Poor_Mixed | 690 | 1200 | 1.368 | 0.99 | 9.64 | 0.955 | 8.99 | 0.1025 | 0.6137 | 0.1232 | 0.1998 | 1 | 0.0562 | 0.1849 | 0.3227 | 0.3227 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2009 | 937.1 | 449.9 | 103.1 | 112 | 15.4 | 854.6 | 5461.9 | 46.7 | 33 | 91.4 | 93.2 | 83.3 | 100.2 | 39.5 | 26.9 | 5443.6 | 5320.7 | 6149.9 | 8893.9 | 8359.3 | 9623.1 | 1.634 | 1.571 | 1.565 | 0.745 | 0.719 | 0.713 | 6.28 | 6.23 | 5.8 | 0.684 | 0.697 | 0.661 | 5.18 | -3.22 | 4.83 | 0.61 | 0.685 | 0.625 | 4.52 | 5.56 | 4.51 | 0.693 | 0.629 | 0.609 | 3.93 | 4.29 | 3.89 | Poor_Mixed | 5320.7 | 8359.3 | 1.565 | 0.745 | 6.28 | 0.697 | 5.56 | 0.4595 | 0.7581 | 0.4764 | 0.512 | 1 | 0.4046 | 0.5199 | 0.5893 | 0.5893 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2010 | 850.8 | 512.5 | 102.4 | 120.8 | 15.6 | 821.3 | 6118.1 | 47.2 | 33.3 | 91.2 | 92.5 | 85.3 | 99 | 40.1 | 26.3 | 4952.1 | 5343.9 | 2944.6 | 7314.1 | 8141.4 | 4012.8 | 1.477 | 1.523 | 1.363 | 0.72 | 0.694 | 0.681 | -5.7 | 5.49 | -4.69 | 0.663 | 0.672 | 0.667 | -4.87 | 4.94 | 4.72 | 0.785 | 0.726 | 0.789 | -5.31 | 6.55 | 5.52 | 0.66 | 0.728 | 0.716 | 5.81 | -3.93 | 3.88 | Poor_Mixed | 2944.6 | 4012.8 | 1.363 | 0.72 | 5.7 | 0.789 | 6.55 | 0.4468 | 0.7544 | 0.472 | 0.5335 | 1 | 0.4745 | 0.428 | 0.5796 | 0.5796 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
2011 | 1660.3 | 895.8 | 136 | 170.8 | 31.5 | 1232.6 | 7775.4 | 32.7 | 46 | 109.3 | 109.3 | 94.9 | 118.1 | 44.9 | 29.8 | 1215 | 2480.6 | 1513.8 | 1275.7 | 2833.2 | 1846.5 | 1.05 | 1.142 | 1.22 | 0.953 | 0.882 | 0.853 | -9.05 | -8.2 | 8.04 | 0.89 | 0.922 | 0.791 | 7.98 | 6.85 | 8.68 | 0.89 | 0.689 | 0.834 | 8.57 | 6.8 | -9.84 | 0.885 | 0.771 | 0.863 | 9.27 | 8.04 | 9.12 | Very Poor_Mixed | 1215 | 1275.7 | 1.05 | 0.953 | 9.05 | 0.922 | 9.84 | 0.12 | 0.6203 | 0.084 | 0.4051 | 1 | 0.1494 | 0.1909 | 0.3484 | 0.3484 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
2012 | 410.7 | 259.9 | 81 | 86.1 | 2.3 | 553.9 | 3358.4 | 56.8 | 24 | 79.8 | 77.8 | 70 | 83.3 | 35.9 | 13.9 | 747.3 | 58.3 | 690 | 801.4 | 73 | 724 | 1.072 | 1.252 | 1.049 | 0.718 | 0.7 | 0.732 | 5.96 | 5.59 | 5.74 | 0.519 | 0.5 | 0.506 | 2 | 2.74 | 3.17 | 0.516 | 0.565 | 0.576 | 3.33 | -2.65 | -2 | 0.528 | 0.549 | 0.572 | -2.74 | -2.92 | 2.53 | Critical_IR_PI | 58.3 | 73 | 1.049 | 0.732 | 5.96 | 0.576 | 3.33 | 0.7701 | 0.8875 | 0.8861 | 0.9219 | 0.7 | 0.4312 | 0.8121 | 0.7523 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2013 | 183.8 | 205.5 | 69.1 | 59.8 | 2.1 | 359.2 | 3152 | 59.9 | 20.5 | 78.8 | 79 | 71.9 | 83.5 | 35.6 | 10 | 7161.5 | 7669.6 | 7703.4 | 11950.7 | 13570.3 | 14150.7 | 1.669 | 1.769 | 1.837 | 0.537 | 0.544 | 0.548 | 2.61 | 2 | 2.95 | 0.513 | 0.5 | 0.516 | 2.19 | 2.23 | 2.88 | 0.542 | 0.513 | 0.5 | -2 | -2.62 | 2.1 | 0.526 | 0.5 | 0.5 | 2.78 | 2 | 2.26 | Fair_IR_PI | 7161.5 | 11950.7 | 1.669 | 0.548 | 2.95 | 0.542 | 2.88 | 0.8813 | 0.9709 | 0.862 | 1 | 1 | 0.8346 | 0.9102 | 0.9137 | 0.9137 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2014 | 1468.8 | 845.7 | 135.5 | 181.4 | 30.8 | 1303.4 | 8530 | 32.9 | 46.7 | 108 | 105.1 | 95.9 | 117.8 | 43.3 | 32.6 | 1049.6 | 1979 | 2955.3 | 1200 | 2279.2 | 3665.2 | 1.143 | 1.152 | 1.24 | 0.951 | 0.918 | 0.936 | 9.17 | 9.23 | 8.51 | 0.749 | 0.889 | 0.76 | 8.05 | -8.01 | 7.02 | 0.801 | 0.88 | 0.869 | 6.85 | -6.02 | -8.27 | 0.79 | 0.909 | 0.839 | 9.4 | 5.34 | 6.04 | Very Poor_Mixed | 1049.6 | 1200 | 1.143 | 0.951 | 9.23 | 0.909 | 9.4 | 0.1163 | 0.6137 | 0.1216 | 0.2982 | 1 | 0.0944 | 0.231 | 0.3446 | 0.3446 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2015 | 289 | 252.8 | 81.3 | 71.1 | 3.5 | 497.5 | 3008.8 | 59.8 | 20 | 77.6 | 79.5 | 71.8 | 81.9 | 35.5 | 14.1 | 9568.5 | 9832.7 | 9864.4 | 18848 | 19459 | 18897.9 | 1.97 | 1.979 | 1.916 | 0.735 | 0.766 | 0.764 | 6.04 | 5.99 | 6.43 | 0.554 | 0.557 | 0.517 | 2.86 | -2.31 | 2.76 | 0.621 | 0.514 | 0.554 | 3.02 | 3.11 | 3.19 | 0.546 | 0.576 | 0.607 | 2.53 | 2.59 | -2.7 | Poor_Winding_TD_Cap | 9568.5 | 18848 | 1.916 | 0.766 | 6.43 | 0.621 | 3.19 | 0.7859 | 1 | 0.8785 | 0.9169 | 1 | 0.3766 | 0.7438 | 0.7968 | 0.7968 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2016 | 1540 | 932 | 144.6 | 176.4 | 31.4 | 1273.6 | 8076.3 | 34.6 | 46.3 | 105.9 | 106.6 | 93.5 | 113.7 | 44.2 | 32.9 | 2444.3 | 2201.7 | 3126.4 | 2803 | 2640.5 | 3764.4 | 1.147 | 1.199 | 1.204 | 0.909 | 0.855 | 0.974 | 9.1 | 8.88 | 9.21 | 0.83 | 0.851 | 0.83 | 7.82 | -6.72 | -7.75 | 0.864 | 0.776 | 0.895 | 5.76 | 7.14 | 8.26 | 0.848 | 0.842 | 0.918 | 7.85 | 8.14 | 5.45 | Very Poor_Mixed | 2201.7 | 2640.5 | 1.147 | 0.974 | 9.21 | 0.918 | 8.26 | 0.1052 | 0.6175 | 0.1521 | 0.2865 | 1 | 0.1057 | 0.2129 | 0.3431 | 0.3431 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2017 | 540.8 | 352.7 | 83 | 92.7 | 9.4 | 672.1 | 4603.3 | 51.7 | 30.4 | 87.4 | 86.3 | 78.6 | 96 | 37.9 | 20.1 | 8721.3 | 7771.8 | 7896.5 | 15635.3 | 12966.7 | 13986.9 | 1.793 | 1.668 | 1.771 | 0.697 | 0.675 | 0.7 | 4.7 | 4.73 | 4.75 | 0.562 | 0.653 | 0.6 | 4.2 | 3.13 | -5.26 | 0.591 | 0.653 | 0.58 | 2.7 | 4.63 | 4.42 | 0.651 | 0.618 | 0.584 | 3.7 | -4.32 | 3.21 | Fair_Mixed | 7771.8 | 12966.7 | 1.668 | 0.7 | 4.75 | 0.653 | 5.26 | 0.6155 | 0.7907 | 0.6106 | 0.7436 | 1 | 0.5137 | 0.603 | 0.6875 | 0.6875 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2018 | 1639.6 | 946.4 | 137.3 | 178.3 | 34.1 | 1331.2 | 8154.2 | 32 | 46.2 | 107.7 | 103.1 | 95.3 | 115.9 | 44 | 32 | 854.2 | 690 | 714.3 | 1200 | 1200 | 1200 | 1.405 | 1.739 | 1.68 | 0.89 | 0.981 | 0.968 | 8.47 | 8.91 | 8.87 | 0.842 | 0.904 | 0.69 | 6 | 8.62 | 9.36 | 0.857 | 0.827 | 0.836 | -6.49 | -7.55 | 9.28 | 0.888 | 0.759 | 0.948 | 8.88 | 8.68 | 7.78 | Very Poor_Mixed | 690 | 1200 | 1.405 | 0.981 | 8.91 | 0.948 | 9.36 | 0.0816 | 0.6184 | 0.1422 | 0.3214 | 1 | 0.0982 | 0.1984 | 0.3344 | 0.3344 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2019 | 896.7 | 560.9 | 107.2 | 123.9 | 23.1 | 895.2 | 5793.4 | 54.3 | 23.2 | 82.1 | 82.1 | 75.3 | 88.1 | 36 | 10.9 | 10000 | 9737 | 10000 | 19767.3 | 19473.9 | 19283.7 | 1.977 | 2 | 1.928 | 0.532 | 0.5 | 0.544 | 2 | 2.01 | 2.65 | 0.526 | 0.539 | 0.562 | 2.72 | 2.56 | 3.09 | 0.562 | 0.574 | 0.556 | 2.81 | 2.51 | 2.28 | 0.558 | 0.529 | 0.5 | 2.17 | 3.59 | 2.36 | Poor_DGA | 9737 | 19283.7 | 1.928 | 0.544 | 2.65 | 0.574 | 3.59 | 0.3809 | 0.9027 | 0.7545 | 0.9875 | 1 | 0.9053 | 0.7853 | 0.7565 | 0.7565 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2020 | 1065.2 | 527.8 | 108 | 137.8 | 21.5 | 839.1 | 6308.7 | 45.2 | 32.4 | 93.1 | 92.1 | 83.8 | 101.4 | 40.8 | 26 | 5866.7 | 6098.1 | 5787.8 | 8921.6 | 9333.2 | 9058.1 | 1.521 | 1.531 | 1.565 | 0.758 | 0.759 | 0.737 | 5.73 | 5.95 | 6.16 | 0.777 | 0.602 | 0.723 | 4.96 | 4.53 | -5.58 | 0.612 | 0.709 | 0.745 | -4.49 | 3.92 | 4.3 | 0.696 | 0.565 | 0.688 | -3.82 | 3.68 | 5.02 | Poor_Mixed | 5787.8 | 8921.6 | 1.521 | 0.759 | 6.16 | 0.777 | 5.58 | 0.368 | 0.7654 | 0.455 | 0.5442 | 1 | 0.3909 | 0.4925 | 0.5599 | 0.5599 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2021 | 1009.4 | 561.2 | 103.8 | 118.5 | 19.3 | 879.7 | 5950.4 | 46.3 | 32.6 | 90.2 | 88.2 | 82.5 | 97 | 40.2 | 25.9 | 5638.1 | 4703.2 | 5479.2 | 9204.1 | 7043.3 | 8238.3 | 1.632 | 1.498 | 1.504 | 0.731 | 0.705 | 0.661 | 5.39 | 5.5 | 4.47 | 0.614 | 0.672 | 0.649 | -5.51 | 3.95 | 4.22 | 0.665 | 0.673 | 0.616 | 2.98 | 3.32 | 3.76 | 0.691 | 0.618 | 0.626 | 5.03 | 5.27 | 4.71 | Poor_Mixed | 4703.2 | 7043.3 | 1.498 | 0.731 | 5.5 | 0.691 | 5.51 | 0.4014 | 0.7629 | 0.5336 | 0.5478 | 1 | 0.4843 | 0.5348 | 0.5967 | 0.5967 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2022 | 660 | 464.6 | 93.4 | 90.8 | 12.3 | 674.4 | 4542.8 | 50.7 | 29.6 | 90.7 | 91.9 | 80.7 | 96.4 | 40.2 | 24 | 6823.1 | 6283.6 | 6348 | 11380.1 | 10408.4 | 10678 | 1.668 | 1.656 | 1.682 | 0.684 | 0.679 | 0.726 | 4.61 | -4.79 | 5.12 | 0.643 | 0.656 | 0.686 | 3.75 | 4.16 | 4.33 | 0.616 | 0.586 | 0.648 | 3.63 | 3.8 | 3.84 | 0.594 | 0.661 | 0.661 | -4.18 | 4.17 | -4.03 | Poor_Mixed | 6283.6 | 10408.4 | 1.656 | 0.726 | 5.12 | 0.686 | 4.33 | 0.5638 | 0.8013 | 0.5204 | 0.6143 | 1 | 0.5022 | 0.5578 | 0.6506 | 0.6506 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2023 | 1582.4 | 912.3 | 137.4 | 180.5 | 32.8 | 1293.4 | 7897.3 | 31.6 | 49.4 | 103.2 | 104.6 | 92.9 | 115.5 | 43.6 | 31.3 | 1952.9 | 1252 | 2484.3 | 2241.8 | 1328.8 | 2950 | 1.148 | 1.061 | 1.187 | 0.904 | 0.905 | 0.929 | -8.45 | 9.54 | -9.22 | 0.687 | 0.895 | 0.861 | 8.45 | 7.02 | 8.56 | 0.765 | 0.859 | 0.824 | -7.77 | -7.6 | 6.72 | 0.725 | 0.754 | 0.737 | 7.66 | 6.53 | 8.36 | Very Poor_Mixed | 1252 | 1328.8 | 1.061 | 0.929 | 9.54 | 0.895 | 8.56 | 0.1005 | 0.5888 | 0.177 | 0.3483 | 1 | 0.1047 | 0.2589 | 0.3522 | 0.3522 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2024 | 925.6 | 562.7 | 107.2 | 120.4 | 19 | 885.1 | 5997.8 | 56.2 | 25 | 79.4 | 77.3 | 70.9 | 83.9 | 36.8 | 12.6 | 9441.7 | 7704.1 | 8580.6 | 18142.3 | 14007.1 | 15606.3 | 1.922 | 1.818 | 1.819 | 0.576 | 0.567 | 0.562 | -3.21 | 3.12 | 3.16 | 0.595 | 0.592 | 0.538 | 2.69 | 2.29 | -3.48 | 0.594 | 0.571 | 0.528 | -3.58 | 3.07 | 3.01 | 0.603 | 0.6 | 0.574 | -3.19 | -2.81 | 2.33 | Poor_DGA | 7704.1 | 14007.1 | 1.818 | 0.576 | 3.21 | 0.603 | 3.58 | 0.4041 | 0.87 | 0.8753 | 0.953 | 1 | 0.7477 | 0.7008 | 0.7314 | 0.7314 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2025 | 1597 | 906.8 | 144.4 | 197 | 34.3 | 1379 | 8125.6 | 35.6 | 47.1 | 107.8 | 106.4 | 92.9 | 115.2 | 45.2 | 32.4 | 1654.9 | 2368.5 | 1900 | 1869.2 | 2783.4 | 2085.9 | 1.129 | 1.175 | 1.098 | 0.927 | 0.934 | 0.971 | 8.52 | -8.96 | 8.66 | 0.849 | 0.807 | 0.765 | 7.64 | 5.72 | 6.8 | 0.938 | 0.877 | 0.864 | 6.45 | -8.24 | 7.62 | 0.798 | 0.728 | 0.748 | 7.42 | 5.71 | 5.8 | Very Poor_Mixed | 1654.9 | 1869.2 | 1.098 | 0.971 | 8.96 | 0.938 | 8.24 | 0.0623 | 0.61 | 0.1313 | 0.3059 | 1 | 0.1013 | 0.2562 | 0.3375 | 0.3375 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2026 | 995.8 | 506.2 | 111.2 | 115.8 | 17.2 | 909.6 | 5440.5 | 46.3 | 33.9 | 90.5 | 90.6 | 82.9 | 99.2 | 38.7 | 23.2 | 6080.2 | 6438.1 | 5862.9 | 9510.2 | 9816.4 | 9203.5 | 1.564 | 1.525 | 1.57 | 0.736 | 0.728 | 0.704 | 5.72 | -5.5 | 5.27 | 0.631 | 0.672 | 0.759 | -6.41 | 4.89 | 4.82 | 0.663 | 0.754 | 0.685 | 4.45 | -4.72 | 4.2 | 0.681 | 0.779 | 0.643 | 5.56 | 4.34 | 5.57 | Poor_Mixed | 5862.9 | 9203.5 | 1.525 | 0.736 | 5.72 | 0.779 | 6.41 | 0.4206 | 0.7473 | 0.5115 | 0.6416 | 1 | 0.4407 | 0.4486 | 0.5805 | 0.5805 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2027 | 375.5 | 245.4 | 81.7 | 76.9 | 1 | 565.9 | 4188.2 | 31.8 | 74.2 | 83.9 | 85.9 | 75.7 | 90.5 | 38.7 | 16.7 | 4760.6 | 5937.6 | 4610.9 | 6587.7 | 9067.7 | 7064.3 | 1.384 | 1.527 | 1.532 | 0.647 | 0.649 | 0.678 | 4.65 | 4.46 | 4.63 | 0.5 | 0.538 | 0.5 | 2.25 | 2 | 2 | 0.506 | 0.5 | 0.532 | 2.79 | 2.31 | 2.78 | 0.564 | 0.579 | 0.535 | 2.67 | 2 | 2.14 | Critical_Oil | 4610.9 | 6587.7 | 1.384 | 0.678 | 4.65 | 0.579 | 2.79 | 0.851 | 0.5833 | 0.6821 | 0.8465 | 1 | 0.5545 | 0.865 | 0.7866 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2028 | 904.3 | 563.3 | 106.6 | 120.8 | 16.3 | 775.2 | 5299 | 45.3 | 34.6 | 92.1 | 95 | 84.9 | 96.8 | 40.8 | 27.4 | 6415.2 | 5822.8 | 5364.4 | 10465 | 8990.2 | 8362.6 | 1.631 | 1.544 | 1.559 | 0.8 | 0.729 | 0.777 | -6.5 | 5.94 | -6.16 | 0.607 | 0.664 | 0.68 | 4.05 | -5.13 | -5.04 | 0.708 | 0.58 | 0.706 | 5.68 | 3.38 | 5.77 | 0.647 | 0.695 | 0.605 | 5.03 | 4.68 | 4.72 | Poor_Mixed | 5364.4 | 8362.6 | 1.544 | 0.8 | 6.5 | 0.708 | 5.77 | 0.4438 | 0.7391 | 0.4594 | 0.4938 | 1 | 0.3631 | 0.5071 | 0.5724 | 0.5724 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2029 | 1617.7 | 952.8 | 137.4 | 175.6 | 31.3 | 1236.4 | 7864.8 | 35.8 | 45.2 | 103.7 | 106.9 | 91.9 | 113.9 | 43.4 | 30.7 | 690 | 2748.3 | 1928.2 | 1200 | 3275.9 | 2186.8 | 1.739 | 1.192 | 1.134 | 0.888 | 0.917 | 0.954 | 8.42 | -9.11 | 9.5 | 0.737 | 0.647 | 0.774 | 6.05 | 5.9 | -6.13 | 0.691 | 0.765 | 0.732 | 5.32 | -7.83 | 5.43 | 0.806 | 0.734 | 0.787 | -7.56 | 7.65 | 7.68 | Very Poor_Mixed | 690 | 1200 | 1.134 | 0.954 | 9.5 | 0.806 | 7.83 | 0.111 | 0.628 | 0.1765 | 0.3711 | 1 | 0.1031 | 0.3408 | 0.3751 | 0.3751 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2030 | 407.3 | 197.2 | 77.8 | 141.6 | 36 | 514.7 | 3521.6 | 51 | 30.8 | 106.9 | 105.5 | 94 | 115 | 44.7 | 12.8 | 8764.1 | 8292.8 | 8746.9 | 16977.5 | 15187.2 | 15613.9 | 1.937 | 1.831 | 1.785 | 0.667 | 0.587 | 0.679 | 4.2 | -4.19 | -4.63 | 0.598 | 0.612 | 0.545 | 2.43 | 3.5 | -3.84 | 0.588 | 0.542 | 0.594 | 2.63 | -2.84 | -3.46 | 0.623 | 0.536 | 0.537 | 2.8 | 3.29 | -3.33 | Critical_Thermal | 8292.8 | 15187.2 | 1.785 | 0.679 | 4.63 | 0.623 | 3.84 | 0.4828 | 0.7855 | 0.1397 | 0.9484 | 1 | 0.5853 | 0.6981 | 0.644 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2031 | 235.4 | 169.8 | 72.8 | 56.2 | 3.5 | 443.3 | 2576.6 | 58.7 | 23.3 | 79.5 | 77.2 | 73 | 82.3 | 36 | 11.4 | 6446 | 5681.1 | 6617.5 | 11153.9 | 9197.9 | 10928.9 | 1.73 | 1.619 | 1.652 | 0.527 | 0.557 | 0.634 | 3.14 | 3.45 | 3.74 | 0.586 | 0.526 | 0.546 | 2.66 | 2.02 | -2.89 | 0.579 | 0.523 | 0.554 | 2 | 3.12 | -2.12 | 0.557 | 0.534 | 0.5 | 2.21 | 2.85 | 2.78 | Fair_IR_PI | 5681.1 | 9197.9 | 1.619 | 0.634 | 3.74 | 0.586 | 3.12 | 0.8394 | 0.9008 | 0.8679 | 0.9783 | 1 | 0.7313 | 0.7964 | 0.8594 | 0.8594 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2032 | 408 | 238.5 | 77 | 72 | 1.7 | 501.9 | 3471.3 | 56.9 | 23.8 | 83 | 80.7 | 75.7 | 89.8 | 36.5 | 16.1 | 478.9 | 7678.8 | 8811.1 | 738.3 | 13654.6 | 15801.6 | 1.542 | 1.778 | 1.793 | 0.99 | 0.926 | 0.925 | 9.49 | -8.99 | 8.62 | 0.5 | 0.5 | 0.51 | 2 | 2 | 2 | 0.523 | 0.538 | 0.5 | 2.33 | -3 | 2 | 0.511 | 0.5 | 0.5 | 2 | 2.98 | 2.36 | Critical_Winding_TD_Cap | 478.9 | 738.3 | 1.542 | 0.99 | 9.49 | 0.538 | 3 | 0.8175 | 0.8912 | 0.745 | 0.8635 | 0.85 | 0.0833 | 0.9304 | 0.7441 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_HV_TanDelta_pct
2033 | 866.9 | 479.6 | 103.3 | 117.9 | 13.6 | 843.8 | 5283.8 | 45.2 | 34 | 92.6 | 87.4 | 81.7 | 97.5 | 39.2 | 23 | 5538.4 | 5344.2 | 5625.1 | 8658.1 | 8379.5 | 8561.1 | 1.563 | 1.568 | 1.522 | 0.739 | 0.695 | 0.753 | -6.27 | 5.79 | 5.46 | 0.701 | 0.727 | 0.765 | -3.83 | 5.82 | -4.65 | 0.596 | 0.661 | 0.724 | 5.54 | -4.94 | -3.33 | 0.726 | 0.732 | 0.616 | -5.64 | 4.11 | 2.97 | Poor_Mixed | 5344.2 | 8379.5 | 1.522 | 0.753 | 6.27 | 0.765 | 5.82 | 0.4715 | 0.7461 | 0.5325 | 0.6484 | 1 | 0.4165 | 0.4704 | 0.5961 | 0.5961 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2034 | 1513.2 | 824.9 | 135.4 | 186.2 | 32.7 | 1231.9 | 7935.1 | 35.1 | 44.3 | 99.8 | 102.8 | 87.1 | 111.2 | 42.8 | 32.9 | 1699.1 | 1363.7 | 2250 | 2222.7 | 1618 | 2878.4 | 1.308 | 1.186 | 1.279 | 0.897 | 0.849 | 0.885 | 8.35 | 7.77 | -7.47 | 0.914 | 0.815 | 0.754 | 7.31 | 6.36 | 7.59 | 0.801 | 0.749 | 0.799 | -6.99 | 5.38 | 7.81 | 0.873 | 0.741 | 0.755 | 5.61 | 4.92 | 5.14 | Very Poor_Mixed | 1363.7 | 1618 | 1.186 | 0.897 | 8.35 | 0.914 | 7.81 | 0.1186 | 0.6367 | 0.2674 | 0.2865 | 1 | 0.1915 | 0.2903 | 0.3862 | 0.3862 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2035 | 203.3 | 170.6 | 69.5 | 60.7 | 1 | 448.7 | 2500 | 58.5 | 20.8 | 77.8 | 78.5 | 75.5 | 86.2 | 36.1 | 11.3 | 9346.2 | 8680 | 9334 | 18692.5 | 16610.3 | 18395.1 | 2 | 1.914 | 1.971 | 0.503 | 0.571 | 0.589 | -2.2 | -2.23 | 2.7 | 0.5 | 0.617 | 0.546 | 2.3 | -4.39 | -2.55 | 0.537 | 0.5 | 0.541 | -3.03 | -2.44 | -2.19 | 0.557 | 0.548 | 0.508 | 2.2 | 2.7 | 2 | Fair_Bushing_TD_Cap | 8680 | 16610.3 | 1.914 | 0.589 | 2.7 | 0.617 | 4.39 | 0.9352 | 0.9605 | 0.8311 | 0.9802 | 1 | 0.8391 | 0.8159 | 0.9055 | 0.9055 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
2036 | 1763.1 | 934.5 | 146.8 | 194.1 | 33.4 | 1379 | 9070.4 | 56.4 | 24.9 | 82.3 | 81.4 | 73.9 | 86.8 | 36.4 | 19 | 8804.4 | 9312.3 | 7857 | 15810.8 | 18468.5 | 14459 | 1.796 | 1.983 | 1.84 | 0.594 | 0.575 | 0.572 | 2.53 | 3.21 | 3.59 | 0.521 | 1.218 | 0.558 | 2.8 | 2.51 | 2.16 | 0.546 | 0.6 | 0.5 | -2 | 3.03 | 2 | 0.529 | 0.509 | 0.514 | 3.3 | 3.38 | -2.07 | Critical_DGA | 7857 | 14459 | 1.796 | 0.594 | 3.59 | 1.218 | 3.38 | 0.0392 | 0.8717 | 0.774 | 0.778 | 1 | 0.7358 | 0.7625 | 0.631 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
2037 | 926.7 | 486.5 | 100.5 | 115.4 | 22.3 | 863.2 | 5391.7 | 54.7 | 22.8 | 77.5 | 80.2 | 70.8 | 82.7 | 36.1 | 12.2 | 8903.3 | 9709.6 | 9251.5 | 16964.1 | 19280.4 | 18503 | 1.905 | 1.986 | 2 | 0.5 | 0.521 | 0.534 | 2 | 2.21 | 3.05 | 0.513 | 0.635 | 0.557 | 2.33 | 3.46 | 2.86 | 0.544 | 0.515 | 0.562 | 2.76 | 2.79 | 2.63 | 0.543 | 0.506 | 0.541 | 3.12 | -2.6 | 2.46 | Fair_DGA | 8903.3 | 16964.1 | 1.905 | 0.534 | 3.05 | 0.635 | 3.46 | 0.4125 | 0.9108 | 0.8768 | 0.9618 | 1 | 0.9032 | 0.7792 | 0.7749 | 0.7749 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2038 | 362.3 | 300.5 | 82.4 | 78 | 46.9 | 524.9 | 3613 | 53.3 | 27 | 77.4 | 75.9 | 72.2 | 81.1 | 35.3 | 17.6 | 731.3 | 757.7 | 2118.5 | 804.8 | 793.3 | 2381 | 1.101 | 1.047 | 1.124 | 0.699 | 0.685 | 0.667 | -5.04 | 6 | 5.04 | 0.617 | 0.637 | 0.647 | 3.99 | -4.4 | 4.38 | 0.558 | 0.64 | 0.642 | 3.69 | 3.66 | -3.92 | 0.639 | 0.574 | 0.639 | 3.31 | 3.87 | 4.52 | Critical_IR_PI | 731.3 | 793.3 | 1.047 | 0.699 | 6 | 0.647 | 4.52 | 0.5346 | 0.8382 | 0.9193 | 0.8203 | 0.85 | 0.4846 | 0.5842 | 0.6762 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2039 | 323.6 | 148.6 | 72.7 | 65.9 | 3.5 | 441.8 | 3063.9 | 60 | 21.3 | 77.2 | 75.1 | 72.2 | 81.4 | 35.7 | 12.2 | 9903.1 | 10000 | 9524.5 | 19133.3 | 20000 | 19048.9 | 1.932 | 2 | 2 | 0.558 | 0.54 | 0.531 | 2.83 | 2.35 | 2.63 | 0.517 | 0.537 | 0.54 | 3.32 | -3.15 | 2.2 | 0.513 | 0.699 | 0.527 | 2.08 | -4.62 | 2.09 | 0.5 | 0.516 | 0.505 | 2.1 | -2.79 | 3.01 | Fair_Bushing_TD_Cap | 9524.5 | 19048.9 | 1.932 | 0.558 | 2.83 | 0.699 | 4.62 | 0.8164 | 0.9458 | 0.9313 | 0.9618 | 1 | 0.8268 | 0.8144 | 0.8812 | 0.8812 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2040 | 709 | 403.4 | 96 | 100.9 | 10.9 | 705.7 | 4665.3 | 49.8 | 29.6 | 86.5 | 87 | 77.8 | 93 | 38.2 | 21.8 | 6983.6 | 5978.7 | 6321.7 | 11672.9 | 9488.4 | 10085.6 | 1.671 | 1.587 | 1.595 | 0.684 | 0.663 | 0.671 | -5.53 | 3.64 | 4.22 | 0.653 | 0.565 | 0.599 | 4.22 | -3.02 | 4.17 | 0.63 | 0.64 | 0.523 | 3.91 | 4.51 | -4.81 | 0.622 | 0.702 | 0.618 | 4.65 | -3.12 | 5.12 | Poor_Mixed | 5978.7 | 9488.4 | 1.587 | 0.684 | 5.53 | 0.702 | 5.12 | 0.56 | 0.8013 | 0.6307 | 0.6885 | 1 | 0.5475 | 0.5893 | 0.6764 | 0.6764 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2041 | 1760.3 | 961.2 | 146.5 | 197 | 34.3 | 1379 | 8358.5 | 52.2 | 50.8 | 79.4 | 80.7 | 71.9 | 84.3 | 36.1 | 12.2 | 9589.4 | 8400.9 | 8455.8 | 18100.6 | 15274.5 | 14929.7 | 1.888 | 1.818 | 1.766 | 0.611 | 0.611 | 0.616 | -4.71 | -4.46 | 4.81 | 0.586 | 0.549 | 0.522 | 2.42 | 2.31 | 2.34 | 0.5 | 0.536 | 0.567 | -2.57 | -2.74 | 2.15 | 0.556 | 0.521 | 0.537 | 2 | 2.85 | -2 | Critical_DGA | 8400.9 | 14929.7 | 1.766 | 0.616 | 4.81 | 0.586 | 2.85 | 0.0401 | 0.5833 | 0.8353 | 0.9618 | 1 | 0.5989 | 0.8111 | 0.6015 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
2042 | 1142 | 562.5 | 114.2 | 137.6 | 20.1 | 908.7 | 6135.5 | 57.2 | 23.8 | 82.8 | 80.3 | 76 | 86.2 | 37 | 11.3 | 9611.2 | 8594.2 | 8797.7 | 19222.4 | 15764.3 | 16576.7 | 2 | 1.834 | 1.884 | 0.524 | 0.588 | 0.538 | -2.33 | 3.07 | 2.74 | 0.531 | 0.598 | 0.513 | -3.02 | 2.81 | 2 | 0.569 | 0.5 | 0.529 | -2.3 | 2.4 | 2 | 0.551 | 0.519 | 0.571 | -2 | 2.32 | -2 | Poor_DGA | 8594.2 | 15764.3 | 1.834 | 0.588 | 3.07 | 0.598 | 3.02 | 0.3553 | 0.8912 | 0.7631 | 0.9802 | 1 | 0.8114 | 0.8172 | 0.7418 | 0.7418 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2043 | 857.8 | 442.1 | 91.9 | 113 | 15.2 | 786.6 | 4578 | 48.1 | 30.7 | 88.2 | 92.9 | 80.5 | 96.7 | 38.7 | 23.1 | 6761.2 | 5498 | 5428.7 | 11036.9 | 8582.9 | 8140.2 | 1.632 | 1.561 | 1.499 | 0.638 | 0.689 | 0.668 | -4.21 | -4.21 | 4.75 | 0.681 | 0.69 | 0.708 | 4.92 | -3.84 | 3.68 | 0.653 | 0.552 | 0.705 | -3.94 | -3.76 | -5.27 | 0.671 | 0.593 | 0.627 | 4.39 | 3.72 | -4.51 | Poor_Mixed | 5428.7 | 8140.2 | 1.499 | 0.689 | 4.75 | 0.708 | 5.27 | 0.4921 | 0.7868 | 0.54 | 0.645 | 1 | 0.5589 | 0.5334 | 0.6379 | 0.6379 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2044 | 434.2 | 290.6 | 88.3 | 91.4 | 8.5 | 625.1 | 3982.2 | 56.1 | 26.6 | 84.5 | 82.3 | 77 | 89.8 | 38.2 | 18.4 | 8440.5 | 8072.5 | 8263.8 | 15415.8 | 14015.6 | 15230.4 | 1.826 | 1.736 | 1.843 | 0.689 | 0.642 | 0.641 | 5.52 | 3.7 | -5.48 | 0.56 | 0.531 | 0.5 | 2.91 | -3.55 | 3.23 | 0.614 | 0.538 | 0.639 | -3.6 | 3.35 | 3.29 | 0.576 | 0.579 | 0.549 | 3.29 | -3.64 | 3.55 | Fair_Mixed | 8072.5 | 14015.6 | 1.736 | 0.689 | 5.52 | 0.639 | 3.64 | 0.6504 | 0.8443 | 0.7017 | 0.7963 | 1 | 0.5381 | 0.7163 | 0.7382 | 0.7382 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2045 | 1196.4 | 746.5 | 121.2 | 143.7 | 29.2 | 986.4 | 6420.6 | 57 | 21.2 | 77.6 | 77 | 73.9 | 86.8 | 36.1 | 13.1 | 9303.1 | 9238.8 | 10000 | 17452.2 | 18104.4 | 19836.4 | 1.876 | 1.96 | 1.984 | 0.565 | 0.568 | 0.542 | 3.02 | 3.49 | 2.43 | 0.565 | 0.601 | 0.601 | 3.22 | 3.3 | 3.04 | 0.599 | 0.587 | 0.52 | 3.42 | -2.99 | 3.3 | 0.569 | 0.572 | 0.556 | -3.19 | 2.78 | 2.7 | Poor_DGA | 9238.8 | 17452.2 | 1.876 | 0.568 | 3.49 | 0.601 | 3.42 | 0.2602 | 0.9486 | 0.8578 | 0.9414 | 1 | 0.7763 | 0.6976 | 0.706 | 0.706 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2046 | 190.4 | 197.4 | 71.9 | 57.7 | 3.5 | 472.2 | 3077.1 | 59.1 | 20.4 | 78.5 | 75 | 72.6 | 86.1 | 35.4 | 14.8 | 5957.7 | 4890.7 | 5041.7 | 9256.8 | 7167.8 | 7345.1 | 1.554 | 1.466 | 1.457 | 0.536 | 0.66 | 0.575 | 2.51 | -4.44 | 3.94 | 0.523 | 0.581 | 0.554 | 3.1 | 2.35 | 2 | 0.518 | 0.545 | 0.531 | 3.24 | 3.24 | 3.18 | 0.562 | 0.54 | 0.53 | 2.06 | 2.19 | 2 | Poor_IR_PI | 4890.7 | 7167.8 | 1.457 | 0.66 | 4.44 | 0.581 | 3.24 | 0.8315 | 0.9748 | 0.8955 | 0.8988 | 1 | 0.6981 | 0.7895 | 0.8592 | 0.8592 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2047 | 769.7 | 387.2 | 92 | 100.1 | 9.7 | 659.4 | 5035.1 | 50.4 | 28.1 | 87.2 | 85.4 | 78.6 | 91.8 | 39.4 | 19.9 | 6477.3 | 7327.3 | 7440.2 | 10670 | 12333.3 | 13412.7 | 1.647 | 1.683 | 1.803 | 0.657 | 0.662 | 0.724 | 4.71 | 4.16 | 5.47 | 0.631 | 0.656 | 0.519 | 3.77 | -4.39 | 3.64 | 0.593 | 0.607 | 0.647 | 3.38 | 3.94 | 3.7 | 0.625 | 0.596 | 0.608 | 3.8 | -3.03 | 3.42 | Fair_Mixed | 6477.3 | 10670 | 1.647 | 0.724 | 5.47 | 0.656 | 4.39 | 0.5735 | 0.8221 | 0.6304 | 0.7499 | 1 | 0.5212 | 0.6184 | 0.6869 | 0.6869 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2048 | 1665.4 | 907.1 | 137.8 | 192.2 | 34.3 | 1301.2 | 8368.8 | 36.2 | 44.7 | 103.2 | 108.3 | 92.1 | 112 | 43.8 | 34.1 | 1492.4 | 1201.6 | 690 | 1567 | 1261.6 | 1200 | 1.05 | 1.05 | 1.739 | 0.976 | 0.936 | 0.99 | 9.64 | 9.01 | 8.7 | 0.741 | 0.775 | 0.923 | 7.24 | -9.84 | 5.93 | 0.944 | 0.749 | 0.91 | 8.43 | 6.43 | 8.8 | 0.917 | 0.909 | 0.781 | 5.83 | 7.64 | 8.82 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.99 | 9.64 | 0.944 | 9.84 | 0.0718 | 0.6328 | 0.1772 | 0.2395 | 1 | 0.0655 | 0.2022 | 0.3291 | 0.3291 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2049 | 1555.1 | 923.4 | 140.8 | 180.8 | 31.7 | 1263 | 7864 | 33.1 | 45.1 | 108.2 | 109.3 | 96.1 | 118.4 | 43.8 | 31.6 | 1358.2 | 2693.9 | 1604 | 1595.3 | 3134.2 | 1742.1 | 1.175 | 1.163 | 1.086 | 0.942 | 0.934 | 0.957 | -8.23 | -8.6 | 8.89 | 0.865 | 0.786 | 0.915 | 8.73 | 7.38 | -7.44 | 0.938 | 0.86 | 0.712 | 8.93 | 8.53 | 7.25 | 0.776 | 0.837 | 0.898 | -7.36 | 8.24 | 5.59 | Very Poor_Mixed | 1358.2 | 1595.3 | 1.086 | 0.957 | 8.89 | 0.938 | 8.93 | 0.107 | 0.6289 | 0.0898 | 0.3368 | 1 | 0.1081 | 0.2054 | 0.3401 | 0.3401 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
2050 | 957.1 | 578.6 | 103.5 | 121.2 | 17 | 878.1 | 5490.1 | 45.5 | 34.1 | 91.5 | 93.9 | 85.6 | 101 | 40 | 26.1 | 5279.2 | 6183.3 | 5902.5 | 7778.5 | 9730.3 | 9252.3 | 1.473 | 1.574 | 1.568 | 0.786 | 0.728 | 0.779 | 6.29 | -6.16 | 6.05 | 0.639 | 0.621 | 0.625 | 6.15 | 5.49 | 5.27 | 0.672 | 0.666 | 0.7 | 4.44 | 4.44 | 3.54 | 0.672 | 0.646 | 0.634 | 4.43 | 4.88 | -3.97 | Poor_Mixed | 5279.2 | 7778.5 | 1.473 | 0.786 | 6.29 | 0.7 | 6.15 | 0.4205 | 0.7449 | 0.45 | 0.5407 | 1 | 0.3683 | 0.5102 | 0.5699 | 0.5699 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2051 | 911.7 | 535.7 | 102.6 | 125 | 19.2 | 889.3 | 5775.1 | 49.2 | 30.7 | 92.5 | 90.6 | 83.4 | 96.7 | 40.5 | 24.2 | 5333.6 | 6181 | 5858.8 | 8471.5 | 10137.1 | 8906.1 | 1.588 | 1.64 | 1.52 | 0.773 | 0.759 | 0.741 | -5.88 | 5.86 | 6.11 | 0.625 | 0.716 | 0.648 | 3.92 | 4.02 | 5.58 | 0.628 | 0.672 | 0.697 | 3.93 | 4.48 | -3.62 | 0.73 | 0.622 | 0.686 | -3.66 | -4.23 | 5.5 | Poor_Mixed | 5333.6 | 8471.5 | 1.52 | 0.773 | 6.11 | 0.73 | 5.58 | 0.4078 | 0.7868 | 0.4965 | 0.6074 | 1 | 0.3854 | 0.5056 | 0.5814 | 0.5814 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2052 | 170.5 | 263.2 | 76.4 | 75.2 | 1.2 | 516.3 | 3500 | 55.9 | 22.7 | 80.2 | 82.6 | 74.1 | 84.6 | 35.8 | 12.3 | 9434.5 | 8868.9 | 8966.3 | 18540.9 | 16766 | 17669.1 | 1.965 | 1.89 | 1.971 | 0.819 | 0.87 | 0.863 | 7.1 | -7.37 | 7.7 | 0.563 | 0.591 | 0.552 | -3.5 | -3.47 | -3.28 | 0.631 | 0.63 | 0.604 | 3.35 | 2.97 | 2.61 | 0.579 | 0.554 | 0.608 | 2.72 | 4.07 | 3.2 | Poor_Winding_TD_Cap | 8868.9 | 16766 | 1.89 | 0.87 | 7.7 | 0.631 | 4.07 | 0.8558 | 0.9129 | 0.794 | 0.9597 | 1 | 0.2354 | 0.6637 | 0.7633 | 0.7633 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
2053 | 160.7 | 120 | 65 | 50 | 1 | 380.4 | 2500 | 57 | 23.6 | 76.5 | 77.2 | 70.7 | 81.5 | 35.2 | 12.9 | 6588.9 | 7645.3 | 7558.8 | 11038.2 | 13495.3 | 12625.9 | 1.675 | 1.765 | 1.67 | 0.584 | 0.552 | 0.591 | 3.62 | -2.66 | 3.12 | 0.53 | 0.52 | 0.536 | 2.64 | 2.32 | 2.8 | 0.544 | 0.568 | 0.518 | 3.41 | 2 | 2.33 | 0.5 | 0.515 | 0.533 | 2 | 2 | -2.06 | Fair_IR_PI | 6588.9 | 11038.2 | 1.67 | 0.591 | 3.62 | 0.568 | 3.41 | 0.9835 | 0.895 | 0.9271 | 0.9461 | 1 | 0.7411 | 0.8405 | 0.9083 | 0.9083 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2054 | 278.9 | 207.4 | 75.9 | 55.5 | 1 | 443.3 | 3096.1 | 60 | 20 | 75.5 | 78.4 | 70 | 84.4 | 35.1 | 10 | 8911 | 9474.3 | 9568.4 | 16560.5 | 18804.8 | 18902.8 | 1.858 | 1.985 | 1.976 | 0.517 | 0.552 | 0.543 | 2.73 | 3.31 | 2.31 | 0.5 | 0.5 | 0.519 | 2.64 | 2.43 | 2.96 | 0.52 | 0.528 | 0.541 | -2.76 | 2.27 | 2.24 | 0.584 | 0.543 | 0.527 | 2.17 | 2.94 | 2 | Fair_Winding_TD_Cap | 8911 | 16560.5 | 1.858 | 0.552 | 3.31 | 0.584 | 2.96 | 0.9263 | 1 | 0.9239 | 1 | 1 | 0.8264 | 0.8427 | 0.9214 | 0.9214 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_LV_TanDelta_pct
2055 | 361.6 | 182.6 | 70.5 | 63.9 | 1.8 | 397.9 | 2923.7 | 58.2 | 21.5 | 76.7 | 79.1 | 75.1 | 81.7 | 35 | 11.9 | 10000 | 9385.3 | 8553.6 | 20000 | 17915.9 | 15921.8 | 2 | 1.909 | 1.861 | 0.5 | 0.549 | 0.515 | 2.42 | 2.7 | 2.81 | 0.524 | 0.504 | 0.529 | 2.62 | 2.81 | 2.43 | 0.5 | 0.501 | 0.524 | 3 | 2.07 | 2.34 | 0.515 | 0.525 | 0.554 | 2.37 | 3.05 | 2 | Good_Mixed | 8553.6 | 15921.8 | 1.861 | 0.549 | 2.81 | 0.554 | 3.05 | 0.8612 | 0.9406 | 0.8671 | 0.9682 | 1 | 0.8797 | 0.8653 | 0.9022 | 0.9022 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2056 | 508.9 | 289 | 85 | 80.7 | 1 | 519.6 | 3958.5 | 52.1 | 29.2 | 79.6 | 78.9 | 73.4 | 84.5 | 35.5 | 13.8 | 1407.4 | 690 | 690 | 1565.4 | 705.4 | 703.8 | 1.112 | 1.022 | 1.02 | 0.686 | 0.695 | 0.741 | 4.66 | 5.77 | 24.19 | 0.507 | 0.561 | 0.5 | 2.57 | -2.05 | 2.73 | 0.587 | 0.569 | 0.541 | 2.44 | -3.29 | 2.44 | 0.571 | 0.568 | 0.563 | 2.71 | -2.07 | -2.34 | Critical_IR_PI | 690 | 703.8 | 1.02 | 0.741 | 24.19 | 0.587 | 3.29 | 0.8361 | 0.8067 | 0.838 | 0.9244 | 0.85 | 0.3875 | 0.7831 | 0.7671 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
2057 | 458.4 | 347.7 | 86.1 | 78.7 | 1.8 | 614.2 | 4244.3 | 16.7 | 47.9 | 82 | 82.3 | 76.5 | 86.3 | 36.9 | 14.2 | 5085.6 | 3870.4 | 4881.2 | 7600.2 | 5482.8 | 7223.4 | 1.494 | 1.417 | 1.48 | 0.671 | 0.654 | 0.657 | -3.93 | -4.04 | -4.2 | 0.603 | 0.58 | 0.531 | 2.49 | 3.63 | 3.08 | 0.592 | 0.604 | 0.578 | -2.82 | -2.89 | 2.96 | 0.55 | 0.539 | 0.613 | 3.13 | 3.01 | 3.22 | Critical_Oil | 3870.4 | 5482.8 | 1.417 | 0.671 | 4.2 | 0.613 | 3.63 | 0.7599 | 0.0192 | 0.7494 | 0.9144 | 1 | 0.5827 | 0.6977 | 0.6801 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2058 | 1397.6 | 785 | 129.3 | 163.7 | 45.1 | 1191.9 | 7453.6 | 34.4 | 45.2 | 102.6 | 101.7 | 91.8 | 114.1 | 43.5 | 35.8 | 1416.7 | 1578 | 2177.7 | 1614.2 | 1918.8 | 2468.5 | 1.139 | 1.216 | 1.134 | 0.886 | 0.907 | 0.902 | 8.1 | -8.27 | 9.08 | 0.712 | 0.893 | 0.89 | 5.14 | 5.82 | 8.34 | 0.707 | 0.834 | 0.775 | 7.51 | -5.64 | 6.19 | 0.783 | 0.764 | 0.907 | -5.5 | 7.5 | -5.56 | Critical_Mixed | 1416.7 | 1614.2 | 1.134 | 0.907 | 9.08 | 0.907 | 8.34 | 0.1556 | 0.628 | 0.2107 | 0.1718 | 1 | 0.1444 | 0.2847 | 0.3754 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2059 | 1611.4 | 943 | 140.4 | 186.3 | 34.3 | 1353.3 | 8659.1 | 35.5 | 43.9 | 105.9 | 107.4 | 93.3 | 115.8 | 44.2 | 30.7 | 1561.4 | 2164.5 | 1386.4 | 1922.6 | 2301.4 | 1688.1 | 1.231 | 1.063 | 1.218 | 0.955 | 0.934 | 0.94 | 9.15 | -8.88 | 8.48 | 0.699 | 0.759 | 0.954 | 6 | 8.26 | -6.12 | 0.723 | 0.8 | 0.804 | 7.82 | 4.6 | 7.2 | 0.917 | 0.868 | 0.749 | 7.14 | 6.06 | 6.21 | Very Poor_Mixed | 1386.4 | 1688.1 | 1.063 | 0.955 | 9.15 | 0.954 | 8.26 | 0.065 | 0.6406 | 0.1384 | 0.3711 | 1 | 0.0956 | 0.2765 | 0.3487 | 0.3487 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2060 | 110.9 | 120 | 66.6 | 60.3 | 3.1 | 350 | 2810.4 | 56.3 | 22.6 | 79 | 80.7 | 71.3 | 84.6 | 35 | 11.9 | 1241.2 | 1784.1 | 1095.8 | 1272.9 | 2015.4 | 945.2 | 1.026 | 1.13 | 0.863 | 0.78 | 0.737 | 0.729 | 5.83 | 5.94 | -5.59 | 0.586 | 0.623 | 0.562 | 3.97 | 3.62 | 3.85 | 0.635 | 0.623 | 0.562 | 4.72 | 3.63 | -3.09 | 0.597 | 0.579 | 0.598 | 4.06 | 3.99 | 2.81 | Critical_IR_PI | 1095.8 | 945.2 | 0.863 | 0.78 | 5.94 | 0.635 | 4.72 | 0.8835 | 0.915 | 0.8475 | 0.9682 | 0.7375 | 0.4022 | 0.6316 | 0.7518 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_TV
2061 | 1443.9 | 804.3 | 135.9 | 178.2 | 34.3 | 1221.1 | 8089.3 | 35.4 | 44.5 | 102.9 | 102.4 | 91.3 | 113.1 | 43.9 | 32.2 | 2033.9 | 2391.2 | 2741.9 | 2215.2 | 2861.9 | 3364.3 | 1.089 | 1.197 | 1.227 | 0.905 | 0.921 | 0.86 | 7.99 | 8.65 | 8.1 | 0.717 | 0.804 | 0.833 | -6.3 | 5.5 | 5.88 | 0.803 | 0.804 | 0.885 | 6.01 | 7.44 | 6.94 | 0.777 | 0.866 | 0.831 | 6.89 | -5.2 | 6.63 | Very Poor_Mixed | 2033.9 | 2215.2 | 1.089 | 0.921 | 8.65 | 0.885 | 7.44 | 0.1243 | 0.6347 | 0.21 | 0.3137 | 1 | 0.1588 | 0.2777 | 0.3761 | 0.3761 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2062 | 691.7 | 456.4 | 97.3 | 98.3 | 16.4 | 713.7 | 4835.1 | 51.5 | 30.6 | 86.2 | 85.8 | 77.3 | 92.2 | 38.6 | 21 | 7108.9 | 6997.2 | 7067.3 | 11876.6 | 12421.6 | 11779.4 | 1.671 | 1.775 | 1.667 | 0.604 | 0.671 | 0.644 | 3.72 | 3.9 | 4.97 | 0.628 | 0.632 | 0.554 | 3.29 | 3.71 | 4.24 | 0.628 | 0.601 | 0.602 | -4.13 | 3.62 | 3.73 | 0.596 | 0.574 | 0.592 | 5.09 | 3.95 | 3.25 | Poor_Mixed | 6997.2 | 11779.4 | 1.667 | 0.671 | 4.97 | 0.632 | 5.09 | 0.5141 | 0.7881 | 0.6465 | 0.7147 | 1 | 0.5978 | 0.6182 | 0.6785 | 0.6785 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2063 | 540.3 | 375.5 | 87.2 | 87.4 | 11.8 | 578.2 | 4478.3 | 50 | 29.5 | 88.6 | 90.1 | 78.9 | 93.7 | 39.3 | 21.5 | 6560.3 | 5944.2 | 6493.8 | 10919.6 | 9870.4 | 10612.4 | 1.664 | 1.661 | 1.634 | 0.644 | 0.628 | 0.667 | 4.45 | 4.61 | 4.53 | 0.707 | 0.612 | 0.671 | 3.88 | 5.07 | 3.6 | 0.594 | 0.669 | 0.631 | 3.91 | 4.28 | 3.09 | 0.691 | 0.594 | 0.599 | 4.37 | 3.14 | 4.08 | Fair_Mixed | 5944.2 | 9870.4 | 1.634 | 0.667 | 4.61 | 0.707 | 5.07 | 0.6099 | 0.8027 | 0.5774 | 0.6984 | 1 | 0.5696 | 0.5593 | 0.6819 | 0.6819 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2064 | 1617.5 | 834.7 | 131.9 | 186.7 | 34.3 | 1270.4 | 8221 | 34.4 | 44.3 | 101.1 | 106.3 | 92.5 | 115.1 | 45.2 | 31.9 | 1581 | 1728.9 | 2026.9 | 1883.1 | 2089.3 | 2391.8 | 1.191 | 1.208 | 1.18 | 0.935 | 0.905 | 0.924 | 8.65 | 8.73 | 8.07 | 0.767 | 0.891 | 0.86 | -8.34 | -9.34 | 8.67 | 0.924 | 0.708 | 0.876 | 8.73 | 7.21 | 7.41 | 0.892 | 0.745 | 0.842 | 7.08 | 6.59 | 6.79 | Very Poor_Mixed | 1581 | 1883.1 | 1.18 | 0.935 | 8.73 | 0.924 | 9.34 | 0.0975 | 0.6367 | 0.1721 | 0.3252 | 1 | 0.1284 | 0.2115 | 0.3503 | 0.3503 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2065 | 478.7 | 383.5 | 87.8 | 90 | 11.2 | 568.4 | 3772.8 | 52.7 | 26.8 | 82.7 | 82.2 | 74.5 | 88.7 | 37.5 | 17.6 | 7700.8 | 6759.8 | 7194.5 | 12419 | 10480.9 | 12759.7 | 1.613 | 1.55 | 1.774 | 0.705 | 0.678 | 0.691 | -5.11 | 4.02 | 4.29 | 0.575 | 0.576 | 0.565 | 4.02 | 4.25 | 4.49 | 0.632 | 0.577 | 0.666 | 5.01 | -3.28 | -4.05 | 0.592 | 0.591 | 0.578 | 3.56 | 3.59 | 4.01 | Fair_Mixed | 6759.8 | 10480.9 | 1.55 | 0.705 | 5.11 | 0.666 | 5.01 | 0.6232 | 0.8412 | 0.7443 | 0.8203 | 1 | 0.5283 | 0.6233 | 0.7184 | 0.7184 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2066 | 232.7 | 163.5 | 70.3 | 61.5 | 1 | 441.5 | 2655.4 | 58.7 | 22 | 76 | 77.2 | 71.4 | 84.1 | 35.7 | 13.6 | 9238.6 | 10000 | 9888.4 | 16766.4 | 20000 | 18531.5 | 1.815 | 2 | 1.874 | 0.522 | 0.526 | 0.579 | 2.56 | -2 | 2.59 | 0.555 | 0.531 | 0.5 | 3.54 | 2.04 | 3.16 | 0.512 | 0.745 | 0.509 | 2.83 | 5.04 | 2.61 | 0.537 | 0.513 | 0.509 | 3.53 | -2.6 | -2.57 | Poor_Bushing_TD_Cap | 9238.6 | 16766.4 | 1.815 | 0.579 | 2.59 | 0.745 | 5.04 | 0.9322 | 0.9283 | 0.911 | 0.9294 | 1 | 0.8503 | 0.7927 | 0.9037 | 0.9037 | Good | 1 | 0 | No_Anomaly | 0 |  | Bushing_LV_Y_TanDelta_pct
2067 | 284.5 | 155.5 | 66.5 | 64.1 | 3.6 | 399.1 | 2549.6 | 53.2 | 26.5 | 75 | 75 | 72.9 | 82.5 | 36.5 | 11.5 | 5301.1 | 4338.7 | 5093.8 | 7584.8 | 6435 | 7510.3 | 1.431 | 1.483 | 1.474 | 0.66 | 0.662 | 0.582 | 4.53 | 4.44 | 3.82 | 0.546 | 0.585 | 0.627 | 2.88 | 2.89 | -3.59 | 0.548 | 0.5 | 0.521 | 3.54 | 2.98 | 2.52 | 0.552 | 0.576 | 0.575 | -3.72 | 3 | 3.21 | Poor_IR_PI | 4338.7 | 6435 | 1.431 | 0.662 | 4.53 | 0.627 | 3.72 | 0.8335 | 0.8458 | 0.9503 | 0.9764 | 1 | 0.6002 | 0.7378 | 0.8306 | 0.8306 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2068 | 872.2 | 584.5 | 104.8 | 119.7 | 19.3 | 826.2 | 5194.1 | 47.8 | 33.2 | 90.3 | 89.6 | 81.5 | 97.7 | 38.8 | 23.8 | 5901.4 | 5702.3 | 6285.5 | 9495.5 | 8920 | 10157.6 | 1.609 | 1.564 | 1.616 | 0.705 | 0.674 | 0.691 | 5.38 | 4.96 | 4.78 | 0.735 | 0.689 | 0.577 | -5.81 | -4.39 | 5.09 | 0.716 | 0.66 | 0.642 | 4.42 | 3.4 | -5.04 | 0.673 | 0.666 | 0.693 | 4.15 | 3.39 | 5.16 | Poor_Mixed | 5702.3 | 8920 | 1.564 | 0.705 | 5.38 | 0.735 | 5.81 | 0.4222 | 0.7556 | 0.5352 | 0.6212 | 1 | 0.4965 | 0.4951 | 0.5994 | 0.5994 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2069 | 199.4 | 120 | 69.2 | 50 | 1 | 380.2 | 2500 | 59.2 | 21.2 | 75 | 75 | 70 | 80 | 35 | 12 | 9821.1 | 9770.2 | 9125.3 | 19552.1 | 19540.4 | 18240 | 1.991 | 2 | 1.999 | 0.512 | 0.5 | 0.518 | 2.07 | 2 | 2.32 | 0.527 | 0.5 | 0.562 | 2 | 2.06 | -2.11 | 0.505 | 0.5 | 0.516 | 2.26 | 2.53 | 2.39 | 0.5 | 0.525 | 0.508 | 2.41 | -2.23 | 2.38 | Good_Mixed | 9125.3 | 18240 | 1.991 | 0.518 | 2.32 | 0.562 | 2.53 | 0.9774 | 0.9486 | 1 | 0.9661 | 1 | 0.9439 | 0.9002 | 0.9607 | 0.9607 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2070 | 953.8 | 527.8 | 103.9 | 118.3 | 19.4 | 833.1 | 5378.6 | 46.5 | 33 | 90.6 | 90.2 | 82.3 | 98.8 | 38.3 | 21 | 5458.7 | 6331.4 | 4962 | 8455.1 | 10018.3 | 7967.2 | 1.549 | 1.582 | 1.606 | 0.726 | 0.672 | 0.76 | 6.58 | 5.4 | 5.67 | 0.656 | 0.649 | 0.632 | 3.75 | 4.59 | 3.96 | 0.661 | 0.703 | 0.636 | 6.25 | -3.86 | -4.69 | 0.67 | 0.643 | 0.664 | 3.66 | 3.89 | 3.85 | Poor_Mixed | 4962 | 7967.2 | 1.549 | 0.76 | 6.58 | 0.703 | 6.25 | 0.4208 | 0.7581 | 0.5216 | 0.7147 | 1 | 0.4234 | 0.5215 | 0.5972 | 0.5972 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2071 | 1424.5 | 822.7 | 139.8 | 171.6 | 34.3 | 1240.4 | 7593.6 | 33.7 | 47 | 102.7 | 101.3 | 91.1 | 112 | 44.5 | 32 | 2138 | 2544.5 | 2820.4 | 2479.2 | 2871 | 3611.7 | 1.16 | 1.128 | 1.281 | 0.911 | 0.95 | 0.966 | 7.96 | 9.19 | 8.68 | 0.716 | 0.804 | 0.916 | 5.05 | 7.15 | 6.74 | 0.725 | 0.721 | 0.724 | 6.06 | 6.75 | 7.93 | 0.85 | 0.917 | 0.697 | 7.7 | 5.77 | -6.5 | Very Poor_Mixed | 2138 | 2479.2 | 1.128 | 0.966 | 9.19 | 0.917 | 7.93 | 0.1303 | 0.6109 | 0.2197 | 0.3214 | 1 | 0.1078 | 0.2978 | 0.3726 | 0.3726 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2072 | 913.7 | 576.1 | 108.5 | 128 | 23.2 | 958.9 | 6592.5 | 53 | 26.5 | 79 | 79.4 | 73.5 | 86.2 | 35.9 | 12.2 | 9176.8 | 8385.1 | 7914 | 17075.2 | 16582.8 | 13386 | 1.861 | 1.978 | 1.691 | 0.5 | 0.55 | 0.5 | -2 | 2.6 | 2.13 | 0.54 | 0.542 | 0.514 | 2.09 | 2.01 | 3.59 | 0.634 | 0.54 | 0.51 | 3.09 | 2.54 | -2.41 | 0.551 | 0.574 | 0.5 | 2 | 3.05 | 2.58 | Poor_DGA | 7914 | 13386 | 1.691 | 0.55 | 2.6 | 0.634 | 3.59 | 0.3559 | 0.8458 | 0.8278 | 0.9618 | 1 | 0.9334 | 0.7997 | 0.756 | 0.756 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2073 | 343.7 | 251.7 | 80.7 | 80.9 | 38.7 | 510.8 | 3443.5 | 31.7 | 46.8 | 80.5 | 80.4 | 75.9 | 87.6 | 37.3 | 18.2 | 4828.6 | 4487.3 | 4363 | 7272.2 | 6976.7 | 6081.8 | 1.506 | 1.555 | 1.394 | 0.708 | 0.646 | 0.601 | 5.14 | -4.44 | 3.78 | 0.609 | 0.587 | 0.611 | 2.78 | -3.26 | 3.57 | 0.566 | 0.633 | 0.627 | -4.05 | 3.28 | 3.58 | 0.539 | 0.526 | 0.617 | -2.79 | 2.59 | 4.18 | Critical_Oil | 4363 | 6081.8 | 1.394 | 0.708 | 5.14 | 0.633 | 4.18 | 0.5431 | 0.6128 | 0.7731 | 0.8024 | 1 | 0.5713 | 0.6625 | 0.686 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2074 | 1467.7 | 802.7 | 128.6 | 170.9 | 27 | 1177.9 | 7888.6 | 36.4 | 45.2 | 105 | 107.5 | 92 | 112.5 | 43.1 | 33.1 | 1914.3 | 2043.6 | 993.4 | 2187.5 | 2148.8 | 1200 | 1.143 | 1.051 | 1.208 | 0.922 | 0.873 | 0.915 | 7.81 | 8.45 | -8.62 | 0.702 | 0.894 | 0.698 | 7.97 | 7.3 | -7.12 | 0.81 | 0.878 | 0.858 | 7.06 | -6.01 | -7.5 | 0.757 | 0.801 | 0.858 | 7.05 | 6.88 | 7.67 | Very Poor_Mixed | 993.4 | 1200 | 1.051 | 0.922 | 8.62 | 0.894 | 7.97 | 0.1754 | 0.628 | 0.1745 | 0.2787 | 1 | 0.1507 | 0.2576 | 0.3781 | 0.3781 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2075 | 937.6 | 587.5 | 109.7 | 127 | 13.5 | 913.2 | 5697.2 | 43.1 | 35.7 | 93 | 94.2 | 82.7 | 96.6 | 40.3 | 25.8 | 4784.6 | 4201.9 | 5263.2 | 6794 | 6387 | 8279.5 | 1.42 | 1.52 | 1.573 | 0.782 | 0.749 | 0.736 | 5.74 | 5.63 | 5.33 | 0.594 | 0.668 | 0.702 | 4.75 | 3.54 | 4.61 | 0.678 | 0.607 | 0.611 | -6.06 | 4.68 | 4.42 | 0.747 | 0.685 | 0.598 | 5.75 | 4.4 | -4.89 | Poor_Mixed | 4201.9 | 6387 | 1.42 | 0.782 | 5.74 | 0.747 | 6.06 | 0.4284 | 0.7265 | 0.4766 | 0.5513 | 1 | 0.4084 | 0.5097 | 0.5784 | 0.5784 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2076 | 162.4 | 120 | 70.7 | 55.5 | 3.7 | 350 | 2604.5 | 58.6 | 20 | 75 | 76 | 72.5 | 80.1 | 35.4 | 12 | 9204.1 | 9589.1 | 9280.4 | 17800.3 | 18635.7 | 18405.9 | 1.934 | 1.943 | 1.983 | 0.526 | 0.585 | 0.5 | 2.46 | 2.87 | -2 | 0.52 | 0.505 | 0.5 | 2.07 | -2 | 2.25 | 0.517 | 0.525 | 0.5 | 2.54 | 2.14 | 2 | 0.508 | 0.533 | 0.507 | 2.26 | 2.41 | -2.64 | Good_Mixed | 9204.1 | 17800.3 | 1.934 | 0.585 | 2.87 | 0.533 | 2.64 | 0.8729 | 1 | 0.9534 | 0.9661 | 1 | 0.8709 | 0.903 | 0.9263 | 0.9263 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2077 | 796.9 | 455.1 | 101.4 | 105.2 | 15.8 | 825.2 | 4874.3 | 44.3 | 34.1 | 91.8 | 94.1 | 82 | 100.2 | 40.7 | 27.6 | 5658.2 | 5003.5 | 5903.6 | 8388.1 | 7604.5 | 9056.3 | 1.482 | 1.52 | 1.534 | 0.766 | 0.756 | 0.751 | -5.73 | 5.72 | 6.25 | 0.651 | 0.669 | 0.635 | 5.54 | 4.41 | -5.36 | 0.593 | 0.631 | 0.724 | -4.03 | -4.48 | -4.8 | 0.625 | 0.667 | 0.687 | -5.2 | 3.47 | 4.08 | Poor_Mixed | 5003.5 | 7604.5 | 1.482 | 0.766 | 6.25 | 0.724 | 5.54 | 0.4849 | 0.7449 | 0.4687 | 0.4866 | 1 | 0.3881 | 0.5155 | 0.589 | 0.589 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2078 | 891.3 | 538.5 | 107.1 | 112.5 | 16.7 | 874.3 | 5192.9 | 59.1 | 22.8 | 78.3 | 75.3 | 74.3 | 83.7 | 35 | 10.4 | 8558.9 | 8854.8 | 9341.9 | 16289.9 | 17290.2 | 18042.2 | 1.903 | 1.953 | 1.931 | 0.532 | 0.5 | 0.531 | 2.55 | -2.37 | 2.39 | 0.505 | 0.513 | 0.539 | 2.3 | 2.6 | 3.26 | 0.535 | 0.522 | 0.5 | 2 | 2.73 | 2.55 | 0.522 | 0.527 | 0.515 | 2.83 | -3.15 | 2.04 | Fair_DGA | 8558.9 | 16289.9 | 1.903 | 0.532 | 2.55 | 0.539 | 3.26 | 0.4414 | 0.9108 | 0.8896 | 0.9955 | 1 | 0.8929 | 0.8554 | 0.7974 | 0.7974 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2079 | 949.5 | 598.4 | 103.7 | 125.8 | 22.1 | 916.1 | 5823.2 | 55.5 | 25.3 | 79.8 | 77.8 | 70.8 | 84.9 | 35.6 | 11.6 | 8695 | 9213.8 | 9550.3 | 16555.9 | 18164.8 | 18927.7 | 1.904 | 1.971 | 1.982 | 0.561 | 0.701 | 0.553 | 3.17 | 4.81 | 3.14 | 0.516 | 0.509 | 0.523 | 2.26 | 2.05 | 2.32 | 0.528 | 0.54 | 0.519 | 2.3 | -2.7 | 2.78 | 0.514 | 0.507 | 0.5 | -2 | -2.44 | 2.9 | Poor_DGA | 8695 | 16555.9 | 1.904 | 0.701 | 4.81 | 0.54 | 2.9 | 0.3759 | 0.865 | 0.8684 | 0.9744 | 1 | 0.6763 | 0.8723 | 0.745 | 0.745 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2080 | 1030.5 | 606.6 | 117.4 | 135.1 | 26.6 | 976.5 | 6232.7 | 55.2 | 25.5 | 77.3 | 79 | 74.6 | 85.6 | 35.9 | 14 | 9812.3 | 9385.3 | 8822.2 | 18668.4 | 17961.2 | 17112.2 | 1.903 | 1.914 | 1.94 | 0.572 | 0.59 | 0.539 | 3.24 | -3.11 | 3.16 | 0.572 | 0.534 | 0.612 | -2.07 | -3.42 | 2.75 | 0.528 | 0.562 | 0.557 | -2.37 | 3.18 | 2.26 | 0.539 | 0.543 | 0.531 | 2.82 | 2.77 | 2.63 | Poor_DGA | 8822.2 | 17112.2 | 1.903 | 0.59 | 3.24 | 0.612 | 3.42 | 0.3147 | 0.8617 | 0.8424 | 0.9194 | 1 | 0.7511 | 0.7598 | 0.7142 | 0.7142 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2081 | 967.8 | 588.6 | 116.3 | 132.4 | 21.8 | 943.8 | 6061.5 | 54.7 | 23.1 | 79 | 79.4 | 72.3 | 86.7 | 36.7 | 11.6 | 9685.2 | 9722.3 | 9408.4 | 18091.2 | 18964.4 | 18417.3 | 1.868 | 1.951 | 1.958 | 0.588 | 0.519 | 0.64 | -3.65 | 3.36 | 3.94 | 0.542 | 0.51 | 0.5 | 2.53 | -2.88 | 2.35 | 0.553 | 0.5 | 0.545 | 2.25 | 2.54 | 2.08 | 0.557 | 0.531 | 0.512 | 2.79 | 3.05 | -2.82 | Poor_DGA | 9408.4 | 18091.2 | 1.868 | 0.64 | 3.94 | 0.557 | 3.05 | 0.3558 | 0.9047 | 0.8316 | 0.9744 | 1 | 0.7076 | 0.8411 | 0.7399 | 0.7399 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2082 | 511.6 | 286.4 | 86.6 | 81.5 | 3.2 | 662.8 | 4035 | 56.5 | 24.1 | 77.6 | 81 | 72.5 | 85.6 | 36.5 | 10.5 | 885.2 | 2628.4 | 1295.2 | 984.5 | 3103.7 | 1393.1 | 1.112 | 1.181 | 1.076 | 0.759 | 0.773 | 0.686 | -5.63 | 6.6 | -10.9 | 0.544 | 0.602 | 0.541 | 2.96 | 2.76 | -2.68 | 0.52 | 0.505 | 0.569 | 2.78 | 2.54 | 2.87 | 0.523 | 0.579 | 0.571 | -2.47 | 3.02 | 2.6 | Critical_IR_PI | 885.2 | 984.5 | 1.076 | 0.773 | 10.9 | 0.602 | 3.02 | 0.7196 | 0.8857 | 0.8361 | 0.994 | 0.925 | 0.3263 | 0.7682 | 0.7515 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Winding_TV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
2083 | 1529.9 | 839.9 | 125.2 | 165 | 31.8 | 1158.8 | 7700.7 | 35.6 | 43.6 | 103.7 | 102.3 | 90.2 | 112.6 | 44.8 | 34.8 | 871.9 | 1493.3 | 1843.3 | 1001.6 | 1523.2 | 2055.5 | 1.149 | 1.02 | 1.115 | 0.924 | 1.741 | 0.944 | 8.63 | 8.2 | 9.18 | 0.859 | 0.797 | 0.791 | 9.26 | -4.98 | -6.74 | 0.854 | 0.69 | 0.821 | -8.72 | 7.6 | -6.55 | 0.851 | 0.819 | 0.791 | 7.21 | -6.42 | -6.62 | Critical_Mixed | 871.9 | 1001.6 | 1.02 | 1.741 | 9.18 | 0.859 | 9.26 | 0.1566 | 0.6435 | 0.2083 | 0.2118 | 1 | 0.0957 | 0.2565 | 0.3673 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
2084 | 954.8 | 492 | 102 | 125.7 | 16.4 | 860.8 | 5519.3 | 48.7 | 33.4 | 90 | 90.9 | 80.5 | 96.3 | 39.3 | 25.1 | 5520.7 | 6162.8 | 6189.5 | 7716.4 | 9600.5 | 10441.8 | 1.398 | 1.558 | 1.687 | 0.756 | 0.82 | 0.743 | 6.11 | 6.23 | 5.67 | 0.658 | 0.76 | 0.709 | 3.75 | 4.55 | -6.15 | 0.672 | 0.703 | 0.691 | 6.56 | 4.17 | 5.22 | 0.623 | 0.779 | 0.735 | 4.94 | 5.33 | -5.15 | Poor_Mixed | 5520.7 | 7716.4 | 1.398 | 0.82 | 6.23 | 0.779 | 6.56 | 0.4328 | 0.7532 | 0.5391 | 0.576 | 1 | 0.3704 | 0.4368 | 0.5718 | 0.5718 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2085 | 869 | 531.1 | 103.1 | 101 | 19.5 | 805.7 | 5521.9 | 44.2 | 34.2 | 90.6 | 92.6 | 83.1 | 98.1 | 39.2 | 24.1 | 4946.6 | 4856.4 | 5307 | 7484.3 | 7112.5 | 7860 | 1.513 | 1.465 | 1.481 | 0.693 | 0.695 | 0.732 | 5.72 | 5.19 | 6.19 | 0.698 | 0.661 | 0.712 | 6.31 | -4.66 | 4.57 | 0.623 | 0.647 | 0.647 | -4.31 | -5.23 | -4.82 | 0.614 | 0.654 | 0.684 | 5.15 | -4.16 | 3.95 | Poor_Mixed | 4856.4 | 7112.5 | 1.465 | 0.732 | 6.19 | 0.712 | 6.31 | 0.4465 | 0.7438 | 0.4991 | 0.6108 | 1 | 0.4441 | 0.4989 | 0.5933 | 0.5933 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2086 | 403.4 | 277.7 | 78.4 | 80.4 | 2.8 | 550.6 | 3689.2 | 54.3 | 69.4 | 83.5 | 81.4 | 73.2 | 89.2 | 37.4 | 14.1 | 3380.6 | 2709.1 | 3204.6 | 4019.2 | 3357.8 | 3881.5 | 1.189 | 1.239 | 1.211 | 0.734 | 0.694 | 0.676 | 5.52 | 5.04 | 5.26 | 0.571 | 0.5 | 0.576 | 2 | -2.68 | -2.95 | 0.518 | 0.533 | 0.5 | 2.47 | -2.49 | 2.65 | 0.531 | 0.5 | 0.545 | -2.4 | -3.28 | 2.07 | Critical_IR_PI | 2709.1 | 3357.8 | 1.189 | 0.734 | 5.52 | 0.576 | 3.28 | 0.7634 | 0.5833 | 0.7531 | 0.9169 | 1 | 0.473 | 0.8447 | 0.7603 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2087 | 263.7 | 223.7 | 79.5 | 50.7 | 4.5 | 407 | 3230.2 | 57.4 | 21.1 | 75 | 75 | 70.4 | 80 | 35.2 | 10.3 | 10000 | 9684.8 | 9766 | 19042.9 | 18422.9 | 19531.9 | 1.904 | 1.902 | 2 | 0.678 | 0.694 | 0.738 | -4.7 | 5.42 | -6.33 | 0.513 | 0.5 | 0.534 | 2 | 2.08 | -2 | 0.538 | 0.518 | 0.5 | -2.91 | 2.13 | 2.58 | 0.5 | 0.537 | 0.508 | -2 | 2 | 2 | Poor_Winding_TD_Cap | 9684.8 | 18422.9 | 1.902 | 0.738 | 6.33 | 0.538 | 2.91 | 0.8249 | 0.9514 | 0.9931 | 0.9968 | 1 | 0.4599 | 0.9019 | 0.8563 | 0.8563 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2088 | 988.3 | 605 | 109.3 | 126.7 | 21.5 | 917.2 | 6202.2 | 47.2 | 33.5 | 91.4 | 90.3 | 83.6 | 98.5 | 41.4 | 25.9 | 5520.8 | 5389.5 | 4537.7 | 8903.7 | 8264.3 | 6475.8 | 1.613 | 1.533 | 1.427 | 0.698 | 0.675 | 0.722 | 5.37 | 5.08 | -5.06 | 0.662 | 0.711 | 0.645 | -5.02 | 4.75 | 5.58 | 0.667 | 0.637 | 0.675 | 6.31 | 4.74 | 5.04 | 0.665 | 0.736 | 0.653 | -4.23 | 4.73 | 5.02 | Poor_Mixed | 4537.7 | 6475.8 | 1.427 | 0.722 | 5.37 | 0.736 | 6.31 | 0.3662 | 0.752 | 0.4893 | 0.5478 | 1 | 0.4814 | 0.4735 | 0.5708 | 0.5708 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2089 | 958.5 | 489.1 | 102.5 | 112.1 | 15.5 | 832.6 | 5327.3 | 47.4 | 31.7 | 91.2 | 89.5 | 84.4 | 95.6 | 40.8 | 25.5 | 6602.4 | 6003.4 | 5872.4 | 10882.6 | 10277.1 | 9295.7 | 1.648 | 1.712 | 1.583 | 0.749 | 0.76 | 0.734 | -5.82 | 6.55 | -5.81 | 0.761 | 0.703 | 0.719 | 4.6 | 5.66 | 6.05 | 0.707 | 0.689 | 0.725 | 4.86 | 4.99 | 3.63 | 0.718 | 0.764 | 0.61 | 5.02 | 4.71 | -4.49 | Poor_Mixed | 5872.4 | 9295.7 | 1.583 | 0.76 | 6.55 | 0.764 | 6.05 | 0.4572 | 0.7741 | 0.5095 | 0.562 | 1 | 0.3879 | 0.4351 | 0.5789 | 0.5789 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2090 | 286.5 | 161.4 | 71.2 | 66.6 | 1 | 470 | 3719.4 | 55.5 | 27.8 | 83 | 85 | 77.5 | 89.6 | 37.4 | 13.8 | 7948.7 | 7533.2 | 6929.7 | 13923.7 | 12606.9 | 11859.9 | 1.752 | 1.674 | 1.711 | 0.937 | 2.379 | 0.916 | 8.52 | 8.88 | -9.05 | 0.575 | 0.617 | 0.589 | -3.9 | 3.39 | 2.65 | 0.594 | 0.575 | 0.571 | -3.4 | 4.27 | 3.64 | 0.547 | 0.625 | 0.569 | 3.63 | 3.42 | -3.9 | Critical_Winding_TD_Cap | 6929.7 | 11859.9 | 1.674 | 2.379 | 9.05 | 0.625 | 4.27 | 0.9079 | 0.8264 | 0.6946 | 0.9244 | 1 | 0.0916 | 0.6576 | 0.733 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | Winding_LV_TanDelta_pct
2091 | 188.1 | 169.7 | 68 | 57.4 | 46.6 | 407.3 | 3386 | 35.3 | 44.1 | 82.4 | 83.1 | 77.3 | 86.8 | 36.2 | 16.7 | 5312.4 | 5543.5 | 6464.3 | 8062.7 | 8803.8 | 10613.8 | 1.518 | 1.588 | 1.642 | 0.626 | 0.607 | 0.662 | 4.03 | 3.5 | 4.4 | 0.543 | 0.504 | 0.583 | -2.05 | 2 | 2.2 | 0.517 | 0.5 | 0.507 | 2 | 3.02 | 2.37 | 0.5 | 0.508 | 0.537 | -2.56 | 2.76 | 2 | Critical_Oil | 5312.4 | 8062.7 | 1.518 | 0.662 | 4.4 | 0.583 | 3.02 | 0.626 | 0.6386 | 0.7352 | 0.8465 | 1 | 0.6191 | 0.8786 | 0.7538 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2092 | 584.4 | 367.9 | 80.5 | 82.2 | 8.9 | 595.4 | 4291.9 | 51.1 | 29.2 | 83.2 | 85.6 | 77.7 | 90.9 | 37.1 | 18.5 | 7295.9 | 8794.6 | 7943.1 | 12483.6 | 15879.2 | 13873.5 | 1.711 | 1.806 | 1.747 | 0.698 | 0.642 | 0.714 | 5.11 | 4.28 | 5.34 | 0.557 | 0.605 | 0.563 | 3.5 | 4.44 | 3.32 | 0.6 | 0.546 | 0.579 | 2.81 | 2.94 | -3.03 | 0.565 | 0.568 | 0.585 | -2.86 | 3.48 | -2.89 | Fair_Mixed | 7295.9 | 12483.6 | 1.711 | 0.714 | 5.34 | 0.605 | 4.44 | 0.6416 | 0.8067 | 0.6824 | 0.7933 | 1 | 0.5101 | 0.6894 | 0.7206 | 0.7206 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2093 | 263.6 | 146 | 70.2 | 56.6 | 3.3 | 411.5 | 3205.5 | 53.4 | 23.3 | 80.2 | 81.4 | 75 | 86.4 | 36.3 | 14 | 7434.9 | 5908 | 5053 | 12091 | 9234.5 | 7860.1 | 1.626 | 1.563 | 1.556 | 0.592 | 0.558 | 0.65 | 3.86 | -2.76 | 3.56 | 0.535 | 0.566 | 0.59 | 2.67 | -2.41 | 3.04 | 0.558 | 0.51 | 0.536 | 3.23 | 3.61 | -3.47 | 0.578 | 0.509 | 0.539 | 3.1 | 3 | 2.54 | Poor_IR_PI | 5053 | 7860.1 | 1.556 | 0.65 | 3.86 | 0.59 | 3.61 | 0.8466 | 0.9008 | 0.7853 | 0.9194 | 1 | 0.6953 | 0.7629 | 0.8389 | 0.8389 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2094 | 257.1 | 151.5 | 74.4 | 56.3 | 1 | 497.4 | 2831 | 57.6 | 22.1 | 77.2 | 78.9 | 73.4 | 85.2 | 37 | 10.7 | 9054.9 | 8815.4 | 10000 | 17934.1 | 17293.7 | 20000 | 1.981 | 1.962 | 2 | 0.688 | 0.693 | 0.781 | -5.55 | -5.04 | 6.15 | 0.572 | 0.537 | 0.517 | -2.67 | 2.86 | -2.87 | 0.563 | 0.5 | 0.558 | 2.07 | 2.3 | 2.17 | 0.5 | 0.5 | 0.54 | -2.43 | 2.17 | 2.3 | Fair_Winding_TD_Cap | 8815.4 | 17293.7 | 1.962 | 0.781 | 6.15 | 0.572 | 2.87 | 0.9274 | 0.926 | 0.8505 | 0.9909 | 1 | 0.4393 | 0.8468 | 0.8515 | 0.8515 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
2095 | 982.5 | 586.2 | 112.2 | 124.7 | 19.1 | 931.7 | 5970.7 | 47.7 | 32.7 | 89.7 | 90.6 | 80 | 96.6 | 38.8 | 26.6 | 4534.8 | 5878.6 | 5745.9 | 6737.5 | 9544.1 | 8818.5 | 1.486 | 1.624 | 1.535 | 0.733 | 0.76 | 0.694 | 5.44 | 5.84 | 4.52 | 0.61 | 0.619 | 0.654 | -5.27 | 4.32 | 5.1 | 0.708 | 0.639 | 0.676 | 3.88 | 4.98 | 4.96 | 0.625 | 0.603 | 0.696 | 5.35 | -5.93 | 5.5 | Poor_Mixed | 4534.8 | 6737.5 | 1.486 | 0.76 | 5.84 | 0.708 | 5.93 | 0.3833 | 0.7617 | 0.5479 | 0.5228 | 1 | 0.4488 | 0.5069 | 0.5822 | 0.5822 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2096 | 1369.9 | 822.9 | 132.2 | 168.7 | 27.5 | 1200.7 | 8052.9 | 40.7 | 42.3 | 100 | 102.4 | 90.1 | 110.3 | 42.1 | 29.8 | 2126.2 | 1712.3 | 1629.8 | 2547 | 1952.1 | 1792.7 | 1.198 | 1.14 | 1.1 | 0.843 | 0.855 | 0.87 | 7.75 | -8.31 | 8.84 | 0.738 | 0.902 | 0.837 | 7.31 | 8.77 | 5.83 | 0.709 | 0.736 | 0.776 | 5.91 | -8.18 | 6.87 | 0.712 | 0.839 | 0.809 | 7.95 | 5.83 | 7.54 | Very Poor_Mixed | 1629.8 | 1792.7 | 1.1 | 0.87 | 8.84 | 0.902 | 8.77 | 0.1723 | 0.6564 | 0.2603 | 0.4051 | 1 | 0.1843 | 0.2804 | 0.4044 | 0.4044 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2097 | 290.6 | 146 | 70.3 | 51.3 | 63.4 | 441.7 | 2837.6 | 53.1 | 25.9 | 83 | 82 | 75.1 | 87 | 36.5 | 14.6 | 2700.1 | 3481.2 | 1852.3 | 3425.3 | 4254.6 | 2139.7 | 1.269 | 1.222 | 1.155 | 0.705 | 0.696 | 0.679 | 5.47 | 4.48 | -4.95 | 0.614 | 0.58 | 0.53 | 3.87 | 2.48 | 2.8 | 0.537 | 0.509 | 0.554 | -2.65 | -3.44 | 2.59 | 0.602 | 0.551 | 0.604 | 2.78 | 3.07 | -3.05 | Critical_IR_PI | 1852.3 | 2139.7 | 1.155 | 0.705 | 5.47 | 0.614 | 3.87 | 0.6265 | 0.8552 | 0.7528 | 0.904 | 1 | 0.4976 | 0.7285 | 0.7405 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2098 | 1053.7 | 563.8 | 113.2 | 140.9 | 19.3 | 932.6 | 5942.4 | 58.9 | 20.9 | 78.7 | 80 | 72.4 | 82.6 | 35.6 | 14.8 | 7367.5 | 8715.3 | 8171 | 13260.3 | 16907.3 | 14889.2 | 1.8 | 1.94 | 1.822 | 0.568 | 0.515 | 0.556 | 3.06 | -2 | 3.01 | 0.543 | 0.525 | 0.52 | 3.27 | -3.01 | 2.26 | 0.563 | 0.5 | 0.53 | -2 | -2 | 2.21 | 0.538 | 0.529 | 0.527 | 2.44 | 3.01 | 3.06 | Poor_DGA | 7367.5 | 13260.3 | 1.8 | 0.568 | 3.06 | 0.563 | 3.27 | 0.3635 | 0.9574 | 0.8539 | 0.8988 | 1 | 0.8218 | 0.8252 | 0.7597 | 0.7597 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2099 | 922.3 | 501.6 | 103.3 | 120.1 | 15.5 | 860.3 | 5594.6 | 44.8 | 35.4 | 93 | 92.5 | 82.1 | 99.5 | 41.1 | 25.8 | 6128.5 | 4529.3 | 4353.4 | 9439.6 | 6860.2 | 6214.2 | 1.54 | 1.515 | 1.427 | 0.756 | 0.758 | 0.808 | 5.71 | 6.68 | 7.25 | 0.708 | 0.648 | 0.697 | -4.5 | 4.67 | 5.47 | 0.62 | 0.688 | 0.642 | -5.57 | 3.97 | 4.13 | 0.679 | 0.686 | 0.593 | 4.99 | -4.7 | -5.63 | Poor_Mixed | 4353.4 | 6214.2 | 1.427 | 0.808 | 7.25 | 0.708 | 5.63 | 0.444 | 0.7299 | 0.4713 | 0.5513 | 1 | 0.3401 | 0.4947 | 0.5699 | 0.5699 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2100 | 1513.4 | 907 | 136.7 | 175.9 | 32.2 | 1267.5 | 7961.9 | 32.7 | 46.7 | 107.3 | 107.2 | 94 | 118.2 | 43.7 | 32.5 | 2769.2 | 1607.9 | 851.6 | 3361.9 | 1698.5 | 1200 | 1.214 | 1.056 | 1.409 | 0.892 | 0.979 | 0.954 | 8.24 | 9.78 | 9.31 | 0.853 | 0.895 | 0.831 | 6.61 | -5.51 | 8.42 | 0.806 | 0.81 | 0.962 | 5.83 | -7.3 | -6.15 | 0.879 | 0.868 | 0.86 | 8.65 | 7.72 | 6.34 | Very Poor_Mixed | 851.6 | 1200 | 1.056 | 0.979 | 9.78 | 0.962 | 8.65 | 0.1151 | 0.6137 | 0.1194 | 0.302 | 1 | 0.0834 | 0.2109 | 0.3391 | 0.3391 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2101 | 987.7 | 533.1 | 111.4 | 125.9 | 19.8 | 882.4 | 5926.9 | 45.7 | 32.7 | 90.4 | 89.9 | 83.3 | 96.3 | 38.9 | 26.8 | 6204.1 | 5992 | 5873.6 | 10157.5 | 9520 | 8871.9 | 1.637 | 1.589 | 1.51 | 0.711 | 0.743 | 0.775 | 6.12 | 5.36 | 6.16 | 0.624 | 0.698 | 0.589 | 4.42 | 5.76 | 4.71 | 0.656 | 0.725 | 0.629 | 4.26 | -5 | -4.05 | 0.64 | 0.687 | 0.716 | 4.7 | 4.95 | 4.67 | Poor_Mixed | 5873.6 | 8871.9 | 1.51 | 0.775 | 6.16 | 0.725 | 5.76 | 0.3905 | 0.7617 | 0.5275 | 0.5156 | 1 | 0.4022 | 0.4996 | 0.5738 | 0.5738 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2102 | 586.6 | 404.2 | 88.2 | 86 | 14.3 | 660.7 | 4720.6 | 55.2 | 25.5 | 83.2 | 83 | 76.6 | 88.3 | 37.8 | 18.6 | 6777.8 | 6771.7 | 8173 | 11449.1 | 11234.1 | 14254 | 1.689 | 1.659 | 1.744 | 0.681 | 0.66 | 0.65 | 4.23 | 3.52 | -4.87 | 0.602 | 0.626 | 0.554 | 3.66 | 2.88 | 2.77 | 0.556 | 0.559 | 0.567 | 2.96 | 3.63 | 3.97 | 0.537 | 0.637 | 0.648 | 3.15 | 2.47 | 4.05 | Fair_Mixed | 6771.7 | 11234.1 | 1.659 | 0.681 | 4.87 | 0.648 | 4.05 | 0.5711 | 0.8617 | 0.7188 | 0.7902 | 1 | 0.5714 | 0.6703 | 0.7182 | 0.7182 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2103 | 947.3 | 516 | 111.6 | 123.1 | 20.5 | 855.2 | 5791.4 | 44.9 | 36.2 | 92.7 | 90.4 | 82.1 | 99.8 | 38.9 | 25.9 | 6246.4 | 4222.8 | 4142.7 | 9518.5 | 6061.6 | 6161.6 | 1.524 | 1.435 | 1.487 | 0.75 | 0.69 | 0.706 | 6.53 | 5.61 | 5.37 | 0.716 | 0.615 | 0.644 | 5.38 | 4.64 | 5.51 | 0.669 | 0.643 | 0.675 | 5.18 | 5.02 | 5.52 | 0.63 | 0.733 | 0.673 | 5.96 | 4.98 | 4.53 | Poor_Mixed | 4142.7 | 6061.6 | 1.435 | 0.75 | 6.53 | 0.733 | 5.96 | 0.3989 | 0.7208 | 0.4994 | 0.5478 | 1 | 0.429 | 0.4764 | 0.5694 | 0.5694 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2104 | 808.2 | 589.9 | 98.3 | 120.9 | 18.7 | 782 | 5141.5 | 48.2 | 32.7 | 91.8 | 88.4 | 84 | 98.9 | 39.6 | 26.1 | 5056.6 | 5573.8 | 5881.8 | 7393.1 | 8954 | 9488.8 | 1.462 | 1.606 | 1.613 | 0.751 | 0.8 | 0.731 | 6.51 | 6.32 | 5.98 | 0.599 | 0.693 | 0.712 | -5.07 | 4.14 | -4.71 | 0.684 | 0.671 | 0.619 | 5.18 | 4.62 | -3.78 | 0.686 | 0.676 | 0.718 | -5.31 | 3.51 | 4.94 | Poor_Mixed | 5056.6 | 7393.1 | 1.462 | 0.8 | 6.51 | 0.718 | 5.31 | 0.4399 | 0.7617 | 0.5067 | 0.5407 | 1 | 0.3659 | 0.491 | 0.5787 | 0.5787 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2105 | 1615.7 | 966.6 | 148.3 | 192.7 | 32.1 | 1283.4 | 8782.1 | 31.4 | 48.9 | 106.2 | 106.9 | 95.6 | 115.7 | 44.2 | 30.6 | 1664.6 | 1533.4 | 2295 | 1906.3 | 1610.1 | 2765.6 | 1.145 | 1.05 | 1.205 | 0.928 | 0.943 | 0.916 | 8.86 | -8.74 | -8.86 | 0.867 | 0.768 | 0.812 | 6.58 | -7.07 | 6.88 | 0.776 | 0.926 | 0.858 | 7.27 | 6.19 | -8.55 | 0.956 | 0.859 | 0.894 | 8.73 | 6.21 | -8.88 | Very Poor_Mixed | 1533.4 | 1610.1 | 1.05 | 0.943 | 8.86 | 0.956 | 8.88 | 0.0661 | 0.5933 | 0.1272 | 0.3749 | 1 | 0.106 | 0.2026 | 0.3305 | 0.3305 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2106 | 1628.8 | 887.4 | 142.9 | 189.7 | 33.4 | 1319.9 | 7791.4 | 33.2 | 46.6 | 108.2 | 105.7 | 94.7 | 115.8 | 45.6 | 31.5 | 1935 | 2070.1 | 2373.1 | 2154.5 | 2489 | 2654.6 | 1.113 | 1.202 | 1.119 | 0.939 | 0.956 | 0.967 | -8.8 | 9.06 | -9.84 | 0.81 | 0.945 | 0.887 | 5.52 | -6.19 | 6.89 | 0.758 | 0.866 | 0.925 | 4.88 | 9.03 | 8.85 | 0.775 | 0.754 | 0.826 | -7.24 | 6.71 | 8.59 | Very Poor_Mixed | 1935 | 2154.5 | 1.113 | 0.967 | 9.84 | 0.945 | 9.03 | 0.0838 | 0.6147 | 0.117 | 0.3406 | 1 | 0.0684 | 0.23 | 0.3344 | 0.3344 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2107 | 361.3 | 198.4 | 72.1 | 65.1 | 2.4 | 452.3 | 3289 | 59.6 | 20.3 | 78.1 | 77.6 | 71.2 | 81.8 | 35.5 | 13.8 | 9390 | 9277.5 | 8922.8 | 18121.9 | 17963.9 | 16371.5 | 1.93 | 1.936 | 1.835 | 0.575 | 0.532 | 0.5 | -3.08 | 2.79 | 2.28 | 0.539 | 0.5 | 0.529 | 2.12 | 2.96 | -2.24 | 0.552 | 0.505 | 0.515 | -2 | 2.39 | 2 | 0.51 | 0.53 | 0.5 | 2.06 | 2 | 2.28 | Good_Mixed | 8922.8 | 16371.5 | 1.835 | 0.575 | 3.08 | 0.552 | 2.96 | 0.8277 | 0.9791 | 0.8979 | 0.9244 | 1 | 0.8497 | 0.8839 | 0.8985 | 0.8985 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2108 | 543.6 | 423.5 | 86.7 | 93.6 | 11.6 | 671.6 | 4825.3 | 51.9 | 27.8 | 84.8 | 85.7 | 79.8 | 91.5 | 37.8 | 18.8 | 7057.2 | 7915.1 | 8608.7 | 11591.8 | 13435.6 | 16027.1 | 1.643 | 1.697 | 1.862 | 0.705 | 0.68 | 0.649 | 5.13 | 5.16 | 4.56 | 0.616 | 0.607 | 0.65 | 3.71 | -3.23 | -3.76 | 0.614 | 0.626 | 0.578 | -3.8 | -3.56 | -3.14 | 0.603 | 0.642 | 0.593 | 2.9 | 3.38 | 4.24 | Fair_Mixed | 7057.2 | 11591.8 | 1.643 | 0.705 | 5.16 | 0.65 | 4.24 | 0.5829 | 0.8264 | 0.6484 | 0.7841 | 1 | 0.5136 | 0.6112 | 0.6909 | 0.6909 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2109 | 154.1 | 196.9 | 73 | 58.1 | 2.1 | 392.5 | 3349.5 | 57.8 | 24.5 | 75.2 | 78.3 | 70.4 | 82.1 | 35.3 | 12.4 | 8446.3 | 9075 | 8948.2 | 15088 | 16267 | 17319.2 | 1.786 | 1.793 | 1.935 | 0.5 | 0.538 | 0.506 | -2 | 2.55 | 2.15 | 0.5 | 0.5 | 0.528 | 2.54 | 2.8 | 2.04 | 0.504 | 0.5 | 0.52 | -2.83 | 2.18 | -2.07 | 0.5 | 0.5 | 0.547 | 2.13 | -2.54 | 2.37 | Good_Mixed | 8446.3 | 15088 | 1.786 | 0.538 | 2.55 | 0.547 | 2.83 | 0.8775 | 0.8786 | 0.9345 | 0.9575 | 1 | 0.9282 | 0.9188 | 0.9215 | 0.9215 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2110 | 1711.7 | 965.3 | 147.1 | 197 | 33.1 | 1377.3 | 9122.1 | 50.5 | 27.9 | 84.5 | 82.3 | 76.6 | 88.3 | 37.9 | 15.5 | 7146.9 | 8602.5 | 7688.6 | 13561.8 | 16371.5 | 4508.9 | 1.898 | 1.903 | 0.586 | 0.541 | 0.58 | 0.568 | -2.98 | 3.56 | -3.1 | 0.527 | 0.507 | 0.521 | 2.43 | 2 | 2.27 | 0.523 | 0.533 | 0.594 | 2 | 2.87 | 2 | 0.5 | 0.508 | 0.5 | -2.52 | 2.04 | 2 | Critical_DGA | 7146.9 | 4508.9 | 0.586 | 0.58 | 3.56 | 0.594 | 2.87 | 0.0377 | 0.825 | 0.7139 | 0.88 | 0.8125 | 0.7536 | 0.8773 | 0.6172 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
2111 | 1601.4 | 982.4 | 147.3 | 187.3 | 33.2 | 1293.7 | 8974.8 | 32.9 | 46.8 | 106.7 | 104.5 | 95.8 | 113.8 | 45.1 | 31.6 | 1085.6 | 1752.6 | 2682.5 | 1200 | 2030.2 | 3108.3 | 1.105 | 1.158 | 1.159 | 0.99 | 0.959 | 0.919 | 9.45 | 9.43 | 9.8 | 0.725 | 0.753 | 0.695 | 7.72 | 6.95 | 8.6 | 0.778 | 0.963 | 0.87 | 6.45 | 6.14 | 7.16 | 0.711 | 0.756 | 0.822 | 6.66 | 9.08 | -7.6 | Very Poor_Mixed | 1085.6 | 1200 | 1.105 | 0.99 | 9.8 | 0.963 | 9.08 | 0.062 | 0.6128 | 0.1395 | 0.3368 | 1 | 0.0509 | 0.2723 | 0.336 | 0.336 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2112 | 983.9 | 525.7 | 106.2 | 123.1 | 19.6 | 864.6 | 4916.1 | 47.1 | 33.6 | 91.7 | 90.2 | 82.3 | 96.4 | 40.5 | 24.8 | 5726.5 | 5746.3 | 5675 | 8749.5 | 8841.4 | 8506.8 | 1.528 | 1.539 | 1.499 | 0.664 | 0.662 | 0.671 | 4.54 | -4.9 | 5.06 | 0.613 | 0.639 | 0.705 | 4.4 | 5.09 | 4.36 | 0.731 | 0.672 | 0.707 | -5.02 | 4.41 | 5.09 | 0.573 | 0.621 | 0.718 | 4.73 | -5.32 | 4.26 | Poor_Mixed | 5675 | 8506.8 | 1.499 | 0.671 | 5.06 | 0.731 | 5.32 | 0.412 | 0.7509 | 0.5127 | 0.5865 | 1 | 0.5318 | 0.4985 | 0.5979 | 0.5979 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2113 | 599 | 422.3 | 96.7 | 115.1 | 14.5 | 743.7 | 4605.7 | 55.3 | 25.2 | 80.5 | 80.1 | 72.7 | 83 | 35.5 | 10.5 | 9524.2 | 8639.2 | 8923 | 18145.9 | 16622.3 | 17367.1 | 1.905 | 1.924 | 1.946 | 0.5 | 0.546 | 0.505 | 2.43 | 2.74 | 2.01 | 0.533 | 0.569 | 0.53 | 2.85 | -3.24 | 3.12 | 0.554 | 0.532 | 0.518 | 2 | -2.73 | 3.01 | 0.556 | 0.566 | 0.525 | 2.67 | -2 | 2.64 | Fair_DGA | 8639.2 | 16622.3 | 1.905 | 0.546 | 2.74 | 0.569 | 3.24 | 0.5201 | 0.8666 | 0.8328 | 0.994 | 1 | 0.9122 | 0.7832 | 0.7957 | 0.7957 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2114 | 867.2 | 559.5 | 111.9 | 128.7 | 18.2 | 876.3 | 5486.6 | 54.4 | 25.6 | 75.9 | 76.1 | 70.2 | 80.6 | 35.5 | 16.1 | 9663.3 | 9389.9 | 10000 | 18563.3 | 18473.7 | 19624.3 | 1.921 | 1.967 | 1.962 | 0.585 | 0.55 | 0.531 | 3.03 | -2.85 | -3.32 | 0.533 | 0.513 | 0.589 | 2.32 | 2.81 | -2.62 | 0.576 | 0.542 | 0.536 | 2 | 2 | -2.21 | 0.527 | 0.561 | 0.576 | 2.42 | 3.07 | 3.09 | Poor_DGA | 9389.9 | 18473.7 | 1.921 | 0.585 | 3.32 | 0.589 | 3.09 | 0.409 | 0.86 | 0.957 | 0.8635 | 1 | 0.7762 | 0.7779 | 0.753 | 0.753 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2115 | 1540 | 841.8 | 137.2 | 180 | 31.2 | 1188.6 | 8045.8 | 34.4 | 44.7 | 102.3 | 106.7 | 92.4 | 112 | 44 | 31.1 | 1601.9 | 2968.2 | 1133.1 | 1878 | 3592.4 | 1242 | 1.172 | 1.21 | 1.096 | 0.922 | 0.891 | 0.913 | 8.63 | -8.38 | 8.85 | 0.875 | 0.804 | 0.895 | -8.7 | 8.4 | 9.26 | 0.867 | 0.875 | 0.951 | 8.59 | 6.7 | 8.68 | 0.844 | 0.733 | 0.909 | 6.62 | 7.2 | 9.3 | Very Poor_Mixed | 1133.1 | 1242 | 1.096 | 0.922 | 8.85 | 0.951 | 9.3 | 0.1286 | 0.6328 | 0.1879 | 0.3559 | 1 | 0.1302 | 0.1737 | 0.3541 | 0.3541 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2116 | 1552.8 | 879.5 | 147.3 | 197 | 32 | 1213.8 | 8131.1 | 30.9 | 48.6 | 109.3 | 106.6 | 95.5 | 119.1 | 45.3 | 33.4 | 1275.7 | 2114.6 | 2050.2 | 1412 | 2514.3 | 2438.9 | 1.107 | 1.189 | 1.19 | 0.927 | 0.937 | 0.934 | 9.84 | 9.25 | 9.57 | 0.774 | 0.872 | 0.829 | -6.17 | 7.6 | 7.54 | 0.881 | 0.894 | 0.766 | 8.29 | -7.37 | -6.21 | 0.762 | 0.802 | 0.78 | 5.65 | -6.62 | 5.43 | Very Poor_Mixed | 1275.7 | 1412 | 1.107 | 0.937 | 9.84 | 0.894 | 8.29 | 0.0941 | 0.5961 | 0.0874 | 0.267 | 1 | 0.0667 | 0.2585 | 0.333 | 0.333 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2117 | 973.8 | 652.1 | 106.1 | 130 | 18.1 | 930.2 | 5696.4 | 59.2 | 20 | 75.9 | 77.8 | 70.7 | 82.4 | 35.1 | 10 | 9142.7 | 8976.3 | 8317.2 | 17876.4 | 17244.8 | 15152 | 1.955 | 1.921 | 1.822 | 0.57 | 0.572 | 0.531 | -2.84 | -3.05 | 2.86 | 0.561 | 0.508 | 0.5 | -2.21 | 2.9 | 2.13 | 0.503 | 0.56 | 0.517 | 2 | 2.64 | 2.47 | 0.505 | 0.502 | 0.5 | -2 | 3.05 | 3.03 | Poor_DGA | 8317.2 | 15152 | 1.822 | 0.572 | 3.05 | 0.561 | 3.05 | 0.3853 | 1 | 0.9242 | 1 | 1 | 0.782 | 0.8869 | 0.7879 | 0.7879 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2118 | 179.7 | 126.1 | 68.3 | 55.3 | 1 | 361.2 | 2540 | 56.3 | 24.8 | 80.3 | 79.5 | 75.7 | 88.7 | 36.8 | 15.2 | 4448 | 4472.8 | 5193.6 | 6490.6 | 6349.2 | 7886.3 | 1.459 | 1.42 | 1.518 | 0.623 | 0.673 | 0.598 | 3.79 | 5.02 | -4.08 | 0.562 | 0.582 | 0.567 | 2.81 | 3.8 | -2.13 | 0.592 | 0.579 | 0.569 | 2.14 | 3.81 | -2.84 | 0.599 | 0.544 | 0.567 | 2.98 | 2.56 | 3.72 | Poor_IR_PI | 4448 | 6349.2 | 1.42 | 0.673 | 5.02 | 0.599 | 3.81 | 0.9705 | 0.8734 | 0.7813 | 0.8882 | 1 | 0.6012 | 0.7041 | 0.8409 | 0.8409 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2119 | 1448.7 | 761.5 | 128 | 165.6 | 24 | 1846.9 | 23973.5 | 34.9 | 45.6 | 103.1 | 103 | 89.2 | 110 | 44 | 34 | 1649.9 | 2236.7 | 3273.3 | 1819.3 | 2756.8 | 4191.2 | 1.103 | 1.233 | 1.28 | 0.815 | 0.782 | 0.794 | 7.23 | 7.02 | 6.43 | 0.711 | 0.743 | 0.764 | -5.49 | 5.31 | -6.41 | 0.801 | 0.774 | 0.671 | 7.54 | 6.36 | 4.9 | 0.693 | 0.774 | 0.735 | 4.85 | 8.14 | 6.56 | Critical_Mixed | 1649.9 | 1819.3 | 1.103 | 0.815 | 7.23 | 0.801 | 8.14 | 0.1484 | 0.6241 | 0.2324 | 0.2434 | 1 | 0.3025 | 0.3562 | 0.4139 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | C2H2
2120 | 1396.1 | 836.2 | 130.2 | 167.4 | 31.9 | 1211.8 | 7763.1 | 33.9 | 47.9 | 106.4 | 101.5 | 90.9 | 113.2 | 44.6 | 32.9 | 1297.6 | 2353.8 | 1496.4 | 1415.2 | 2896.8 | 1700.2 | 1.091 | 1.231 | 1.136 | 0.95 | 0.916 | 0.912 | -9.16 | -9.27 | 8.66 | 0.823 | 0.841 | 0.742 | 8.45 | -7.42 | -8.94 | 0.764 | 0.835 | 0.745 | 6.44 | 5.65 | 5.64 | 0.876 | 0.932 | 0.694 | -8.37 | -8.26 | 5.87 | Very Poor_Mixed | 1297.6 | 1415.2 | 1.091 | 0.95 | 9.27 | 0.932 | 8.94 | 0.1536 | 0.6025 | 0.1923 | 0.2865 | 1 | 0.0975 | 0.2571 | 0.3642 | 0.3642 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2121 | 856.3 | 477.7 | 97.1 | 122.1 | 19.2 | 829.1 | 5287.1 | 47.6 | 37.1 | 91.8 | 89.3 | 82.3 | 96.9 | 40 | 24.3 | 5161.6 | 5216.3 | 5148.9 | 7735.8 | 7347.9 | 7358.1 | 1.499 | 1.409 | 1.429 | 0.745 | 0.734 | 0.748 | -5.85 | 5.92 | 6.26 | 0.664 | 0.564 | 0.648 | 4.8 | 4.01 | 5.38 | 0.647 | 0.618 | 0.615 | 4.62 | 3.76 | -3.89 | 0.648 | 0.687 | 0.667 | -4.97 | 5.83 | 4.03 | Poor_Mixed | 5148.9 | 7347.9 | 1.409 | 0.748 | 6.26 | 0.687 | 5.83 | 0.4379 | 0.7109 | 0.5188 | 0.6039 | 1 | 0.395 | 0.5349 | 0.5884 | 0.5884 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2122 | 984 | 610.4 | 101.1 | 130.4 | 23.1 | 863.8 | 5694.2 | 46 | 36.3 | 91.3 | 89.3 | 81.4 | 95.3 | 39.8 | 24.3 | 5954.4 | 5375.8 | 4785.1 | 8797.7 | 8150.2 | 6832 | 1.478 | 1.516 | 1.428 | 0.761 | 0.681 | 0.775 | 5.92 | -5.47 | 6.75 | 0.615 | 0.649 | 0.625 | 4.63 | -5.66 | 5.79 | 0.667 | 0.665 | 0.642 | -4.28 | 4.4 | 4.3 | 0.652 | 0.632 | 0.688 | 3.68 | 5.49 | 5.05 | Poor_Mixed | 4785.1 | 6832 | 1.428 | 0.775 | 6.75 | 0.688 | 5.79 | 0.3718 | 0.7197 | 0.5371 | 0.6039 | 1 | 0.3974 | 0.5129 | 0.5712 | 0.5712 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2123 | 1543.4 | 885.9 | 133 | 173.7 | 34.3 | 1178.7 | 7894.8 | 34.1 | 45 | 104.6 | 107 | 92.3 | 116.4 | 44 | 29.7 | 2103.8 | 2122.8 | 3365.7 | 2401.4 | 2368 | 4382.2 | 1.141 | 1.116 | 1.302 | 0.917 | 0.895 | 0.901 | 9.17 | -7.34 | 7.94 | 0.76 | 0.922 | 0.922 | 6.34 | 6.65 | 5.01 | 0.778 | 0.734 | 0.746 | 5.77 | 7.69 | 8 | 0.906 | 0.703 | 0.737 | 5.73 | 6.28 | 7.81 | Very Poor_Mixed | 2103.8 | 2368 | 1.116 | 0.917 | 9.17 | 0.922 | 8 | 0.1215 | 0.6299 | 0.1519 | 0.4089 | 1 | 0.1575 | 0.284 | 0.3748 | 0.3748 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2124 | 288.1 | 236.9 | 71.1 | 158.9 | 1 | 476.2 | 3133.6 | 57.3 | 24.7 | 107.1 | 109.3 | 93.2 | 112.8 | 45 | 15.7 | 8709.6 | 8394.4 | 6991.7 | 4942.8 | 15478.5 | 12547.3 | 0.568 | 1.844 | 1.795 | 0.688 | 0.648 | 0.652 | 5.26 | -4.6 | -4.37 | 0.517 | 0.585 | 0.531 | -2.04 | 2.98 | 3.04 | 0.565 | 0.558 | 0.509 | 2.65 | 2 | 2.18 | 0.513 | 0.518 | 0.555 | 2.79 | 2.09 | -2.22 | Critical_Thermal | 6991.7 | 4942.8 | 0.568 | 0.688 | 5.26 | 0.585 | 3.04 | 0.8065 | 0.8751 | 0.1312 | 0.8746 | 0.8187 | 0.5406 | 0.8107 | 0.7161 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H4
2125 | 465 | 313.2 | 75.9 | 76.1 | 9.1 | 637.7 | 4072.5 | 52.2 | 27.5 | 81.9 | 82.3 | 76.6 | 87 | 36.4 | 15.6 | 7631.1 | 7863.4 | 7366.4 | 14015.4 | 14161.1 | 12611.5 | 1.837 | 1.801 | 1.712 | 0.626 | 0.621 | 0.655 | 4.36 | 3.99 | 4.21 | 0.591 | 0.58 | 0.529 | -2.73 | 4.55 | -2.3 | 0.5 | 0.546 | 0.53 | -3.53 | 3.3 | 2.85 | 0.527 | 0.586 | 0.599 | 3.6 | 3.52 | 2.89 | Fair_Mixed | 7366.4 | 12611.5 | 1.712 | 0.655 | 4.36 | 0.599 | 4.55 | 0.6625 | 0.8308 | 0.7485 | 0.8773 | 1 | 0.6031 | 0.7437 | 0.7623 | 0.7623 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2126 | 261.9 | 241.3 | 69.9 | 72.8 | 1 | 494.8 | 2553.6 | 56.1 | 25.2 | 79.3 | 85.1 | 72.1 | 87.6 | 37.7 | 17 | 9655 | 10000 | 9163.5 | 18120 | 19860.3 | 8030.2 | 1.877 | 1.986 | 0.876 | 0.653 | 0.574 | 0.631 | 4.25 | 3.05 | -3.54 | 0.557 | 0.589 | 0.588 | 4.04 | 3.65 | 3.18 | 0.52 | 0.601 | 0.957 | -2.57 | 2.4 | 8.12 | 0.532 | 0.537 | 0.549 | -2.78 | -3.11 | 2.93 | Critical_Bushing_TD_Cap | 9163.5 | 8030.2 | 0.876 | 0.653 | 4.25 | 0.957 | 8.12 | 0.8958 | 0.8666 | 0.7751 | 0.8378 | 0.8125 | 0.6572 | 0.6597 | 0.7881 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | PI_TV
2127 | 1531.8 | 936.9 | 142.8 | 192.7 | 34.3 | 1286.5 | 8410 | 34.6 | 46.1 | 106.3 | 103.6 | 93.2 | 116.2 | 45.1 | 31.6 | 1281 | 1478 | 2060.7 | 1517.3 | 1627.8 | 2263.2 | 1.184 | 1.101 | 1.098 | 0.94 | 0.971 | 0.99 | 8.85 | 8.83 | -9.68 | 0.88 | 0.948 | 0.8 | 7.17 | 8.25 | -5.55 | 0.88 | 0.747 | 0.818 | -9.03 | -5.97 | 7.36 | 0.924 | 0.903 | 0.832 | 8.63 | 8.04 | 7.7 | Very Poor_Mixed | 1281 | 1517.3 | 1.098 | 0.99 | 9.68 | 0.948 | 9.03 | 0.0747 | 0.6194 | 0.1492 | 0.3368 | 1 | 0.0655 | 0.1964 | 0.3293 | 0.3293 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2128 | 507.6 | 312.5 | 80.4 | 85.7 | 11.7 | 583.2 | 3952.1 | 53.4 | 27.9 | 84.6 | 82.2 | 75.4 | 86.9 | 36.6 | 17.1 | 6744 | 7792 | 7366.8 | 11242.3 | 14260.5 | 12578.1 | 1.667 | 1.83 | 1.707 | 0.594 | 0.624 | 0.594 | 3.51 | 4.26 | 3.32 | 0.543 | 0.612 | 0.568 | 2.85 | 4.05 | 4.12 | 0.564 | 0.562 | 0.589 | 3.53 | 4.31 | -2.93 | 0.613 | 0.52 | 0.53 | 3.91 | 3.83 | 3.67 | Fair_Mixed | 6744 | 11242.3 | 1.667 | 0.624 | 4.26 | 0.613 | 4.31 | 0.631 | 0.825 | 0.7368 | 0.8349 | 1 | 0.6678 | 0.6899 | 0.7498 | 0.7498 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2129 | 501 | 349.6 | 85.4 | 84.5 | 2.8 | 611.1 | 3764.1 | 57.5 | 24.2 | 77.1 | 76.9 | 70.3 | 82.8 | 35.2 | 25.3 | 9551 | 8330.9 | 8567.1 | 18773.4 | 15060.4 | 15329.3 | 1.966 | 1.808 | 1.789 | 0.515 | 0.537 | 0.53 | 2.39 | 2.43 | 2.67 | 0.561 | 0.593 | 0.564 | 2.44 | 2.81 | 2.92 | 0.566 | 0.625 | 0.578 | 3.64 | 3.03 | 3.06 | 0.594 | 0.565 | 0.572 | 4.17 | 3.24 | 2.35 | Poor_Age | 8330.9 | 15060.4 | 1.789 | 0.537 | 2.67 | 0.625 | 4.17 | 0.7278 | 0.8839 | 0.922 | 0.569 | 1 | 0.8642 | 0.6877 | 0.8134 | 0.8134 | Good | 1 | 0 | No_Anomaly | 0 |  | Age_Years
2130 | 215.5 | 171.2 | 66.6 | 62.4 | 4.4 | 421.4 | 2881.2 | 57.5 | 20.8 | 75.8 | 76 | 70.7 | 80 | 35.8 | 10.7 | 8583.7 | 9785.4 | 10000 | 16232.4 | 18747.5 | 20000 | 1.891 | 1.916 | 2 | 0.598 | 0.5 | 0.535 | -2.95 | 2.11 | 2.89 | 0.505 | 0.534 | 0.571 | 2.67 | 2.99 | -2.71 | 0.553 | 0.708 | 0.532 | 3.07 | 5.02 | -2.41 | 0.5 | 0.532 | 0.546 | -2 | -2.32 | 2.69 | Fair_Bushing_TD_Cap | 8583.7 | 16232.4 | 1.891 | 0.598 | 2.95 | 0.708 | 5.02 | 0.8225 | 0.9605 | 0.9551 | 0.9909 | 1 | 0.8433 | 0.7757 | 0.8836 | 0.8836 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2131 | 686.4 | 511.5 | 96 | 109.2 | 18.1 | 750.6 | 5273.2 | 46.8 | 34.6 | 93.2 | 93.5 | 84.4 | 102.7 | 40.2 | 24.5 | 5569.7 | 6091.7 | 5677.5 | 8526.4 | 9669 | 8784.8 | 1.531 | 1.587 | 1.547 | 0.696 | 0.737 | 0.735 | 6.13 | 6.2 | 5.73 | 0.699 | 0.697 | 0.581 | 4.23 | 5.78 | 3.79 | 0.766 | 0.663 | 0.685 | 5.12 | 4.2 | 5.5 | 0.622 | 0.64 | 0.685 | 6.06 | -4.43 | 5.02 | Poor_Mixed | 5569.7 | 8526.4 | 1.531 | 0.737 | 6.2 | 0.766 | 6.06 | 0.478 | 0.7391 | 0.4392 | 0.597 | 1 | 0.4119 | 0.4839 | 0.5867 | 0.5867 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2132 | 744.6 | 436.3 | 93.5 | 84.2 | 11.6 | 720.2 | 4790.8 | 52.7 | 25.6 | 82 | 84.4 | 75.5 | 88.5 | 38.6 | 16.1 | 8116.1 | 8134.1 | 7412.9 | 14440.1 | 15188.3 | 13075.1 | 1.779 | 1.867 | 1.764 | 0.626 | 0.643 | 0.658 | 4.23 | 4.56 | 4.54 | 0.558 | 0.672 | 0.562 | -3.61 | 4.03 | 4.31 | 0.638 | 0.58 | 0.562 | 3.39 | 3.39 | 3.96 | 0.618 | 0.632 | 0.623 | 2.93 | 3.01 | 3.15 | Fair_Mixed | 7412.9 | 13075.1 | 1.764 | 0.658 | 4.56 | 0.672 | 4.31 | 0.5646 | 0.86 | 0.7199 | 0.8635 | 1 | 0.5788 | 0.6291 | 0.7138 | 0.7138 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2133 | 889.8 | 555.4 | 104.2 | 120.2 | 16.5 | 860.2 | 5005.8 | 47.2 | 33.1 | 89.7 | 90.9 | 82.1 | 96.4 | 41.4 | 26.4 | 4398 | 5749.1 | 4631 | 6226.9 | 8836.2 | 6880.4 | 1.416 | 1.537 | 1.486 | 0.78 | 0.766 | 0.776 | -5.65 | 5.98 | -6.69 | 0.639 | 0.629 | 0.678 | 4.31 | 3.64 | 5.44 | 0.644 | 0.65 | 0.68 | -4.84 | 4.43 | 4.7 | 0.603 | 0.753 | 0.612 | -4.05 | 5.4 | -4.58 | Poor_Mixed | 4398 | 6226.9 | 1.416 | 0.78 | 6.69 | 0.753 | 5.44 | 0.4391 | 0.7568 | 0.5165 | 0.5299 | 1 | 0.3634 | 0.515 | 0.5823 | 0.5823 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2134 | 276.5 | 166.6 | 68.5 | 57.7 | 3.4 | 411.6 | 2500 | 59.7 | 21.2 | 77.7 | 77.5 | 73.7 | 82.2 | 36 | 10 | 9382.4 | 10000 | 9469.5 | 17877 | 19664.5 | 18568.8 | 1.905 | 1.966 | 1.961 | 0.544 | 0.579 | 0.589 | 2.68 | 3.87 | 3.45 | 0.503 | 0.5 | 0.512 | 2.67 | -2 | 2.19 | 0.565 | 0.506 | 0.528 | 2.18 | 2.31 | -3.21 | 0.672 | 0.5 | 0.527 | -4.65 | 2.61 | 2.68 | Fair_Bushing_TD_Cap | 9382.4 | 17877 | 1.905 | 0.589 | 3.87 | 0.672 | 4.65 | 0.8431 | 0.9486 | 0.8765 | 1 | 1 | 0.7358 | 0.838 | 0.8761 | 0.8761 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2135 | 463.3 | 261.1 | 76.2 | 67.6 | 2.4 | 447.4 | 3166.2 | 22.8 | 23.9 | 75 | 75 | 70.9 | 80 | 35 | 13.1 | 7391.9 | 6731.2 | 7588.7 | 12751.5 | 11105.6 | 13353 | 1.725 | 1.65 | 1.76 | 0.54 | 0.61 | 0.546 | 2.44 | 3.09 | 3.14 | 0.53 | 0.528 | 0.986 | -2.78 | 2.96 | 9.63 | 0.608 | 0.568 | 0.569 | 4.19 | 2.23 | 4.36 | 0.625 | 0.525 | 0.604 | 2.88 | 4.44 | 3.68 | Critical_Bushing_TD_Cap | 6731.2 | 11105.6 | 1.65 | 0.61 | 3.14 | 0.986 | 9.63 | 0.8067 | 0.306 | 0.9879 | 0.9414 | 1 | 0.775 | 0.6234 | 0.765 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2136 | 156.4 | 199.9 | 69.6 | 52 | 4.1 | 364.9 | 2632.4 | 59.2 | 22.8 | 75 | 75 | 72 | 81.1 | 35 | 14.9 | 9558.4 | 9147.3 | 9250.5 | 19116.8 | 17775.8 | 17804.6 | 2 | 1.943 | 1.925 | 0.586 | 0.579 | 0.557 | -3.17 | 3.19 | 3.16 | 0.534 | 0.565 | 0.504 | 2.08 | 2.1 | 2 | 0.507 | 0.509 | 0.522 | 2.01 | 2 | -2 | 0.561 | 0.5 | 0.5 | 2.43 | 2.79 | 2 | Good_Mixed | 9147.3 | 17775.8 | 1.925 | 0.586 | 3.19 | 0.565 | 2.79 | 0.8597 | 0.9108 | 0.9716 | 0.8962 | 1 | 0.7395 | 0.8867 | 0.8893 | 0.8893 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2137 | 941.1 | 556.5 | 100.8 | 122.1 | 20.7 | 772.8 | 5494 | 47.7 | 33.4 | 90.7 | 93.4 | 83.9 | 98.8 | 39.7 | 25.2 | 7275.7 | 6553.1 | 6787.2 | 11893.5 | 10842.2 | 11178.7 | 1.635 | 1.655 | 1.647 | 0.7 | 0.732 | 0.689 | -5.63 | 5.06 | 5.4 | 0.7 | 0.692 | 0.761 | 5.32 | 4.7 | 4.59 | 0.703 | 0.728 | 0.641 | 4.27 | 3.92 | 4.45 | 0.628 | 0.714 | 0.69 | 5.43 | 5.08 | 5.56 | Poor_Mixed | 6553.1 | 10842.2 | 1.635 | 0.732 | 5.63 | 0.761 | 5.56 | 0.416 | 0.7532 | 0.4817 | 0.5725 | 1 | 0.4625 | 0.4552 | 0.5779 | 0.5779 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2138 | 182 | 176.9 | 65 | 50 | 1 | 370 | 2500 | 58.8 | 21 | 78.1 | 80.2 | 71.4 | 80.6 | 35 | 13.7 | 8330.2 | 9770.2 | 8397.8 | 15808.5 | 19540.3 | 15326.6 | 1.898 | 2 | 1.825 | 0.546 | 0.533 | 0.514 | -2.17 | 2.36 | 2.4 | 0.501 | 0.5 | 0.5 | -2.45 | 2.31 | 2.13 | 0.51 | 0.521 | 0.5 | -3.02 | 2.09 | -2.07 | 0.516 | 0.506 | 0.505 | 2 | 2.36 | -2.56 | Good_Mixed | 8330.2 | 15326.6 | 1.825 | 0.546 | 2.4 | 0.521 | 3.02 | 0.9761 | 0.9543 | 0.8794 | 0.9269 | 1 | 0.8724 | 0.9282 | 0.942 | 0.942 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_LV
2139 | 1472.7 | 875 | 137.4 | 182.2 | 34.3 | 1172.8 | 7758.8 | 34.1 | 46.6 | 105.4 | 104.7 | 95.2 | 112.2 | 43.9 | 30.6 | 1379.4 | 2360.4 | 1281.5 | 1546.4 | 2865.6 | 1403.8 | 1.121 | 1.214 | 1.095 | 0.923 | 0.967 | 0.898 | 8.68 | -8.82 | 8.28 | 0.793 | 0.841 | 0.863 | 6.94 | 6.75 | 7.61 | 0.927 | 0.936 | 0.904 | 7.05 | -5.96 | 5.53 | 0.8 | 0.875 | 0.715 | -7.74 | 8.11 | 7.41 | Very Poor_Mixed | 1281.5 | 1403.8 | 1.095 | 0.967 | 8.82 | 0.936 | 8.11 | 0.1196 | 0.6147 | 0.1656 | 0.3749 | 1 | 0.1175 | 0.2212 | 0.3552 | 0.3552 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2140 | 910.3 | 492.4 | 102.8 | 126.7 | 20.1 | 863.2 | 5657.4 | 43.9 | 34.4 | 91.4 | 92.1 | 81.8 | 96.2 | 39.3 | 25 | 4742 | 5750 | 5137.9 | 7250.3 | 8849.7 | 7844 | 1.529 | 1.539 | 1.527 | 0.726 | 0.744 | 0.742 | 6.36 | 5.95 | 5.43 | 0.64 | 0.654 | 0.655 | -4.45 | 3.47 | -3.8 | 0.765 | 0.68 | 0.659 | -5.55 | -5.97 | 4.96 | 0.688 | 0.672 | 0.635 | 4.68 | 4.52 | 4.74 | Poor_Mixed | 4742 | 7250.3 | 1.527 | 0.744 | 6.36 | 0.765 | 5.97 | 0.4102 | 0.7414 | 0.5142 | 0.5796 | 1 | 0.4048 | 0.4883 | 0.5765 | 0.5765 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2141 | 318.2 | 176.6 | 81.3 | 57.4 | 3.3 | 580.8 | 3143.5 | 55.6 | 25.5 | 83.1 | 82.2 | 72.4 | 86.6 | 36.4 | 16.5 | 1534.8 | 228.4 | 2442.1 | 1565.4 | 327.2 | 2613.9 | 1.02 | 1.433 | 1.07 | 0.658 | 0.698 | 0.737 | -5.15 | 5.33 | 6.03 | 0.583 | 0.631 | 0.553 | 2.32 | 2.93 | 4.04 | 0.557 | 0.652 | 0.633 | -2.98 | 3.5 | -2.68 | 0.676 | 0.592 | 0.605 | 4.07 | 3.18 | -3.6 | Critical_IR_PI | 228.4 | 327.2 | 1.02 | 0.737 | 6.03 | 0.676 | 4.07 | 0.8026 | 0.8617 | 0.7749 | 0.8522 | 0.85 | 0.4641 | 0.6353 | 0.7395 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2142 | 763.7 | 583.3 | 104.9 | 110 | 15.9 | 768.9 | 5722.4 | 44.7 | 32.1 | 93 | 92 | 81.8 | 98 | 40.4 | 25 | 7108.7 | 5355.5 | 6767 | 11879 | 8559.1 | 10256.1 | 1.671 | 1.598 | 1.516 | 0.745 | 0.762 | 0.717 | 6.51 | 6.39 | -6.02 | 0.755 | 0.705 | 0.668 | 5.26 | -5.32 | -4.08 | 0.652 | 0.75 | 0.651 | 2.99 | 4.23 | 5.74 | 0.727 | 0.629 | 0.651 | 4.81 | -4.52 | 4.49 | Poor_Mixed | 5355.5 | 8559.1 | 1.516 | 0.762 | 6.51 | 0.755 | 5.74 | 0.4636 | 0.7691 | 0.4886 | 0.5796 | 1 | 0.38 | 0.4734 | 0.5844 | 0.5844 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2143 | 100 | 120 | 66.4 | 50.9 | 1.6 | 350 | 2500 | 50.9 | 31.9 | 76.7 | 77.8 | 70.4 | 82.4 | 35.2 | 14.5 | 9101.9 | 7945.5 | 7735.3 | 17014.9 | 14566.3 | 13299.3 | 1.869 | 1.833 | 1.719 | 0.566 | 0.598 | 0.51 | -3.91 | 3.3 | 2.13 | 0.518 | 0.521 | 0.5 | 2 | 2.42 | 2.45 | 0.5 | 0.536 | 0.582 | 2.61 | 2.03 | 2.02 | 0.53 | 0.55 | 0.543 | 2 | 2.07 | 2.5 | Fair_Oil | 7735.3 | 13299.3 | 1.719 | 0.598 | 3.91 | 0.582 | 2.61 | 0.944 | 0.7716 | 0.9176 | 0.9067 | 1 | 0.7793 | 0.8524 | 0.8882 | 0.8882 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2144 | 100 | 135.1 | 65 | 53.1 | 1 | 378.5 | 2500 | 56.6 | 23 | 77.3 | 75 | 72.3 | 83.8 | 36.5 | 12.7 | 10000 | 9717 | 10000 | 19222.8 | 18918.7 | 20000 | 1.922 | 1.947 | 2 | 0.517 | 0.562 | 0.54 | 2.63 | 2.96 | 2.72 | 0.528 | 0.555 | 0.55 | 2.06 | -2.85 | -2.6 | 0.587 | 0.523 | 0.543 | 3.24 | 2 | 2.68 | 0.542 | 0.519 | 0.5 | 3.01 | 3.24 | 2 | Good_Mixed | 9717 | 18918.7 | 1.922 | 0.562 | 2.96 | 0.587 | 3.24 | 0.9814 | 0.9067 | 0.9166 | 0.9507 | 1 | 0.8229 | 0.8056 | 0.9136 | 0.9136 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2145 | 143.4 | 166.9 | 65 | 71.7 | 4.2 | 379.2 | 2738.3 | 58.3 | 22.9 | 77.7 | 77.1 | 70.3 | 80.8 | 35.7 | 17.1 | 8621.4 | 9934.8 | 9509.7 | 16123.1 | 18969.3 | 18917.5 | 1.87 | 1.909 | 1.989 | 0.548 | 0.542 | 0.527 | -2.36 | 2.8 | -2.54 | 0.549 | 0.5 | 0.505 | 2 | -2.02 | 2 | 0.5 | 0.542 | 0.563 | 2.06 | -2.93 | 2 | 0.537 | 0.511 | 0.554 | -2 | 3.03 | 2.5 | Good_Mixed | 8621.4 | 16123.1 | 1.87 | 0.548 | 2.8 | 0.563 | 3.03 | 0.8309 | 0.9088 | 0.9215 | 0.8349 | 1 | 0.8362 | 0.8594 | 0.8824 | 0.8824 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2146 | 1729.8 | 877 | 136.9 | 180.8 | 31.5 | 1301.4 | 8427.4 | 36.8 | 43.5 | 105.6 | 104.7 | 93 | 116.2 | 44.8 | 33.8 | 1024.9 | 928.4 | 2117.2 | 1200 | 1200 | 2271.5 | 1.171 | 1.293 | 1.073 | 0.906 | 0.88 | 0.891 | 8.74 | 7.57 | 7.76 | 0.745 | 0.779 | 0.767 | 8.14 | 5.52 | 5.15 | 0.906 | 0.837 | 0.84 | 6.37 | 7.1 | 6.87 | 0.893 | 0.662 | 0.814 | 5.03 | 6.41 | 5.8 | Very Poor_Mixed | 928.4 | 1200 | 1.073 | 0.906 | 8.74 | 0.906 | 8.14 | 0.092 | 0.6445 | 0.1502 | 0.2513 | 1 | 0.1723 | 0.2902 | 0.3643 | 0.3643 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2147 | 1438.4 | 793.7 | 134.7 | 165.7 | 31.8 | 1216 | 7813.8 | 33.5 | 42.7 | 103.4 | 101.4 | 90.9 | 114.3 | 43 | 29.3 | 2946 | 2330.1 | 2723.6 | 3319.5 | 2839.5 | 3132 | 1.127 | 1.219 | 1.15 | 0.975 | 0.921 | 0.972 | 9.21 | 9.51 | 9.84 | 0.738 | 0.884 | 0.767 | 8.68 | 5.66 | 7.72 | 0.778 | 0.773 | 0.833 | 8.43 | -5.44 | 5.59 | 0.832 | 0.733 | 0.777 | 7.09 | -5.63 | 7.56 | Very Poor_Mixed | 2330.1 | 2839.5 | 1.127 | 0.975 | 9.84 | 0.884 | 8.68 | 0.1524 | 0.6524 | 0.2156 | 0.4238 | 1 | 0.0528 | 0.2817 | 0.3772 | 0.3772 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2148 | 316.3 | 206 | 70.1 | 57 | 3.1 | 402.2 | 2987.2 | 59.2 | 21.2 | 80.7 | 77.9 | 74.7 | 87.1 | 35.3 | 10 | 8107 | 9206.3 | 8397.1 | 15182.4 | 16967.4 | 15410.4 | 1.873 | 1.843 | 1.835 | 0.615 | 0.6 | 0.604 | 3.99 | 3.74 | 3.15 | 0.517 | 0.517 | 0.519 | 2 | -2.48 | 2.53 | 0.549 | 0.563 | 0.52 | 3.04 | -3.66 | 2.19 | 0.825 | 0.5 | 0.549 | 6.22 | 3.13 | 3.53 | Poor_Bushing_TD_Cap | 8107 | 15182.4 | 1.835 | 0.615 | 3.99 | 0.825 | 6.22 | 0.8402 | 0.9486 | 0.8155 | 1 | 1 | 0.669 | 0.7592 | 0.8458 | 0.8458 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2149 | 495.6 | 297.2 | 90.9 | 141.7 | 4.5 | 583.6 | 4141.5 | 56.3 | 21.5 | 109.3 | 109.1 | 96.3 | 119.1 | 44.7 | 19.1 | 8926.2 | 9142.6 | 9691.9 | 16684.2 | 17170.8 | 19383.7 | 1.869 | 1.878 | 2 | 0.597 | 0.629 | 0.66 | 4.21 | 4.05 | 5.7 | 0.569 | 0.585 | 0.577 | 3.85 | -3.06 | -3.35 | 0.672 | 0.581 | 0.611 | -3.34 | -4.5 | -13.97 | 0.639 | 0.596 | 0.559 | 3.59 | 4.18 | 3.83 | Critical_Thermal | 8926.2 | 16684.2 | 1.869 | 0.66 | 5.7 | 0.672 | 13.97 | 0.6443 | 0.9406 | 0.0738 | 0.7749 | 1 | 0.583 | 0.6064 | 0.6709 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_CapChange_pct>=10% abs: critical bushing capacitance change | C2H2
2150 | 339.7 | 241.5 | 87.2 | 88.9 | 4.4 | 609.4 | 3572.8 | 48 | 30.8 | 80.5 | 77.6 | 73.2 | 86.3 | 37.5 | 18.5 | 338.8 | 8224.1 | 8737.7 | 587.9 | 14814.9 | 15205.6 | 1.735 | 1.801 | 1.74 | 0.99 | 0.99 | 0.965 | -8.93 | 9.25 | 9.6 | 0.61 | 0.588 | 0.612 | 3.29 | 2.86 | 4.13 | 0.599 | 0.642 | 0.627 | 3.59 | 4.48 | 2.67 | 0.629 | 0.582 | 0.6 | 3.16 | 3.74 | -3.31 | Critical_Winding_TD_Cap | 338.8 | 587.9 | 1.735 | 0.99 | 9.6 | 0.642 | 4.48 | 0.7222 | 0.7855 | 0.8255 | 0.7933 | 0.85 | 0.0487 | 0.6204 | 0.6515 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2151 | 1498.6 | 850.5 | 137.6 | 169.7 | 31.4 | 1173.1 | 8122.9 | 33.5 | 46.2 | 104.8 | 104.4 | 92 | 112 | 43.8 | 31.4 | 3045.6 | 1290.1 | 1386.4 | 3459.3 | 1415.7 | 1720.9 | 1.136 | 1.097 | 1.241 | 0.902 | 0.969 | 0.936 | -8.3 | -9.14 | 9.03 | 0.796 | 0.899 | 0.803 | -8.04 | 8.46 | 8.24 | 0.769 | 0.883 | 0.799 | 6.63 | 9.17 | -7.94 | 0.768 | 0.667 | 0.837 | 7.13 | 8.34 | 9.13 | Very Poor_Mixed | 1290.1 | 1415.7 | 1.097 | 0.969 | 9.14 | 0.899 | 9.17 | 0.1387 | 0.6184 | 0.1903 | 0.3444 | 1 | 0.1015 | 0.2307 | 0.3609 | 0.3609 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2152 | 898.3 | 476.2 | 105.2 | 120.2 | 19.7 | 862.4 | 5481.8 | 46.7 | 33 | 90.9 | 88 | 80.6 | 98.7 | 39.5 | 24.1 | 6075.3 | 4766.7 | 4813 | 9603.4 | 7264.7 | 6895.7 | 1.581 | 1.524 | 1.433 | 0.735 | 0.665 | 0.736 | 5.99 | -4.92 | -5.93 | 0.672 | 0.634 | 0.684 | 4.93 | 5.42 | 5.84 | 0.722 | 0.738 | 0.688 | 4.7 | 4.53 | 4.13 | 0.686 | 0.614 | 0.647 | 4.76 | 5 | 3.82 | Poor_Mixed | 4766.7 | 6895.7 | 1.433 | 0.736 | 5.99 | 0.738 | 5.84 | 0.4217 | 0.7581 | 0.5386 | 0.6108 | 1 | 0.4449 | 0.4792 | 0.5893 | 0.5893 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2153 | 350 | 235.5 | 71.9 | 64.4 | 1 | 540.7 | 3579.1 | 46.8 | 30.6 | 77.2 | 76.5 | 70.3 | 83.8 | 36.2 | 10.1 | 7969.5 | 7946.5 | 7522.2 | 14429 | 13908.7 | 12642.4 | 1.811 | 1.75 | 1.681 | 0.577 | 0.559 | 0.567 | 3.42 | 3.29 | 4.05 | 0.525 | 0.547 | 0.549 | -3.26 | 3.12 | 2.58 | 0.525 | 0.587 | 0.517 | 2.94 | 2.1 | 2.27 | 0.5 | 0.532 | 0.569 | 3.5 | 2.62 | 3.04 | Poor_Oil | 7522.2 | 12642.4 | 1.681 | 0.577 | 4.05 | 0.587 | 3.5 | 0.8855 | 0.7881 | 0.9162 | 0.9992 | 1 | 0.7218 | 0.7946 | 0.8616 | 0.8616 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2154 | 713 | 530 | 103.7 | 118.5 | 17.2 | 783.6 | 5143.2 | 45.9 | 34.8 | 92 | 93.8 | 80.9 | 99.2 | 40.2 | 24.4 | 5981.8 | 5648.6 | 5418 | 8980.6 | 9162.9 | 7817 | 1.501 | 1.622 | 1.443 | 0.753 | 0.771 | 0.748 | 6.09 | 6.14 | 5.07 | 0.715 | 0.691 | 0.666 | 4.76 | 3.76 | 4.22 | 0.654 | 0.673 | 0.626 | 5.69 | 4.24 | 3.95 | 0.761 | 0.641 | 0.629 | 6.49 | 4.79 | -3.72 | Poor_Mixed | 5418 | 7817 | 1.443 | 0.771 | 6.14 | 0.761 | 6.49 | 0.4618 | 0.7368 | 0.4847 | 0.6005 | 1 | 0.396 | 0.4903 | 0.586 | 0.586 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2155 | 1093 | 513.2 | 106.1 | 124.4 | 19.8 | 839.8 | 5170.7 | 48.6 | 31.1 | 92.4 | 91 | 83 | 98 | 40.3 | 27.2 | 5760.4 | 5676.8 | 5149.1 | 9371.7 | 8714.6 | 7591.3 | 1.627 | 1.535 | 1.474 | 0.732 | 0.672 | 0.698 | -5.66 | 5.54 | -4.46 | 0.682 | 0.683 | 0.629 | 3.42 | -4.64 | 3.19 | 0.624 | 0.613 | 0.649 | -5.17 | -4.64 | 4.57 | 0.652 | 0.641 | 0.683 | 4.84 | -4.18 | 4.72 | Poor_Mixed | 5149.1 | 7591.3 | 1.474 | 0.732 | 5.66 | 0.683 | 5.17 | 0.4032 | 0.7817 | 0.4919 | 0.5011 | 1 | 0.477 | 0.5266 | 0.5904 | 0.5904 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2156 | 830.7 | 503.8 | 112.1 | 128.2 | 18.6 | 890.4 | 5417.4 | 48.1 | 32.1 | 90 | 92.1 | 80.6 | 99.2 | 39.4 | 24.3 | 7584 | 8242.5 | 6714.9 | 12904.1 | 14248.6 | 10400.8 | 1.701 | 1.729 | 1.549 | 0.679 | 0.702 | 0.691 | -5.48 | 5.59 | -4.9 | 0.727 | 0.714 | 0.675 | 5.01 | 4.11 | 5.08 | 0.739 | 0.733 | 0.708 | 4.59 | 4.21 | 3.81 | 0.647 | 0.688 | 0.695 | 5.37 | -4.18 | 3.66 | Poor_Mixed | 6714.9 | 10400.8 | 1.549 | 0.702 | 5.59 | 0.739 | 5.37 | 0.4151 | 0.7691 | 0.5155 | 0.6039 | 1 | 0.4798 | 0.459 | 0.5876 | 0.5876 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2157 | 689.6 | 484.7 | 93.1 | 102.7 | 17.1 | 690.9 | 4707.7 | 50.5 | 27.8 | 82.6 | 87.3 | 78 | 90.9 | 38.4 | 20.3 | 6649.1 | 6680.2 | 6162.6 | 11064.3 | 11123.2 | 10457.5 | 1.664 | 1.665 | 1.697 | 0.621 | 0.621 | 0.643 | 4.09 | -4.69 | -4.21 | 0.627 | 0.681 | 0.642 | 3.47 | 4.14 | 3.33 | 0.637 | 0.615 | 0.597 | 3.06 | 4.48 | 3.93 | 0.585 | 0.635 | 0.615 | -2.5 | 3.91 | 4 | Fair_Mixed | 6162.6 | 10457.5 | 1.664 | 0.643 | 4.69 | 0.681 | 4.48 | 0.5091 | 0.8264 | 0.6656 | 0.7372 | 1 | 0.6007 | 0.59 | 0.6802 | 0.6802 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2158 | 397.9 | 241.9 | 80.1 | 80.6 | 8.1 | 504.8 | 3388.5 | 52.8 | 28 | 81.5 | 82.4 | 76.7 | 87.3 | 37.3 | 15.6 | 8189.3 | 8466.6 | 8265.9 | 14111.5 | 15561 | 14467.6 | 1.723 | 1.838 | 1.75 | 0.61 | 0.571 | 0.591 | 3.98 | 3.39 | -4.08 | 0.578 | 0.586 | 0.557 | 3.12 | 2.09 | -2.33 | 0.602 | 0.599 | 0.596 | 4.02 | -3.32 | 3.54 | 0.621 | 0.623 | 0.583 | 3.2 | 3.83 | 3.62 | Fair_Mixed | 8189.3 | 14111.5 | 1.723 | 0.61 | 4.08 | 0.623 | 4.02 | 0.7032 | 0.8235 | 0.744 | 0.8773 | 1 | 0.677 | 0.6574 | 0.766 | 0.766 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2159 | 903.7 | 578.1 | 106.1 | 125.4 | 18.2 | 859.8 | 5346.2 | 45.6 | 33.2 | 90.5 | 88.8 | 82.9 | 100.3 | 38.7 | 25.5 | 6598.7 | 5667.2 | 6300.3 | 10641.5 | 8831.4 | 10476.5 | 1.613 | 1.558 | 1.663 | 0.75 | 0.821 | 0.739 | 6.59 | 6.63 | -5.9 | 0.757 | 0.747 | 0.668 | 5.26 | -4.9 | 5.26 | 0.793 | 0.67 | 0.679 | 4.27 | -4.5 | 5.35 | 0.735 | 0.804 | 0.613 | 4.72 | -4.59 | -6.68 | Poor_Mixed | 5667.2 | 8831.4 | 1.558 | 0.821 | 6.63 | 0.804 | 6.68 | 0.415 | 0.7556 | 0.5179 | 0.562 | 1 | 0.3529 | 0.4221 | 0.5597 | 0.5597 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2160 | 768.7 | 462.7 | 94.9 | 97.6 | 12.7 | 750.8 | 5120.7 | 57 | 24.1 | 77.1 | 75 | 70.2 | 80 | 35.8 | 11.4 | 8741.9 | 8652 | 7919.6 | 16416.5 | 16550.4 | 14310.8 | 1.878 | 1.913 | 1.807 | 0.582 | 0.559 | 0.57 | 2.31 | -2.86 | -3.72 | 0.5 | 0.577 | 0.566 | 2.36 | 3.7 | 2.61 | 0.531 | 0.567 | 0.565 | 3 | -3.09 | 3.01 | 0.559 | 0.539 | 0.569 | 3.3 | 2.56 | 2.19 | Poor_DGA | 7919.6 | 14310.8 | 1.807 | 0.582 | 3.72 | 0.577 | 3.7 | 0.528 | 0.8857 | 0.9631 | 0.9783 | 1 | 0.7603 | 0.7599 | 0.7867 | 0.7867 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2161 | 904.1 | 501.2 | 102.1 | 123.3 | 15.2 | 875.8 | 5599.3 | 44.6 | 34.8 | 93.2 | 93.2 | 82.9 | 100.6 | 39.8 | 26 | 5736.7 | 5683.7 | 6818.3 | 9456.7 | 8921.3 | 10818.3 | 1.648 | 1.57 | 1.587 | 0.8 | 0.78 | 0.725 | 6.35 | 5.79 | 5.9 | 0.635 | 0.743 | 0.647 | 4.24 | 5.55 | 5.66 | 0.61 | 0.64 | 0.653 | -4.48 | 5.36 | 4.54 | 0.723 | 0.595 | 0.75 | -4.8 | 4.53 | 4.41 | Poor_Mixed | 5683.7 | 8921.3 | 1.57 | 0.8 | 6.35 | 0.75 | 5.66 | 0.4433 | 0.7368 | 0.4635 | 0.5442 | 1 | 0.3736 | 0.4922 | 0.5737 | 0.5737 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2162 | 942 | 500.1 | 103.2 | 116 | 19.6 | 909.2 | 5509.2 | 47.4 | 33.9 | 91.7 | 91.2 | 82.1 | 98.4 | 39.6 | 22.4 | 6667.2 | 5914.3 | 4950.5 | 10870.3 | 8801.2 | 7553.3 | 1.63 | 1.488 | 1.526 | 0.721 | 0.736 | 0.747 | 6.17 | 5.4 | 6.15 | 0.602 | 0.697 | 0.614 | 3.81 | 4.06 | -5.49 | 0.682 | 0.622 | 0.661 | 5.06 | 5.31 | 4.99 | 0.616 | 0.644 | 0.644 | -4.72 | 4.46 | 3.97 | Poor_Mixed | 4950.5 | 7553.3 | 1.488 | 0.747 | 6.17 | 0.697 | 5.49 | 0.4157 | 0.7473 | 0.5032 | 0.6686 | 1 | 0.4075 | 0.5275 | 0.5894 | 0.5894 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2163 | 1103.2 | 744.1 | 121.1 | 144.6 | 18.8 | 1039.4 | 6520.2 | 60 | 20 | 75 | 76.6 | 70.8 | 80 | 35.4 | 10.7 | 8538.2 | 9341.8 | 8141.3 | 15145.5 | 17909.5 | 14723.3 | 1.774 | 1.917 | 1.808 | 0.523 | 0.554 | 0.525 | 2.93 | 2 | 2.46 | 0.523 | 0.5 | 0.533 | 2.43 | 2.58 | -2.19 | 0.511 | 0.51 | 0.517 | -2.34 | 2 | -2.72 | 0.549 | 0.517 | 0.517 | -2.49 | 2.01 | -2 | Poor_DGA | 8141.3 | 14723.3 | 1.774 | 0.554 | 2.93 | 0.549 | 2.72 | 0.3144 | 1 | 0.963 | 0.9909 | 1 | 0.8568 | 0.8714 | 0.7812 | 0.7812 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2164 | 787.7 | 527.3 | 101.6 | 114.3 | 20.9 | 837.5 | 5218.2 | 47.5 | 29.9 | 89.4 | 91.5 | 83.1 | 96.4 | 39.4 | 22.3 | 6489.8 | 5884.1 | 5425.7 | 10298.6 | 9124.5 | 8574.1 | 1.587 | 1.551 | 1.58 | 0.71 | 0.724 | 0.743 | -5.65 | 5.95 | 6.27 | 0.626 | 0.634 | 0.623 | 4.46 | -3.92 | -3.15 | 0.712 | 0.67 | 0.693 | -4.72 | 3.55 | 4.74 | 0.648 | 0.687 | 0.656 | 4.16 | -4.35 | 5.31 | Poor_Mixed | 5425.7 | 8574.1 | 1.551 | 0.743 | 6.27 | 0.712 | 5.31 | 0.4319 | 0.7973 | 0.5213 | 0.6719 | 1 | 0.4126 | 0.5177 | 0.6003 | 0.6003 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2165 | 1431.2 | 817 | 135.4 | 175 | 34.3 | 1285.7 | 7788.8 | 34.4 | 46.5 | 104.2 | 109.3 | 92.4 | 114.1 | 44.4 | 32.4 | 2149.6 | 2147.8 | 1723.6 | 2657.8 | 2546.4 | 1954.6 | 1.236 | 1.186 | 1.134 | 0.946 | 0.957 | 0.899 | 8.78 | 8.93 | 8.15 | 0.848 | 0.775 | 0.769 | 6.76 | 7.79 | -8.37 | 0.946 | 0.844 | 0.739 | -8.03 | -6.74 | -9.35 | 0.83 | 0.884 | 0.758 | 5.81 | 7.69 | 6.62 | Very Poor_Mixed | 1723.6 | 1954.6 | 1.134 | 0.957 | 8.93 | 0.946 | 9.35 | 0.1237 | 0.6156 | 0.1496 | 0.3059 | 1 | 0.1129 | 0.2331 | 0.3528 | 0.3528 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2166 | 836.9 | 600.3 | 108 | 122.1 | 17 | 798.8 | 5444.8 | 46.8 | 32.3 | 86.4 | 87.8 | 78.5 | 95.4 | 39.4 | 23.3 | 6114.7 | 6449.1 | 5676.7 | 9747.8 | 10634 | 8610.3 | 1.594 | 1.649 | 1.517 | 0.755 | 0.732 | 0.724 | 6.54 | 5.92 | 5.24 | 0.637 | 0.613 | 0.677 | 4.42 | 4.85 | 5.72 | 0.633 | 0.686 | 0.663 | -4.36 | 4.7 | 4.65 | 0.686 | 0.736 | 0.671 | 4.96 | 4.65 | -4.54 | Poor_Mixed | 5676.7 | 8610.3 | 1.517 | 0.755 | 6.54 | 0.736 | 5.72 | 0.4337 | 0.7666 | 0.6018 | 0.6382 | 1 | 0.406 | 0.4913 | 0.5978 | 0.5978 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2167 | 1010.4 | 588.9 | 113.4 | 131.6 | 23.4 | 935.7 | 5974.3 | 57.2 | 20.9 | 78.9 | 75 | 70.1 | 80 | 36 | 13.1 | 9256.1 | 8834.2 | 8703.7 | 16728.4 | 16173.2 | 16352.5 | 1.807 | 1.831 | 1.879 | 0.544 | 0.565 | 0.561 | -2.38 | 3 | 2.52 | 0.5 | 0.528 | 0.547 | 2.22 | 2.64 | -2 | 0.571 | 0.517 | 0.535 | 2.1 | 2.74 | -3.24 | 0.551 | 0.5 | 0.555 | -2.95 | 2.84 | -2.51 | Poor_DGA | 8703.7 | 16173.2 | 1.807 | 0.565 | 3 | 0.571 | 3.24 | 0.3486 | 0.9574 | 0.9458 | 0.9414 | 1 | 0.8022 | 0.8259 | 0.7647 | 0.7647 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2168 | 1361.2 | 807.5 | 131.6 | 166.2 | 28.1 | 1214.2 | 8024.7 | 38.2 | 41.9 | 104.1 | 102.6 | 91.8 | 111 | 43.4 | 30.9 | 3076.4 | 1955.1 | 2611.9 | 3680.8 | 2233.8 | 2984.8 | 1.196 | 1.143 | 1.143 | 0.934 | 0.867 | 0.961 | -9.36 | 7.76 | -8.88 | 0.849 | 0.872 | 0.899 | 5.32 | -8.23 | 6.06 | 0.844 | 0.78 | 0.834 | -7.76 | 7 | 7.48 | 0.934 | 0.898 | 0.931 | 7.13 | 5.89 | 7.41 | Very Poor_Mixed | 1955.1 | 2233.8 | 1.143 | 0.961 | 9.36 | 0.934 | 8.23 | 0.1731 | 0.6604 | 0.2133 | 0.3635 | 1 | 0.1202 | 0.2042 | 0.3756 | 0.3756 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2169 | 1496 | 868 | 135 | 180.1 | 27.9 | 1204 | 7651.3 | 35.9 | 45.6 | 101.9 | 104.6 | 91.6 | 112.2 | 42.8 | 30.7 | 1648.1 | 690 | 2584.4 | 1952.5 | 1200 | 2935.9 | 1.185 | 1.739 | 1.136 | 0.865 | 0.87 | 0.869 | 8.01 | -7.72 | 7.64 | 0.893 | 0.725 | 0.948 | 6.61 | 6.1 | -7.63 | 0.797 | 0.739 | 0.74 | 5.6 | 7.15 | 6.19 | 0.924 | 0.793 | 0.85 | 6.41 | 5.59 | 6.91 | Very Poor_Mixed | 690 | 1200 | 1.136 | 0.87 | 8.01 | 0.948 | 7.63 | 0.1493 | 0.6241 | 0.2139 | 0.3711 | 1 | 0.2016 | 0.2656 | 0.3882 | 0.3882 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2170 | 235.8 | 155.1 | 70.1 | 157 | 2.8 | 383.7 | 3560.3 | 49.1 | 26.8 | 107.5 | 106.8 | 97.6 | 117.3 | 45 | 11.5 | 7771.2 | 7845.5 | 8383.1 | 14184.2 | 14249.3 | 15537.2 | 1.825 | 1.816 | 1.853 | 0.597 | 0.638 | 0.642 | 4.78 | 4.31 | -3.71 | 0.632 | 0.558 | 0.595 | -4 | 3.55 | -3.51 | 0.594 | 0.584 | 0.609 | -2.63 | 3.15 | -24.86 | 0.553 | 0.573 | 0.61 | 3.01 | -2.99 | 3.99 | Critical_Thermal | 7771.2 | 14184.2 | 1.816 | 0.642 | 4.78 | 0.632 | 24.86 | 0.7525 | 0.8412 | 0.0958 | 0.9764 | 1 | 0.6083 | 0.6333 | 0.7066 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_CapChange_pct>=10% abs: critical bushing capacitance change | C2H4
2171 | 1508.9 | 904.9 | 145.1 | 176.8 | 34.3 | 1305.5 | 8223.5 | 36.3 | 45.6 | 104.8 | 103.1 | 90.7 | 114.9 | 44.2 | 31.7 | 3520.6 | 1754.1 | 2295.2 | 4394.5 | 1841.8 | 2678.1 | 1.248 | 1.05 | 1.167 | 0.926 | 0.877 | 0.871 | 8.83 | 8.33 | 8.48 | 0.886 | 0.762 | 0.924 | -6.36 | 7.47 | 9.55 | 0.793 | 0.813 | 0.946 | 9.33 | -6.29 | 5.61 | 0.86 | 0.878 | 0.709 | 6.39 | 7.34 | 6.94 | Very Poor_Mixed | 1754.1 | 1841.8 | 1.05 | 0.926 | 8.83 | 0.946 | 9.55 | 0.0915 | 0.6241 | 0.1876 | 0.3329 | 1 | 0.1462 | 0.2228 | 0.3538 | 0.3538 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2172 | 845.4 | 499.6 | 99.6 | 127.1 | 19.6 | 779.7 | 5805.6 | 44.2 | 34.8 | 91.7 | 89.5 | 82.5 | 98.8 | 39.5 | 24.7 | 6117.5 | 6499.5 | 5006.5 | 9520.9 | 10876 | 7665 | 1.556 | 1.673 | 1.531 | 0.717 | 0.77 | 0.692 | 4.59 | -5.78 | 5.6 | 0.651 | 0.696 | 0.669 | 4.85 | 4.18 | 4.37 | 0.645 | 0.645 | 0.656 | 3.75 | 5.72 | 4.55 | 0.702 | 0.574 | 0.627 | 5.95 | 4.67 | 3.95 | Poor_Mixed | 5006.5 | 7665 | 1.531 | 0.77 | 5.78 | 0.702 | 5.95 | 0.4282 | 0.7368 | 0.5105 | 0.59 | 1 | 0.4482 | 0.5158 | 0.5916 | 0.5916 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2173 | 529.3 | 339.5 | 86.7 | 88.2 | 1 | 537.7 | 3773.5 | 53.1 | 28.3 | 81.4 | 82 | 73.4 | 89.3 | 37.9 | 16.7 | 863 | 690 | 690 | 487.3 | 744.1 | 703.8 | 0.565 | 1.078 | 1.02 | 0.671 | 0.737 | 0.758 | 5.04 | 5.77 | 5.71 | 0.564 | 0.519 | 0.538 | 2 | 2.18 | 2.78 | 0.562 | 0.524 | 0.566 | 3.09 | 2.29 | -2.65 | 0.508 | 0.515 | 0.524 | 2.06 | 2.75 | -2.39 | Critical_IR_PI | 690 | 487.3 | 0.565 | 0.758 | 5.77 | 0.566 | 3.09 | 0.8173 | 0.8193 | 0.7599 | 0.8465 | 0.5938 | 0.4419 | 0.8153 | 0.7246 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_HV
2174 | 1653.6 | 952.5 | 138.3 | 185.7 | 34.3 | 1379 | 8577.5 | 34.5 | 44.8 | 106.1 | 105.1 | 94 | 112.7 | 43.3 | 30.9 | 690 | 1292 | 787 | 1200 | 1383 | 1200 | 1.739 | 1.07 | 1.525 | 0.99 | 0.99 | 0.918 | 9.84 | 8.41 | 9.19 | 0.913 | 0.821 | 0.809 | -7.52 | 6.77 | 6.01 | 0.835 | 0.845 | 0.799 | 7.64 | 8.76 | -7.05 | 0.815 | 0.813 | 0.845 | -7.91 | 8.5 | 6.49 | Very Poor_Mixed | 690 | 1200 | 1.07 | 0.99 | 9.84 | 0.913 | 8.76 | 0.0614 | 0.6318 | 0.168 | 0.3635 | 1 | 0.0651 | 0.2223 | 0.3353 | 0.3353 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2175 | 1514.9 | 895.7 | 139.7 | 179.5 | 34.3 | 1227.2 | 7936.2 | 34.1 | 45.2 | 102.2 | 105.9 | 91 | 113.1 | 44.1 | 29.6 | 2376.6 | 2171.6 | 694.4 | 2729.9 | 2717.1 | 1200 | 1.149 | 1.251 | 1.728 | 0.873 | 0.821 | 0.911 | 8.26 | 7.66 | 8.49 | 0.851 | 0.815 | 0.743 | -7.32 | 7.63 | 7.84 | 0.893 | 0.74 | 0.724 | -6.25 | 8.51 | 7.09 | 0.768 | 0.915 | 0.742 | 8.16 | 8.38 | 7.84 | Very Poor_Mixed | 694.4 | 1200 | 1.149 | 0.911 | 8.49 | 0.915 | 8.51 | 0.1064 | 0.628 | 0.1946 | 0.4126 | 1 | 0.1841 | 0.2482 | 0.3725 | 0.3725 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2176 | 383.1 | 237.5 | 75.1 | 75.3 | 1.7 | 493.7 | 3296.3 | 56.8 | 23.3 | 78.1 | 79 | 73.5 | 85.6 | 37.7 | 13.2 | 9086.3 | 9059.5 | 9391.8 | 17345.2 | 17296.9 | 17328.9 | 1.909 | 1.909 | 1.845 | 0.747 | 0.755 | 0.795 | 6.36 | 6.55 | -5.47 | 0.567 | 0.625 | 0.559 | -2 | 2.41 | -2.91 | 0.554 | 0.542 | 0.616 | 2.67 | 3.07 | 2.35 | 0.534 | 0.533 | 0.616 | -2.49 | 2.55 | -3.27 | Poor_Winding_TD_Cap | 9059.5 | 17296.9 | 1.845 | 0.795 | 6.55 | 0.625 | 3.27 | 0.8193 | 0.9008 | 0.8336 | 0.939 | 1 | 0.3694 | 0.7283 | 0.786 | 0.786 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
2177 | 280.9 | 214.1 | 77.7 | 69.1 | 1.4 | 516.4 | 3407.9 | 32.3 | 45.4 | 80.7 | 82.2 | 108.7 | 88 | 37.2 | 11.6 | 4401.5 | 4781.4 | 4960 | 6204.1 | 6908.7 | 7056.9 | 1.41 | 1.445 | 1.423 | 0.66 | 0.684 | 0.673 | 5.1 | -4.68 | 4.25 | 0.605 | 0.576 | 0.603 | 3.33 | 3.66 | 3.73 | 0.65 | 0.589 | 0.664 | -3.58 | 2.97 | 3.92 | 0.588 | 0.579 | 0.595 | -2.69 | 3.03 | 3.37 | Critical_Oil | 4401.5 | 6204.1 | 1.41 | 0.684 | 5.1 | 0.664 | 3.92 | 0.8463 | 0.6261 | 0.6096 | 0.9744 | 1 | 0.5345 | 0.6328 | 0.7451 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Moisture_PPM
2178 | 1048 | 506 | 104.2 | 117.9 | 18.6 | 901.6 | 5492.8 | 57.9 | 20.2 | 77.1 | 77.1 | 73.2 | 84.3 | 36.8 | 13 | 7713.6 | 8583.7 | 7948.2 | 14119 | 15307.7 | 14812.8 | 1.83 | 1.783 | 1.864 | 0.549 | 0.503 | 0.561 | -2.93 | 2.35 | 3.42 | 0.576 | 0.554 | 0.53 | 2.01 | 2.89 | 2.73 | 0.531 | 0.602 | 0.558 | 3.06 | 2.51 | 2.91 | 0.508 | 0.553 | 0.532 | 3.12 | 2.95 | 3 | Poor_DGA | 7713.6 | 14119 | 1.783 | 0.561 | 3.42 | 0.602 | 3.12 | 0.4114 | 0.984 | 0.8767 | 0.9438 | 1 | 0.8256 | 0.7658 | 0.7692 | 0.7692 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2179 | 917.4 | 472.4 | 104.4 | 120.8 | 15.6 | 825.1 | 5104.8 | 45.4 | 33.3 | 90.1 | 89.1 | 81.9 | 96.6 | 38.9 | 23.6 | 5459.2 | 7270.2 | 6003.5 | 7952 | 12271.7 | 10448.2 | 1.457 | 1.688 | 1.74 | 0.721 | 0.633 | 0.653 | 6.11 | -4.79 | 4.86 | 0.644 | 0.738 | 0.742 | 4.69 | -5.36 | 4.72 | 0.741 | 0.707 | 0.672 | -3.99 | 5.15 | 5.37 | 0.767 | 0.686 | 0.739 | 3.74 | -5.48 | 5.12 | Poor_Mixed | 5459.2 | 7952 | 1.457 | 0.721 | 6.11 | 0.767 | 5.48 | 0.4549 | 0.7544 | 0.5422 | 0.628 | 1 | 0.5065 | 0.4309 | 0.5983 | 0.5983 | Poor | 0 | 1 | Bushing_TD_Cap | 0 |  | C2H2
2180 | 759.8 | 516.4 | 97.6 | 106.7 | 17.8 | 791 | 5167.3 | 46.9 | 35.2 | 93 | 93.4 | 84.1 | 99.8 | 40.6 | 23.4 | 5001.4 | 5409.3 | 6266.7 | 7805.5 | 8015.7 | 9594.2 | 1.561 | 1.482 | 1.531 | 0.793 | 0.724 | 0.708 | 6.8 | -5.34 | 6.07 | 0.645 | 0.613 | 0.638 | 4.74 | 4.49 | 5.69 | 0.636 | 0.688 | 0.699 | 5.84 | -4.74 | 5.34 | 0.643 | 0.579 | 0.652 | 4.85 | 5.15 | -3.96 | Poor_Mixed | 5001.4 | 7805.5 | 1.482 | 0.793 | 6.8 | 0.699 | 5.84 | 0.4707 | 0.7322 | 0.4548 | 0.6348 | 1 | 0.3936 | 0.5144 | 0.5904 | 0.5904 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2181 | 293.7 | 162.6 | 67.5 | 162.9 | 2.2 | 400.6 | 3366.7 | 57 | 24 | 107.5 | 108.7 | 95.1 | 119.2 | 44.4 | 19.6 | 8715.5 | 8083.1 | 8825.2 | 15877.7 | 14975.8 | 17228.3 | 1.822 | 1.853 | 1.952 | 0.596 | 0.629 | 0.629 | -3.49 | 3.44 | 4.15 | 0.558 | 0.659 | 0.538 | 2.7 | -3.66 | -3.57 | 0.544 | 0.592 | 0.571 | 13.81 | -4.06 | -3.69 | 0.62 | 0.618 | 0.566 | -2.68 | -3.97 | 3.36 | Critical_Thermal | 8083.1 | 14975.8 | 1.822 | 0.629 | 4.15 | 0.659 | 13.81 | 0.7542 | 0.8875 | 0.094 | 0.7593 | 1 | 0.6515 | 0.641 | 0.709 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_R_CapChange_pct>=10% abs: critical bushing capacitance change | C2H4
2182 | 1712.8 | 982.4 | 148.3 | 186.1 | 33.3 | 1379 | 8048.8 | 58.3 | 23 | 81.7 | 79 | 73.9 | 86.9 | 36.1 | 15.8 | 9111.6 | 162.1 | 10000 | 18223.2 | 189.5 | 20000 | 2 | 1.169 | 2 | 0.615 | 0.605 | 0.553 | -3.15 | 3.01 | 2.9 | 0.511 | 0.527 | 0.525 | 2 | 2.5 | 2.15 | 0.5 | 0.541 | 0.51 | -2.08 | 2 | -2.12 | 0.5 | 0.5 | 0.517 | 2.83 | 2 | 2 | Critical_DGA | 162.1 | 189.5 | 1.169 | 0.615 | 3.15 | 0.541 | 2.83 | 0.0569 | 0.9067 | 0.8006 | 0.8718 | 0.85 | 0.729 | 0.9066 | 0.6479 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2183 | 381.5 | 206.5 | 77.5 | 70.2 | 2.7 | 443.6 | 3430.6 | 19.3 | 23 | 85.4 | 81.3 | 77.7 | 92 | 39 | 10.4 | 1226 | 1622.1 | 1136 | 1276.8 | 1844.1 | 1199.5 | 1.041 | 1.137 | 1.056 | 0.726 | 0.723 | 0.722 | -5.7 | 5.42 | 5.37 | 0.6 | 0.518 | 0.56 | 3.29 | 3.87 | 3.59 | 0.553 | 0.613 | 0.563 | -3.71 | 2.51 | -3.84 | 0.559 | 0.549 | 0.575 | 3.44 | 2.72 | 3.9 | Critical_IR_PI | 1136 | 1199.5 | 1.041 | 0.726 | 5.7 | 0.613 | 3.9 | 0.8083 | 0.3234 | 0.6824 | 0.9955 | 1 | 0.4397 | 0.7014 | 0.7067 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2184 | 917.4 | 542.8 | 101.3 | 122.7 | 17.2 | 911.8 | 5559.7 | 56.6 | 20.7 | 77.8 | 77.1 | 70 | 80.3 | 35.2 | 11.7 | 8605.9 | 8245.3 | 9878.3 | 15216 | 15432.3 | 19672.1 | 1.768 | 1.872 | 1.991 | 0.58 | 0.583 | 0.564 | 3.26 | 2.75 | 3 | 0.5 | 0.51 | 0.5 | 2.18 | -2.92 | 2 | 0.5 | 0.521 | 0.5 | 2.03 | 2.57 | 2.01 | 0.533 | 0.551 | 0.5 | 2 | 2.14 | 2.11 | Poor_DGA | 8245.3 | 15216 | 1.768 | 0.583 | 3.26 | 0.551 | 2.92 | 0.4216 | 0.9638 | 0.93 | 0.9724 | 1 | 0.7484 | 0.9233 | 0.7936 | 0.7936 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2185 | 1361.8 | 774 | 133.6 | 166.4 | 32.7 | 1172.1 | 7366.3 | 37.7 | 43.2 | 104.3 | 103.5 | 95 | 113.6 | 43.9 | 31.3 | 2242.7 | 1111 | 2142.1 | 2599.7 | 1200 | 2607.3 | 1.159 | 1.08 | 1.217 | 0.925 | 0.918 | 0.866 | 8.79 | 9.18 | 8.99 | 0.802 | 0.75 | 0.756 | 5.51 | 8.36 | -7.72 | 0.765 | 0.822 | 0.935 | 7.19 | -7.31 | 6.26 | 0.787 | 0.923 | 0.8 | 7.59 | -5.43 | -7.91 | Very Poor_Mixed | 1111 | 1200 | 1.08 | 0.925 | 9.18 | 0.935 | 8.36 | 0.1669 | 0.6474 | 0.1726 | 0.3483 | 1 | 0.1158 | 0.2529 | 0.3758 | 0.3758 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2186 | 626.6 | 397.1 | 98.5 | 93.1 | 12.7 | 738 | 3809 | 49.1 | 30.4 | 88.8 | 90.4 | 80.1 | 92.8 | 38.7 | 22.5 | 7275.8 | 7736.7 | 6881.4 | 13075.6 | 13427.2 | 11352.8 | 1.797 | 1.736 | 1.65 | 0.721 | 0.754 | 0.661 | 5.97 | 5.95 | 4.34 | 0.655 | 0.631 | 0.635 | -3.42 | 3.96 | 4.6 | 0.644 | 0.67 | 0.602 | 4.03 | -4.69 | 3.89 | 0.624 | 0.648 | 0.641 | 4.53 | 3.94 | -4.06 | Poor_Mixed | 6881.4 | 11352.8 | 1.65 | 0.754 | 5.97 | 0.67 | 4.69 | 0.5629 | 0.7907 | 0.5742 | 0.6652 | 1 | 0.4565 | 0.5511 | 0.6494 | 0.6494 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2187 | 364.2 | 276.5 | 74.1 | 78.2 | 4.5 | 594.4 | 3544.7 | 32.5 | 48.1 | 86 | 84.8 | 77.5 | 90.6 | 37.6 | 11.1 | 5461.4 | 3956.4 | 6048 | 7912.6 | 5575.1 | 9287.5 | 1.449 | 1.409 | 1.536 | 0.66 | 0.658 | 0.578 | 5.13 | 5.12 | 3.32 | 0.508 | 0.512 | 0.5 | 2.4 | -2.54 | -2.45 | 0.5 | 0.516 | 0.527 | 3.01 | 2.24 | 2 | 0.567 | 0.529 | 0.528 | 3.22 | -2.4 | -12.27 | Critical_Oil | 3956.4 | 5575.1 | 1.409 | 0.66 | 5.13 | 0.567 | 12.27 | 0.7373 | 0.6007 | 0.6676 | 0.984 | 1 | 0.5892 | 0.8344 | 0.765 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
2188 | 216.1 | 175.1 | 66.8 | 52.9 | 1.7 | 474.2 | 3227.3 | 60 | 20.3 | 75 | 75.9 | 71.9 | 81 | 35.3 | 10 | 8818.5 | 9041.7 | 8608.8 | 16478.8 | 17155.9 | 15967.3 | 1.869 | 1.897 | 1.855 | 0.641 | 0.684 | 0.599 | 3.68 | 5.08 | 3.14 | 0.5 | 0.507 | 0.523 | 2.22 | 2.06 | -2 | 0.522 | 0.5 | 0.5 | 2.54 | 2.69 | 2.82 | 0.55 | 0.5 | 0.5 | 2 | 2.16 | -2.1 | Fair_Winding_TD_Cap | 8608.8 | 15967.3 | 1.855 | 0.684 | 5.08 | 0.55 | 2.82 | 0.8849 | 0.9791 | 0.956 | 1 | 1 | 0.6115 | 0.9234 | 0.8962 | 0.8962 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2189 | 1523.3 | 919.1 | 139.2 | 173.7 | 34.3 | 1316.1 | 8136.2 | 34 | 47.6 | 106.1 | 107.2 | 93.6 | 116.5 | 42.9 | 33.8 | 1274.6 | 1719.9 | 1837.8 | 1480.6 | 2031.4 | 2096.4 | 1.162 | 1.181 | 1.141 | 0.963 | 0.951 | 0.94 | 9 | 9.84 | -8.36 | 0.693 | 0.914 | 0.962 | 6.18 | 6.72 | -5.75 | 0.847 | 0.775 | 0.755 | 8.84 | 8.08 | -6.22 | 0.864 | 0.767 | 0.866 | -7 | 8.78 | 7.59 | Very Poor_Mixed | 1274.6 | 1480.6 | 1.141 | 0.963 | 9.84 | 0.962 | 8.84 | 0.0962 | 0.6053 | 0.1425 | 0.2513 | 1 | 0.0786 | 0.237 | 0.3372 | 0.3372 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2190 | 965.1 | 539.1 | 105.6 | 120.8 | 17.1 | 867.3 | 5255.1 | 48.7 | 31.1 | 89.3 | 88.8 | 79.1 | 93.3 | 38.3 | 25.1 | 6358.1 | 6482.5 | 5864.3 | 9983.8 | 10804.3 | 9106.1 | 1.57 | 1.667 | 1.553 | 0.712 | 0.764 | 0.737 | 5.09 | 5.95 | -6 | 0.638 | 0.589 | 0.743 | -3.9 | -3.96 | -4.57 | 0.694 | 0.652 | 0.64 | 5.23 | 4.68 | 4.2 | 0.669 | 0.595 | 0.679 | 4.71 | -3.91 | 6.16 | Poor_Mixed | 5864.3 | 9106.1 | 1.553 | 0.764 | 6 | 0.743 | 6.16 | 0.4262 | 0.7817 | 0.5881 | 0.576 | 1 | 0.4177 | 0.5147 | 0.5991 | 0.5991 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2191 | 857 | 543.6 | 112.7 | 125.1 | 19.8 | 966.7 | 5483.3 | 46.6 | 33 | 92.3 | 95.1 | 83.2 | 99.9 | 40 | 23.3 | 4749.6 | 5423 | 5056.5 | 7061.2 | 7946.1 | 7996.2 | 1.487 | 1.465 | 1.581 | 0.727 | 0.754 | 0.758 | 6.11 | -6.14 | 6.16 | 0.702 | 0.736 | 0.597 | -5.53 | 4.53 | 5.47 | 0.676 | 0.643 | 0.69 | 6.02 | -5.87 | 4.55 | 0.726 | 0.712 | 0.65 | 5.58 | 5.76 | 5.3 | Poor_Mixed | 4749.6 | 7061.2 | 1.465 | 0.758 | 6.16 | 0.736 | 6.02 | 0.394 | 0.7581 | 0.4577 | 0.6382 | 1 | 0.3848 | 0.4512 | 0.5622 | 0.5622 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2192 | 1502.7 | 903.4 | 136.1 | 176.4 | 27.9 | 1256 | 8036.6 | 34.2 | 47.9 | 104.8 | 104.7 | 94.1 | 115.2 | 43.7 | 31 | 2862.8 | 2903.9 | 1553 | 3567.8 | 3563 | 1700.2 | 1.246 | 1.227 | 1.095 | 0.939 | 0.988 | 0.978 | 8.73 | 9.62 | 9.82 | 0.84 | 0.737 | 0.915 | 8.5 | 6.88 | 5.98 | 0.771 | 0.771 | 0.801 | 7.64 | 6.65 | 7.39 | 0.908 | 0.791 | 0.861 | 7.43 | 5.79 | 8.08 | Very Poor_Mixed | 1553 | 1700.2 | 1.095 | 0.988 | 9.82 | 0.915 | 8.5 | 0.1365 | 0.6025 | 0.1615 | 0.3597 | 1 | 0.0511 | 0.2427 | 0.3514 | 0.3514 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2193 | 1305.5 | 819 | 129.6 | 173.7 | 57.5 | 1116.2 | 7119.6 | 33.7 | 44.1 | 102.5 | 105.8 | 89.1 | 112.1 | 43.3 | 34.6 | 3766.4 | 2574.6 | 2649.6 | 5135.4 | 3328.4 | 3022.4 | 1.363 | 1.293 | 1.141 | 0.79 | 0.893 | 0.849 | -7.24 | -7.74 | 7.97 | 0.867 | 0.842 | 0.73 | 7.22 | 6.35 | -6.9 | 0.855 | 0.822 | 0.816 | 4.59 | 5.72 | 5.63 | 0.821 | 0.839 | 0.849 | -6.19 | 6.25 | 5.45 | Critical_Mixed | 2574.6 | 3022.4 | 1.141 | 0.893 | 7.97 | 0.867 | 7.22 | 0.1625 | 0.6386 | 0.2152 | 0.2197 | 1 | 0.2273 | 0.2741 | 0.3909 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2194 | 177.6 | 144.6 | 67.4 | 61.6 | 5.3 | 389.3 | 2973.5 | 56.1 | 23 | 76.2 | 76.7 | 70.6 | 82.5 | 35.9 | 12.1 | 9760 | 10000 | 9591.8 | 18924.6 | 19233.3 | 19021.3 | 1.939 | 1.923 | 1.983 | 0.581 | 0.577 | 0.565 | 2.75 | -2.92 | 3.21 | 0.5 | 0.5 | 0.526 | -2.36 | 2 | 2.16 | 0.512 | 0.524 | 0.535 | 2.16 | 2 | 3.02 | 0.525 | 0.513 | 0.523 | -3.3 | -2 | 2.57 | Good_Mixed | 9591.8 | 18924.6 | 1.923 | 0.581 | 3.21 | 0.535 | 3.3 | 0.8238 | 0.9067 | 0.9295 | 0.964 | 1 | 0.7531 | 0.8784 | 0.8795 | 0.8795 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2195 | 1589.2 | 933.8 | 137.4 | 180 | 55.2 | 1206.8 | 8250.4 | 53.9 | 23.3 | 81.5 | 84.2 | 76.4 | 91.1 | 38.1 | 10.5 | 8364.5 | 8078.5 | 7917.6 | 15830.1 | 14476.6 | 13945.2 | 1.893 | 1.792 | 1.761 | 0.611 | 0.6 | 0.58 | 3.55 | 3.67 | 3.41 | 0.509 | 0.54 | 0.6 | -3.37 | 3.15 | 3.15 | 0.545 | 0.528 | 0.595 | 2.91 | 3.23 | 2.65 | 0.554 | 0.524 | 0.566 | 2.65 | 2.49 | 2.79 | Critical_DGA | 7917.6 | 13945.2 | 1.761 | 0.611 | 3.67 | 0.6 | 3.37 | 0.0936 | 0.9008 | 0.7088 | 0.994 | 1 | 0.6856 | 0.7558 | 0.6441 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2196 | 454.3 | 329.7 | 84.6 | 76.9 | 8.5 | 599.9 | 3966.1 | 53.4 | 27.5 | 82.5 | 82.4 | 77.7 | 88.2 | 36.8 | 17 | 7513.6 | 7944 | 9390.7 | 13974.2 | 13777.5 | 18096 | 1.86 | 1.734 | 1.927 | 0.565 | 0.683 | 0.653 | 3.06 | -4.65 | 4.2 | 0.638 | 0.568 | 0.57 | -3.75 | 3.38 | 4.05 | 0.571 | 0.641 | 0.589 | 3.66 | -2.78 | 3.81 | 0.629 | 0.623 | 0.662 | 4.12 | -3.68 | 3.9 | Fair_Mixed | 7513.6 | 13777.5 | 1.734 | 0.683 | 4.65 | 0.662 | 4.12 | 0.667 | 0.8308 | 0.7271 | 0.8378 | 1 | 0.6221 | 0.6135 | 0.7386 | 0.7386 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2197 | 756 | 510.8 | 105.5 | 105.6 | 19.6 | 825.7 | 4927 | 46.8 | 32.5 | 89.4 | 92.4 | 81.9 | 97.3 | 39.5 | 27.7 | 6589.4 | 6688.1 | 6020.7 | 11197 | 10438 | 9696.2 | 1.699 | 1.561 | 1.61 | 0.743 | 0.72 | 0.711 | 5.44 | -5.87 | 4.99 | 0.649 | 0.634 | 0.714 | 5.44 | -4.19 | 5.47 | 0.771 | 0.678 | 0.7 | 5.99 | 4.87 | 4.36 | 0.652 | 0.665 | 0.671 | -5.05 | 4.85 | 4.9 | Poor_Mixed | 6020.7 | 9696.2 | 1.561 | 0.743 | 5.87 | 0.771 | 5.99 | 0.4542 | 0.7641 | 0.518 | 0.4829 | 1 | 0.4426 | 0.4642 | 0.5867 | 0.5867 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2198 | 1564.2 | 922.9 | 140.5 | 181.8 | 34.3 | 1258.2 | 8480.6 | 34.1 | 46.7 | 108.1 | 107.6 | 94.2 | 116.5 | 45 | 33.2 | 1794.3 | 1985.8 | 1861.2 | 2009 | 2342.2 | 2024.1 | 1.12 | 1.179 | 1.088 | 0.973 | 0.945 | 0.879 | 8.62 | -9.84 | -8.6 | 0.766 | 0.83 | 0.959 | 9.13 | -6.1 | -9.65 | 0.829 | 0.842 | 0.844 | 8.14 | 6.3 | -6.22 | 0.772 | 0.9 | 0.788 | 8.15 | 8.34 | 7.17 | Very Poor_Mixed | 1794.3 | 2009 | 1.088 | 0.973 | 9.84 | 0.959 | 9.65 | 0.0869 | 0.6137 | 0.1108 | 0.2748 | 1 | 0.0942 | 0.2113 | 0.3314 | 0.3314 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2199 | 1503.3 | 823.2 | 139.7 | 178.4 | 31 | 1266.7 | 8127.7 | 32.9 | 46.2 | 108.2 | 108.6 | 96.7 | 118.6 | 44.4 | 31.1 | 690 | 1574.5 | 1397.2 | 1200 | 1674.8 | 1467 | 1.739 | 1.064 | 1.05 | 0.971 | 0.971 | 0.99 | 8.89 | 9.36 | -9.84 | 0.714 | 0.897 | 0.878 | -7.79 | 5.76 | 7.25 | 0.929 | 0.836 | 0.874 | 6.55 | -8.54 | -7.74 | 0.8 | 0.816 | 0.99 | 6.78 | 5.72 | 9.04 | Very Poor_Mixed | 690 | 1200 | 1.05 | 0.99 | 9.84 | 0.99 | 9.04 | 0.1238 | 0.6184 | 0.085 | 0.3559 | 1 | 0.0464 | 0.2065 | 0.3351 | 0.3351 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2200 | 686.1 | 515.3 | 94.7 | 107 | 18.2 | 726.8 | 4998.6 | 43.6 | 35.6 | 91.6 | 92.5 | 83.6 | 98.8 | 40.2 | 24.7 | 5622.2 | 5712.1 | 5305.4 | 8942.2 | 8529.4 | 8166.3 | 1.591 | 1.493 | 1.539 | 0.719 | 0.74 | 0.724 | 5.86 | -5.76 | 5.79 | 0.593 | 0.703 | 0.688 | 4.55 | 4.68 | 5.29 | 0.697 | 0.672 | 0.609 | 5.84 | -5.22 | 4.39 | 0.61 | 0.578 | 0.687 | 4.75 | 4.4 | 4.65 | Poor_Mixed | 5305.4 | 8166.3 | 1.493 | 0.74 | 5.86 | 0.703 | 5.84 | 0.486 | 0.7276 | 0.4802 | 0.59 | 1 | 0.4191 | 0.5142 | 0.5976 | 0.5976 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2201 | 458 | 363.5 | 84.1 | 87.8 | 4.9 | 3052.5 | 11151.9 | 53.2 | 27.1 | 75 | 75 | 72 | 80 | 35 | 17.3 | 8430.1 | 10000 | 9291.5 | 15340.7 | 18400 | 17628.1 | 1.82 | 1.84 | 1.897 | 0.974 | 0.95 | 0.99 | -9.84 | 9.16 | 9.84 | 0.563 | 0.574 | 0.572 | 3.14 | 3.04 | 2.46 | 0.519 | 0.598 | 0.592 | -2.33 | 3.69 | 3.9 | 0.579 | 0.607 | 0.527 | 2.03 | -2.58 | -2.49 | Critical_Winding_TD_Cap | 8430.1 | 15340.7 | 1.82 | 0.99 | 9.84 | 0.607 | 3.9 | 0.5248 | 0.8367 | 0.9771 | 0.8291 | 1 | 0.0379 | 0.721 | 0.6659 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | CO
2202 | 454.1 | 322.6 | 79.5 | 83.9 | 3.4 | 582.9 | 4078.5 | 18.5 | 23.2 | 85.7 | 87.5 | 81.7 | 95.3 | 39.4 | 20.1 | 695.9 | 2776.5 | 1810.1 | 709.8 | 3313.8 | 1955.1 | 1.02 | 1.194 | 1.08 | 0.746 | 0.753 | 0.693 | 5.7 | 6.01 | 5.26 | 0.51 | 0.511 | 0.5 | 2 | 2.93 | -2.41 | 0.589 | 0.582 | 0.523 | 2.36 | -2.71 | -2.39 | 0.538 | 0.527 | 0.544 | 2.14 | -2.98 | 2.9 | Critical_IR_PI | 695.9 | 709.8 | 1.02 | 0.753 | 6.01 | 0.589 | 2.98 | 0.7292 | 0.3194 | 0.5881 | 0.7436 | 0.925 | 0.4252 | 0.8204 | 0.6718 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
2203 | 827.4 | 558.5 | 104.7 | 117.3 | 20.6 | 884.1 | 5517.5 | 59.5 | 22.4 | 76.1 | 76.4 | 70 | 80 | 35.2 | 12 | 9016.6 | 7797.9 | 8289.7 | 17610 | 14512.1 | 14528.2 | 1.953 | 1.861 | 1.753 | 0.53 | 0.513 | 0.506 | 2.51 | 2 | 2.04 | 0.546 | 0.566 | 0.529 | 2.03 | -2.54 | 3.18 | 0.573 | 0.5 | 0.532 | 3.47 | 3.32 | 2.32 | 0.549 | 0.562 | 0.513 | 3.45 | -2.94 | -2.43 | Poor_DGA | 7797.9 | 14512.1 | 1.753 | 0.53 | 2.51 | 0.573 | 3.47 | 0.413 | 0.9193 | 0.9584 | 0.9661 | 1 | 0.9178 | 0.7881 | 0.7881 | 0.7881 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2204 | 187.5 | 120 | 66.8 | 107.3 | 1 | 388.3 | 2500 | 57.8 | 21.8 | 90.1 | 89.6 | 81.6 | 95.7 | 37.9 | 10.1 | 8673.3 | 9695.2 | 8085.3 | 16017.7 | 19039.5 | 15229.4 | 1.847 | 1.964 | 1.884 | 0.5 | 0.561 | 0.553 | 2 | 2.62 | 3.68 | 0.516 | 0.587 | 0.533 | 2.89 | 2.93 | 2.41 | 0.5 | 0.546 | 0.5 | 2 | 2.22 | -2.62 | 0.5 | 0.5 | 0.501 | -2.38 | -2 | 2 | Fair_Thermal | 8085.3 | 15229.4 | 1.847 | 0.561 | 3.68 | 0.587 | 2.93 | 0.9004 | 0.9331 | 0.5512 | 0.9992 | 1 | 0.8443 | 0.8937 | 0.8812 | 0.8812 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2205 | 697.7 | 383.4 | 92 | 88.2 | 9.5 | 667.5 | 3966 | 58.9 | 20.5 | 75.7 | 77.9 | 70.5 | 80 | 35.7 | 10.8 | 9260.1 | 9503 | 9251.4 | 17777.9 | 18290.2 | 18502.8 | 1.92 | 1.925 | 2 | 0.538 | 0.5 | 0.5 | -2.13 | 2.16 | 2.85 | 0.54 | 0.5 | 0.518 | -2.5 | 2.03 | 2.43 | 0.511 | 0.5 | 0.5 | -3.23 | -2 | -2.45 | 0.545 | 0.551 | 0.503 | 2.42 | 2.04 | 2 | Fair_DGA | 9251.4 | 17777.9 | 1.92 | 0.538 | 2.85 | 0.551 | 3.23 | 0.6031 | 0.9709 | 0.938 | 0.9892 | 1 | 0.9287 | 0.8894 | 0.8607 | 0.8607 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2206 | 965.5 | 543.4 | 107 | 114.2 | 19.9 | 852.8 | 6006.7 | 47 | 34.1 | 88.4 | 91.9 | 80.7 | 97 | 38.4 | 24.8 | 5146.8 | 5477.4 | 5568.1 | 7710 | 8488.4 | 8206.7 | 1.498 | 1.55 | 1.474 | 0.752 | 0.713 | 0.766 | 5.73 | 6.22 | 5.67 | 0.693 | 0.705 | 0.689 | 5.9 | -5.46 | 6.76 | 0.622 | 0.728 | 0.653 | 6.26 | 5.81 | 3.9 | 0.709 | 0.684 | 0.626 | -3.86 | -5.47 | 3.91 | Poor_Mixed | 5146.8 | 7710 | 1.474 | 0.766 | 6.22 | 0.728 | 6.76 | 0.4078 | 0.7449 | 0.544 | 0.5865 | 1 | 0.4018 | 0.4594 | 0.574 | 0.574 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2207 | 447.6 | 249 | 79.2 | 83.1 | 1 | 474.9 | 2904.1 | 43.9 | 36.5 | 75.6 | 75.9 | 72.9 | 81.9 | 35 | 10.3 | 7061.2 | 7182.5 | 7338.7 | 11621.3 | 11982.1 | 12917 | 1.646 | 1.668 | 1.76 | 0.603 | 0.571 | 0.676 | 4.21 | -2.91 | 4.98 | 0.56 | 0.531 | 0.5 | -2.83 | 2.66 | 2.64 | 0.54 | 0.53 | 0.526 | -2.38 | 2.96 | 2.73 | 0.596 | 0.589 | 0.512 | 3 | 2 | 2.86 | Poor_Oil | 7061.2 | 11621.3 | 1.646 | 0.676 | 4.98 | 0.596 | 3 | 0.8613 | 0.7175 | 0.9318 | 0.9968 | 1 | 0.6369 | 0.796 | 0.8369 | 0.8369 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2208 | 384.2 | 319.4 | 82 | 75.7 | 8.9 | 612.7 | 3825.5 | 54.7 | 24.5 | 80.9 | 82.3 | 76.1 | 87.4 | 38.3 | 17.5 | 8525.2 | 8094.3 | 8438.7 | 15447.9 | 14560.3 | 15214 | 1.812 | 1.799 | 1.803 | 0.629 | 0.583 | 0.599 | 3.96 | -2.74 | 3.91 | 0.572 | 0.557 | 0.559 | 3.4 | 3.71 | 3.03 | 0.583 | 0.632 | 0.598 | -2.64 | 2.86 | -3.15 | 0.541 | 0.603 | 0.575 | 3.82 | 2.73 | 3.21 | Fair_Mixed | 8094.3 | 14560.3 | 1.799 | 0.629 | 3.96 | 0.632 | 3.82 | 0.6731 | 0.8786 | 0.7479 | 0.8232 | 1 | 0.6793 | 0.6839 | 0.7679 | 0.7679 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2209 | 176.7 | 157.1 | 69.2 | 57.5 | 1 | 390.7 | 3080.7 | 59.4 | 20.8 | 77 | 78 | 71.4 | 81.8 | 35.8 | 10.6 | 10000 | 9809.1 | 9610.1 | 19175.8 | 18608.6 | 19220.2 | 1.918 | 1.897 | 2 | 0.554 | 0.548 | 0.57 | -2.69 | 2.49 | 2.86 | 0.555 | 0.517 | 0.548 | 2.78 | 3.23 | 2 | 0.5 | 0.5 | 0.5 | 3.07 | 2.14 | 2 | 0.5 | 0.573 | 0.5 | -3.04 | -2.07 | 2.32 | Fair_Winding_TD_Cap | 9610.1 | 18608.6 | 1.897 | 0.57 | 2.86 | 0.573 | 3.23 | 0.9533 | 0.9605 | 0.902 | 0.9925 | 1 | 0.7974 | 0.8859 | 0.9245 | 0.9245 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
2210 | 409.6 | 319.6 | 79.6 | 84.7 | 3.4 | 614.1 | 3668.5 | 35.1 | 45.5 | 79.2 | 79.6 | 75 | 86 | 35.5 | 17.9 | 5655.1 | 5126.9 | 5304.4 | 8363.4 | 7837.9 | 7668.8 | 1.479 | 1.529 | 1.446 | 0.725 | 0.654 | 0.665 | 4.23 | 4.44 | 4.71 | 0.594 | 0.574 | 0.527 | 2.44 | -3.96 | 3.1 | 0.543 | 0.532 | 0.595 | 3.39 | 2.55 | -15.9 | 0.624 | 0.581 | 0.54 | 3.75 | 3.72 | 3.18 | Critical_Oil | 5126.9 | 7668.8 | 1.446 | 0.725 | 4.71 | 0.624 | 15.9 | 0.7314 | 0.6251 | 0.8151 | 0.8114 | 1 | 0.5392 | 0.6803 | 0.7379 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
2211 | 795 | 508.6 | 106.3 | 119.6 | 16 | 831.1 | 5675.5 | 46.6 | 34 | 91.5 | 95.9 | 84.3 | 101.5 | 40.4 | 24.7 | 5545.8 | 4668.9 | 4598.4 | 7952.8 | 6750.4 | 6662.4 | 1.434 | 1.446 | 1.449 | 0.775 | 0.747 | 0.75 | 6.14 | 6.54 | -6.03 | 0.707 | 0.695 | 0.672 | 5.68 | 4.25 | 4.29 | 0.742 | 0.629 | 0.655 | 5.63 | -3.81 | 3.89 | 0.737 | 0.771 | 0.645 | -4.18 | 4.41 | 3.8 | Poor_Mixed | 4598.4 | 6662.4 | 1.434 | 0.775 | 6.54 | 0.771 | 5.68 | 0.451 | 0.7461 | 0.4405 | 0.59 | 1 | 0.37 | 0.4708 | 0.5724 | 0.5724 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2212 | 177.5 | 154.8 | 68.2 | 113.2 | 1.3 | 350 | 2628.5 | 53.6 | 26 | 96.1 | 95.7 | 86.3 | 103.5 | 41.7 | 13.4 | 9093.5 | 9187.2 | 9264.5 | 16755 | 18002.7 | 17179.4 | 1.843 | 1.96 | 1.854 | 0.532 | 0.567 | 0.64 | -2.23 | 2.86 | 3.38 | 0.508 | 0.506 | 0.513 | -2.38 | 3.17 | -2.84 | 0.527 | 0.533 | 0.532 | 2.57 | 3.01 | 3.48 | 0.5 | 0.562 | 0.5 | -2.96 | 2.85 | 3.05 | Poor_Thermal | 9093.5 | 16755 | 1.843 | 0.64 | 3.38 | 0.562 | 3.48 | 0.8617 | 0.8536 | 0.3821 | 0.9342 | 1 | 0.7634 | 0.847 | 0.8221 | 0.8221 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2213 | 213.5 | 142.2 | 75.5 | 61.9 | 1.4 | 399.3 | 3056.2 | 58.9 | 20.3 | 75 | 75 | 71.1 | 83.1 | 35.9 | 11.2 | 9361.2 | 9321.3 | 9126.7 | 17938.9 | 17983.7 | 18231.1 | 1.916 | 1.929 | 1.998 | 0.572 | 0.528 | 0.567 | 3.36 | 2.16 | -2.76 | 0.584 | 0.506 | 0.538 | -2.4 | 2.9 | 2 | 0.523 | 0.524 | 0.706 | -2.61 | -3.01 | 6.41 | 0.519 | 0.563 | 0.574 | 2.04 | 3.78 | 2.78 | Poor_Bushing_TD_Cap | 9126.7 | 17938.9 | 1.916 | 0.572 | 3.36 | 0.706 | 6.41 | 0.8958 | 0.9791 | 0.9669 | 0.9821 | 1 | 0.7982 | 0.7477 | 0.8936 | 0.8936 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2214 | 867.5 | 556.8 | 106.6 | 126 | 16 | 818.2 | 5046.6 | 47.8 | 30.1 | 91.7 | 92.6 | 82.6 | 97.4 | 39 | 24.1 | 5108.2 | 6795.6 | 5754.7 | 8455.5 | 10809.9 | 8790 | 1.655 | 1.591 | 1.527 | 0.752 | 0.7 | 0.767 | 5.58 | -5.47 | -6.55 | 0.735 | 0.632 | 0.635 | 4.26 | 3.08 | 6.57 | 0.603 | 0.593 | 0.575 | 3.52 | 4.69 | 6.11 | 0.668 | 0.669 | 0.712 | 4.34 | -5.02 | -5.45 | Poor_Mixed | 5108.2 | 8455.5 | 1.527 | 0.767 | 6.55 | 0.735 | 6.57 | 0.4415 | 0.7947 | 0.4998 | 0.6108 | 1 | 0.406 | 0.5213 | 0.5969 | 0.5969 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2215 | 1064.5 | 588.6 | 112.5 | 137.4 | 21.6 | 931.2 | 6427.7 | 56.3 | 23.2 | 76.8 | 78.9 | 72.2 | 83.3 | 35.9 | 16.8 | 9442.2 | 8620.4 | 9165.7 | 18294.8 | 16713.9 | 17411.5 | 1.938 | 1.939 | 1.9 | 0.513 | 0.513 | 0.54 | 2.46 | 2.95 | 2.13 | 0.526 | 0.505 | 0.546 | 2.57 | 2.83 | 2.12 | 0.573 | 0.519 | 0.555 | 2 | 2 | -3.65 | 0.534 | 0.515 | 0.546 | 2 | 2.36 | -2.33 | Poor_DGA | 8620.4 | 16713.9 | 1.9 | 0.54 | 2.95 | 0.573 | 3.65 | 0.3451 | 0.9027 | 0.8801 | 0.8436 | 1 | 0.8772 | 0.8192 | 0.7551 | 0.7551 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2216 | 943.9 | 513.9 | 100.5 | 111.4 | 19.8 | 775.8 | 5359 | 44.6 | 34.1 | 92.6 | 91 | 82.5 | 98.5 | 40.1 | 23.9 | 5537.8 | 5124.4 | 5446.7 | 8492 | 7588.4 | 8281.1 | 1.533 | 1.481 | 1.52 | 0.693 | 0.722 | 0.719 | 5.66 | 6.12 | 5.72 | 0.711 | 0.688 | 0.656 | 4.24 | 7.46 | -4.74 | 0.669 | 0.709 | 0.733 | 5.39 | 3.8 | 5.31 | 0.691 | 0.688 | 0.67 | 4.42 | -4.91 | -4.54 | Poor_Mixed | 5124.4 | 7588.4 | 1.481 | 0.722 | 6.12 | 0.733 | 7.46 | 0.4375 | 0.7449 | 0.4925 | 0.6177 | 1 | 0.4322 | 0.4539 | 0.5811 | 0.5811 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2217 | 1566.4 | 831.9 | 136.6 | 185.9 | 42.3 | 1296.7 | 7962.7 | 36 | 44.1 | 99.7 | 99.1 | 87.7 | 108.6 | 42.3 | 37.5 | 3250.5 | 3602.8 | 2804.2 | 4093.3 | 4669.3 | 3316.6 | 1.259 | 1.296 | 1.183 | 0.913 | 0.901 | 0.894 | -9.15 | 8.56 | 8.99 | 0.8 | 0.747 | 0.857 | 5.15 | 7.74 | 6.89 | 0.832 | 0.854 | 0.879 | 6.99 | 6.28 | 7.97 | 0.762 | 0.88 | 0.863 | 7.29 | 6.75 | 8.6 | Critical_Mixed | 2804.2 | 3316.6 | 1.183 | 0.913 | 9.15 | 0.88 | 8.6 | 0.0959 | 0.6386 | 0.3023 | 0.1031 | 1 | 0.1202 | 0.2363 | 0.3553 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2218 | 828.6 | 592.1 | 100.8 | 121.9 | 17.8 | 964.6 | 5429.1 | 47 | 31 | 90.1 | 91.5 | 80.2 | 94.4 | 39.7 | 25 | 5212 | 5525.1 | 4862.1 | 7999.1 | 8351.2 | 7038.3 | 1.535 | 1.512 | 1.448 | 0.681 | 0.727 | 0.783 | 4.7 | 5.35 | 7.09 | 0.7 | 0.742 | 0.693 | 5.23 | 6.47 | 3.85 | 0.672 | 0.74 | 0.618 | 3.73 | 4.66 | 4.84 | 0.659 | 0.668 | 0.679 | 3.86 | 4.66 | 5.8 | Poor_Mixed | 4862.1 | 7038.3 | 1.448 | 0.783 | 7.09 | 0.742 | 6.47 | 0.4154 | 0.7829 | 0.5435 | 0.5796 | 1 | 0.4241 | 0.468 | 0.5848 | 0.5848 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2219 | 1090.1 | 572.5 | 108.6 | 141.1 | 23.7 | 853.4 | 6001.3 | 58.5 | 23.5 | 80.3 | 80.8 | 73.2 | 89 | 37.1 | 13.9 | 8253 | 9214.6 | 8975.9 | 15982.9 | 17692.4 | 17368.5 | 1.937 | 1.92 | 1.935 | 0.553 | 0.593 | 0.533 | 2.65 | 3.04 | 2.75 | 0.582 | 0.554 | 0.514 | 2.83 | 3.06 | 2.5 | 0.504 | 0.515 | 0.514 | -2.69 | 3.47 | 3.27 | 0.579 | 0.546 | 0.514 | 2.77 | 2.57 | -3.79 | Poor_DGA | 8253 | 15982.9 | 1.92 | 0.593 | 3.04 | 0.582 | 3.79 | 0.3473 | 0.8969 | 0.7866 | 0.9219 | 1 | 0.7872 | 0.794 | 0.7323 | 0.7323 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2220 | 471.1 | 414 | 84.8 | 74.9 | 1.8 | 670.2 | 3983.8 | 59.8 | 67.9 | 77.8 | 75.1 | 72.9 | 87.3 | 35.6 | 19.6 | 9826 | 10000 | 9416.2 | 18565.3 | 19736.3 | 17960.8 | 1.889 | 1.974 | 1.907 | 0.638 | 0.613 | 0.589 | 3.43 | -3.97 | -4.28 | 0.544 | 0.575 | 0.554 | 4.05 | 2.55 | 3.14 | 0.627 | 0.571 | 0.54 | 2.83 | 2.83 | 3.43 | 0.573 | 0.896 | 0.579 | 3.54 | 8.48 | 3.03 | Critical_Bushing_TD_Cap | 9416.2 | 17960.8 | 1.889 | 0.638 | 4.28 | 0.896 | 8.48 | 0.7511 | 0.5833 | 0.8899 | 0.7593 | 1 | 0.6449 | 0.6381 | 0.7499 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2221 | 691.9 | 439.4 | 95.5 | 109 | 15.4 | 731.9 | 4475.4 | 51.3 | 28.6 | 85.1 | 85.6 | 76.2 | 92.4 | 38.8 | 23.7 | 7639.7 | 7628 | 7679.1 | 13363.8 | 12781.7 | 13929.6 | 1.749 | 1.676 | 1.814 | 0.736 | 0.614 | 0.679 | 5.22 | 4.9 | 4.59 | 0.573 | 0.594 | 0.645 | 3.35 | 3.45 | 3.27 | 0.618 | 0.684 | 0.612 | 4.36 | 3.72 | -3.82 | 0.604 | 0.643 | 0.626 | -3.36 | 4.74 | 3.98 | Fair_Mixed | 7628 | 12781.7 | 1.676 | 0.736 | 5.22 | 0.684 | 4.74 | 0.5138 | 0.815 | 0.6616 | 0.6246 | 1 | 0.5202 | 0.5903 | 0.6627 | 0.6627 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2222 | 1030.8 | 579 | 111.6 | 123 | 15.5 | 868.1 | 5401 | 46.1 | 32.4 | 92.8 | 96.1 | 84.4 | 102.8 | 41.2 | 25 | 4544.5 | 5212.2 | 6030.4 | 6779.2 | 7940.8 | 9273.8 | 1.492 | 1.524 | 1.538 | 0.702 | 0.763 | 0.747 | 5.08 | -5.93 | -5.35 | 0.76 | 0.687 | 0.673 | 5.77 | 5.36 | 4.47 | 0.71 | 0.672 | 0.738 | 5.34 | 5.24 | 4.91 | 0.62 | 0.696 | 0.721 | 5.72 | -4.59 | 4.5 | Poor_Mixed | 4544.5 | 6779.2 | 1.492 | 0.763 | 5.93 | 0.76 | 5.77 | 0.4191 | 0.7654 | 0.4186 | 0.5796 | 1 | 0.4307 | 0.442 | 0.5673 | 0.5673 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
2223 | 1738.8 | 913 | 147.3 | 185 | 32.8 | 1342.2 | 8208.6 | 35.2 | 46.2 | 106 | 107.5 | 96.5 | 116.5 | 46.1 | 34.1 | 1685.8 | 1554.8 | 1313.3 | 1941.3 | 1632.6 | 1391.4 | 1.152 | 1.05 | 1.059 | 0.99 | 0.975 | 0.954 | 9.84 | 9.81 | 8.73 | 0.817 | 0.978 | 0.888 | 5.8 | 7.58 | 7.96 | 0.968 | 0.769 | 0.943 | 8.65 | -6.98 | 7.22 | 0.849 | 0.99 | 0.727 | 9.84 | 8.76 | 7.25 | Very Poor_Mixed | 1313.3 | 1391.4 | 1.05 | 0.99 | 9.84 | 0.99 | 9.84 | 0.0684 | 0.6184 | 0.102 | 0.2395 | 1 | 0.0445 | 0.1711 | 0.3105 | 0.3105 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2224 | 107.4 | 157.6 | 68.2 | 75.9 | 1 | 351.2 | 3305.5 | 58.8 | 22.6 | 89.2 | 81.1 | 81 | 93.9 | 38.4 | 10.3 | 8772.3 | 9913.2 | 9341.6 | 16808.9 | 19826.4 | 17623.7 | 1.916 | 2 | 1.887 | 0.562 | 0.533 | 0.541 | 2.95 | 2.67 | 3.27 | 0.512 | 0.507 | 0.501 | 2 | 2 | 2.46 | 0.501 | 0.5 | 0.5 | 2.41 | 2.5 | 2.1 | 0.5 | 0.51 | 0.544 | 2.37 | 2.05 | 2.22 | Fair_Thermal | 8772.3 | 16808.9 | 1.887 | 0.562 | 3.27 | 0.544 | 2.5 | 0.9448 | 0.915 | 0.6295 | 0.9968 | 1 | 0.7977 | 0.9316 | 0.8982 | 0.8982 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_HV
2225 | 255.5 | 193.3 | 70.4 | 50 | 2.3 | 424.2 | 3204.7 | 58.5 | 20 | 79.9 | 75 | 71 | 85.3 | 35.4 | 15.4 | 9046.1 | 8907.5 | 9189.8 | 17773.6 | 16754.6 | 17396 | 1.965 | 1.881 | 1.893 | 0.741 | 0.858 | 0.85 | 6.04 | -7.07 | -7.1 | 0.545 | 0.552 | 0.513 | -2.67 | 2.94 | 2.52 | 0.553 | 0.554 | 0.578 | 3.03 | 2.12 | 3.18 | 0.521 | 0.525 | 0.503 | 2.8 | 2.43 | -2.16 | Poor_Winding_TD_Cap | 8907.5 | 16754.6 | 1.881 | 0.858 | 7.1 | 0.578 | 3.18 | 0.876 | 1 | 0.9018 | 0.8828 | 1 | 0.2973 | 0.8006 | 0.819 | 0.819 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
2226 | 1345.5 | 794.5 | 127.3 | 176.3 | 34 | 1176.7 | 7209.3 | 33 | 46.1 | 103.9 | 103.5 | 93.6 | 115.4 | 43.5 | 30.9 | 1883.7 | 1645.9 | 1674.6 | 2106.9 | 1897.8 | 1836.6 | 1.118 | 1.153 | 1.097 | 0.944 | 0.894 | 0.915 | 9.12 | 7.97 | -8.6 | 0.751 | 0.752 | 0.868 | -6.29 | 6.04 | -5.51 | 0.738 | 0.762 | 0.744 | 7.26 | 6.3 | 5.9 | 0.848 | 0.657 | 0.742 | -6.94 | 7.02 | 5.08 | Very Poor_Mixed | 1645.9 | 1836.6 | 1.097 | 0.944 | 9.12 | 0.868 | 7.26 | 0.1582 | 0.6194 | 0.1765 | 0.3635 | 1 | 0.127 | 0.3312 | 0.3871 | 0.3871 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2227 | 335.6 | 248.5 | 70 | 76.3 | 1.7 | 2401.8 | 18814.6 | 30.6 | 48 | 83.4 | 79.7 | 75.2 | 84.5 | 37.3 | 11.7 | 4802 | 4425.5 | 4735.2 | 6768 | 6385.1 | 6911.7 | 1.409 | 1.443 | 1.46 | 0.661 | 0.695 | 0.604 | 4.66 | 5.16 | -4.31 | 0.589 | 0.551 | 0.599 | -3.42 | 3.09 | 3.18 | 0.674 | 0.611 | 0.57 | 3.23 | -3.76 | 3.66 | 0.574 | 0.608 | 0.531 | 3.07 | 3.94 | 4.27 | Critical_Oil | 4425.5 | 6385.1 | 1.409 | 0.695 | 5.16 | 0.674 | 4.27 | 0.6364 | 0.6016 | 0.7766 | 0.9724 | 1 | 0.5536 | 0.6556 | 0.7131 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | Moisture_PPM
2228 | 819.8 | 432.4 | 98.3 | 126.9 | 15.5 | 776.6 | 5261 | 46.4 | 35.9 | 91.5 | 95.6 | 81.3 | 101.2 | 39.9 | 25.2 | 5437.2 | 5556.9 | 4619.6 | 7785.7 | 8437.6 | 6772.3 | 1.432 | 1.518 | 1.466 | 0.821 | 0.755 | 0.77 | -6.48 | -6.36 | 6.28 | 0.653 | 0.617 | 0.649 | 5.49 | -5.26 | 4.85 | 0.658 | 0.729 | 0.687 | 4.08 | 6.09 | -3.8 | 0.697 | 0.75 | 0.741 | -4.05 | 5.76 | -4.35 | Poor_Mixed | 4619.6 | 6772.3 | 1.432 | 0.821 | 6.48 | 0.75 | 6.09 | 0.4709 | 0.7242 | 0.4661 | 0.5725 | 1 | 0.3427 | 0.4646 | 0.5715 | 0.5715 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2229 | 763.5 | 508 | 102.6 | 108 | 17.3 | 817.7 | 4617.3 | 48.7 | 33 | 90.3 | 93.4 | 83 | 98.1 | 40.8 | 26.5 | 5368.3 | 5647.3 | 5625.1 | 8050.5 | 8459.8 | 8642.3 | 1.5 | 1.498 | 1.536 | 0.72 | 0.703 | 0.733 | 5.42 | 5.74 | -5.4 | 0.598 | 0.653 | 0.718 | 5.16 | 4.89 | -5.08 | 0.603 | 0.624 | 0.637 | -4.37 | 4.74 | 4.51 | 0.676 | 0.724 | 0.647 | 4.9 | 3.73 | 4.55 | Poor_Mixed | 5368.3 | 8050.5 | 1.498 | 0.733 | 5.74 | 0.724 | 5.16 | 0.4715 | 0.7581 | 0.4863 | 0.5264 | 1 | 0.4429 | 0.514 | 0.5983 | 0.5983 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2230 | 962.8 | 548.3 | 105.3 | 125.4 | 21.9 | 907.9 | 5449.8 | 43.7 | 35.1 | 90.4 | 94.7 | 83.2 | 99.4 | 39.8 | 26.3 | 4971.3 | 5169.5 | 5724.7 | 7590.5 | 7763 | 8870.9 | 1.527 | 1.502 | 1.55 | 0.674 | 0.742 | 0.697 | 4.47 | 5.85 | 4.86 | 0.645 | 0.663 | 0.681 | -5.36 | 4.3 | -5.27 | 0.622 | 0.614 | 0.677 | 3.94 | 4.15 | 3.6 | 0.717 | 0.683 | 0.647 | 4.67 | -3.75 | -4.39 | Poor_Mixed | 4971.3 | 7590.5 | 1.502 | 0.742 | 5.85 | 0.717 | 5.36 | 0.3857 | 0.7333 | 0.4763 | 0.5335 | 1 | 0.4829 | 0.5131 | 0.5787 | 0.5787 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2231 | 367.4 | 330.1 | 84.3 | 87.4 | 10.8 | 528.4 | 3474.9 | 56.1 | 24.6 | 83.6 | 82.6 | 77.7 | 89 | 38.7 | 16.4 | 7500.5 | 7352.7 | 7791.9 | 12982.1 | 12813.8 | 13921.3 | 1.731 | 1.743 | 1.787 | 0.594 | 0.659 | 0.619 | -3.55 | -3.65 | 3.96 | 0.659 | 0.569 | 0.579 | 4.14 | -3.47 | 3.99 | 0.532 | 0.563 | 0.546 | 4.46 | 4 | 3.76 | 0.613 | 0.619 | 0.551 | 3.09 | 3.7 | 4.13 | Fair_Mixed | 7352.7 | 12813.8 | 1.731 | 0.659 | 3.96 | 0.659 | 4.46 | 0.6561 | 0.8768 | 0.7022 | 0.855 | 1 | 0.6436 | 0.6564 | 0.7505 | 0.7505 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2232 | 100 | 120 | 65.7 | 50 | 1.5 | 424.6 | 2609.4 | 56.8 | 20.3 | 75 | 77.2 | 73.9 | 81.8 | 35 | 10.4 | 9718.2 | 10000 | 8731.9 | 18633.8 | 20000 | 16754.9 | 1.917 | 2 | 1.919 | 0.532 | 0.516 | 0.504 | 2.32 | 2.15 | 2.31 | 0.514 | 0.5 | 0.51 | 2.1 | 2.55 | 2.43 | 0.523 | 0.501 | 0.5 | -2.42 | 2 | 2.48 | 0.51 | 0.511 | 0.504 | -2 | 2.96 | 2 | Good_Mixed | 8731.9 | 16754.9 | 1.917 | 0.532 | 2.32 | 0.523 | 2.96 | 0.9347 | 0.9791 | 0.9205 | 0.9955 | 1 | 0.9081 | 0.9183 | 0.9454 | 0.9454 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2233 | 219 | 259 | 67.3 | 66.8 | 1.9 | 413.8 | 3104.3 | 16 | 26.4 | 82.3 | 79.8 | 75 | 86.7 | 36.5 | 18.9 | 690 | 850.1 | 2186.7 | 788.9 | 867.1 | 2597.2 | 1.143 | 1.02 | 1.188 | 0.702 | 0.714 | 0.673 | 5.34 | -5.11 | 4.51 | 0.601 | 0.622 | 0.539 | 4.25 | 4.27 | 3.93 | 0.621 | 0.604 | 0.614 | -3.05 | 3.68 | 2.83 | 0.588 | 0.619 | 0.633 | 3.51 | 3.57 | -3.2 | Critical_IR_PI | 690 | 788.9 | 1.02 | 0.714 | 5.34 | 0.633 | 4.27 | 0.8562 | 0.264 | 0.779 | 0.7811 | 0.85 | 0.4938 | 0.6254 | 0.6804 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
2234 | 706.8 | 425.1 | 97 | 109.9 | 14 | 744.2 | 5182.4 | 59.1 | 23.1 | 76.9 | 80.2 | 73.1 | 82.7 | 35.2 | 12.3 | 8993.6 | 8961.9 | 8184.3 | 16844.6 | 17170.3 | 14028.7 | 1.873 | 1.916 | 1.714 | 0.5 | 0.543 | 0.521 | 2 | 2.12 | -2.49 | 0.52 | 0.533 | 0.552 | -2.17 | 2.63 | 2 | 0.519 | 0.544 | 0.591 | -2.91 | 2.99 | 2.69 | 0.587 | 0.58 | 0.562 | 2.17 | 2.33 | 2.13 | Fair_DGA | 8184.3 | 14028.7 | 1.714 | 0.543 | 2.49 | 0.591 | 2.99 | 0.5137 | 0.9047 | 0.8655 | 0.9597 | 1 | 0.9136 | 0.7723 | 0.7984 | 0.7984 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2235 | 1587.8 | 921 | 140.2 | 192.2 | 34.3 | 1329.5 | 8083 | 33.5 | 46.9 | 106.5 | 104.3 | 95.4 | 117.4 | 43.6 | 34.4 | 835.1 | 1180.1 | 1830.8 | 1200 | 1239.1 | 1982.9 | 1.437 | 1.05 | 1.083 | 0.927 | 0.943 | 0.984 | 9.07 | 8.54 | 9.84 | 0.926 | 0.895 | 0.886 | 5.66 | 6.03 | 8.56 | 0.957 | 0.867 | 0.866 | 9.71 | 5.96 | 7.42 | 0.927 | 0.888 | 0.916 | 8.63 | 9.58 | -6.62 | Very Poor_Mixed | 835.1 | 1200 | 1.05 | 0.984 | 9.84 | 0.957 | 9.71 | 0.0746 | 0.6119 | 0.1368 | 0.2276 | 1 | 0.0745 | 0.1552 | 0.3155 | 0.3155 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2236 | 375.2 | 239.8 | 82.3 | 75.1 | 6.5 | 513.9 | 4034.5 | 53.3 | 26.1 | 81.8 | 83.2 | 74.6 | 88.3 | 37.3 | 16.5 | 9772.8 | 8409.5 | 8863.5 | 19469.3 | 15635.3 | 16705.4 | 1.992 | 1.859 | 1.885 | 0.631 | 0.619 | 0.559 | 4.61 | 3.89 | 3.19 | 0.59 | 0.551 | 0.565 | -3.28 | -2.3 | 3.26 | 0.557 | 0.552 | 0.598 | 2.13 | 3.1 | -4.11 | 0.532 | 0.601 | 0.554 | 3.03 | 3.75 | 3.52 | Fair_Mixed | 8409.5 | 15635.3 | 1.859 | 0.631 | 4.61 | 0.601 | 4.11 | 0.7216 | 0.852 | 0.746 | 0.8522 | 1 | 0.6593 | 0.7098 | 0.7799 | 0.7799 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2237 | 1495.4 | 846.5 | 130.3 | 177.1 | 34.3 | 1153.7 | 7469.7 | 34.3 | 45.8 | 105.2 | 108.6 | 93.3 | 112.7 | 43.8 | 32.2 | 3195.3 | 2700.9 | 2209.8 | 4055.9 | 3280.8 | 2709.6 | 1.269 | 1.215 | 1.226 | 0.93 | 0.942 | 0.959 | -8.79 | -9.03 | 9.77 | 0.909 | 0.916 | 0.773 | 7.93 | 5.56 | 8.02 | 0.978 | 0.785 | 0.793 | 8.5 | 9.2 | 6.61 | 0.872 | 0.888 | 0.92 | 7.53 | 7.09 | -6.73 | Very Poor_Mixed | 2209.8 | 2709.6 | 1.215 | 0.959 | 9.77 | 0.978 | 9.2 | 0.1367 | 0.6222 | 0.1541 | 0.3137 | 1 | 0.0771 | 0.1885 | 0.3447 | 0.3447 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2238 | 115 | 155.5 | 70.5 | 50 | 1 | 403.8 | 3028.8 | 58 | 23.9 | 82 | 78.6 | 71.4 | 85.2 | 36.9 | 13.7 | 9945.6 | 8986.8 | 9178.9 | 19292.5 | 17046.8 | 17857.1 | 1.94 | 1.897 | 1.945 | 0.567 | 0.513 | 0.586 | 2.94 | 2.92 | 3.47 | 0.547 | 0.6 | 0.56 | 2 | 2.88 | -2.78 | 0.616 | 0.562 | 0.572 | -2.81 | -2.73 | 2.98 | 0.554 | 0.597 | 0.819 | 3.55 | 3.24 | -7.3 | Poor_Bushing_TD_Cap | 8986.8 | 17046.8 | 1.897 | 0.586 | 3.47 | 0.819 | 7.3 | 0.975 | 0.8894 | 0.8282 | 0.9269 | 1 | 0.7781 | 0.6532 | 0.8661 | 0.8661 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2239 | 1559.2 | 853.2 | 135.5 | 178.5 | 33.6 | 1379 | 7739.2 | 34.7 | 44.6 | 107.7 | 106.2 | 93.2 | 118 | 43.9 | 29.1 | 1713.6 | 1725.3 | 1900.2 | 1902.2 | 1960.3 | 2358.8 | 1.11 | 1.136 | 1.241 | 0.916 | 0.966 | 0.983 | 8.93 | -9.52 | 9.74 | 0.807 | 0.871 | 0.798 | 6.77 | 8.74 | 8.63 | 0.807 | 0.799 | 0.876 | -7.19 | 5.4 | 6.94 | 0.985 | 0.749 | 0.905 | 8.05 | 7.24 | 7.46 | Very Poor_Mixed | 1713.6 | 1902.2 | 1.11 | 0.983 | 9.74 | 0.985 | 8.74 | 0.1011 | 0.6338 | 0.1268 | 0.4313 | 1 | 0.0597 | 0.2148 | 0.3426 | 0.3426 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2240 | 1392.4 | 806.3 | 128.7 | 170.4 | 33.7 | 1126.1 | 7077.2 | 35.6 | 44.5 | 100.5 | 100.8 | 92.2 | 113.4 | 42.8 | 35.7 | 1829.8 | 2773.8 | 2136.6 | 1930.1 | 3435 | 2640.9 | 1.055 | 1.238 | 1.236 | 0.892 | 0.913 | 0.919 | 8.29 | 16.61 | -8.92 | 0.816 | 0.856 | 0.84 | -6.23 | 6.44 | -6.83 | 0.725 | 0.73 | 0.82 | 7.06 | 6.41 | 4.8 | 0.755 | 0.756 | 0.813 | 7.21 | 8.18 | 6.54 | Critical_Mixed | 1829.8 | 1930.1 | 1.055 | 0.919 | 16.61 | 0.856 | 8.18 | 0.166 | 0.6347 | 0.2342 | 0.1758 | 1 | 0.1081 | 0.2895 | 0.3771 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
2241 | 1115.5 | 627 | 110.1 | 136.6 | 23.8 | 929.9 | 6438.9 | 57.3 | 20 | 79.8 | 79.6 | 73.2 | 87.3 | 36.4 | 12.5 | 8295.9 | 8223.3 | 7781.3 | 14862.1 | 14600.5 | 14115.3 | 1.791 | 1.776 | 1.814 | 0.531 | 0.549 | 0.569 | 2.94 | 3.02 | 2.65 | 0.516 | 0.538 | 0.536 | 2.14 | 2.33 | 2.46 | 0.531 | 0.513 | 0.511 | 3.45 | 2.11 | 2.48 | 0.542 | 0.543 | 0.549 | 3.03 | 2.66 | 2.41 | Poor_DGA | 7781.3 | 14115.3 | 1.776 | 0.569 | 3.02 | 0.549 | 3.45 | 0.3276 | 1 | 0.8134 | 0.9552 | 1 | 0.7973 | 0.818 | 0.7499 | 0.7499 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2242 | 1476.1 | 859.7 | 131.6 | 172.5 | 38.4 | 1193.3 | 7537.4 | 52.1 | 25.2 | 77.4 | 82.6 | 73 | 87.9 | 36 | 13.8 | 8797.9 | 8806.1 | 9189.7 | 16543.2 | 16565.7 | 17647.3 | 1.88 | 1.881 | 1.92 | 0.72 | 0.654 | 0.657 | 5.35 | 4.68 | 4.2 | 0.578 | 0.624 | 0.601 | 3.95 | 3.92 | 4 | 0.622 | 0.639 | 0.551 | 4.36 | 4.75 | 4.06 | 0.599 | 0.608 | 0.551 | 3.41 | 3.55 | -3.01 | Critical_DGA | 8797.9 | 16543.2 | 1.88 | 0.72 | 5.35 | 0.639 | 4.75 | 0.1312 | 0.8666 | 0.8119 | 0.9244 | 1 | 0.5271 | 0.6256 | 0.6106 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2243 | 1438.3 | 804.9 | 129.2 | 169.8 | 30.9 | 1282.5 | 7870.9 | 37.1 | 44.2 | 103 | 103.6 | 90.6 | 114.3 | 44 | 37.6 | 1865 | 2198.8 | 1285.8 | 2174.5 | 2568.3 | 1511.7 | 1.166 | 1.168 | 1.176 | 0.965 | 2.093 | 0.944 | 9.1 | 9.01 | -9.15 | 0.803 | 0.727 | 0.862 | 6.08 | 6.97 | 7.45 | 0.738 | 0.739 | 0.881 | 7.12 | 6.36 | 6.95 | 0.791 | 0.723 | 0.791 | 8.24 | 7.04 | 6.62 | Critical_Mixed | 1285.8 | 1511.7 | 1.166 | 2.093 | 9.15 | 0.881 | 8.24 | 0.148 | 0.6376 | 0.1999 | 0.099 | 1 | 0.0654 | 0.2844 | 0.3588 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
2244 | 689 | 398.9 | 95.1 | 90.3 | 5 | 686.5 | 4647.3 | 53.6 | 27.6 | 82.2 | 84.4 | 75 | 86.1 | 38 | 11.4 | 737.6 | 1726.2 | 1351.8 | 788 | 1583.8 | 1432.6 | 1.068 | 0.918 | 1.06 | 0.702 | 0.732 | 0.667 | 5.16 | 5.29 | 4.96 | 0.583 | 0.593 | 0.613 | 3.24 | 3.19 | 2.98 | 0.596 | 0.531 | 0.578 | 2.84 | 3.98 | 2.5 | 0.536 | 0.596 | 0.621 | 2.31 | 2.27 | -3.03 | Critical_IR_PI | 737.6 | 788 | 0.918 | 0.732 | 5.29 | 0.621 | 3.98 | 0.6384 | 0.8293 | 0.7377 | 0.9783 | 0.7437 | 0.4817 | 0.6922 | 0.6928 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | C2H2
2245 | 1514.8 | 875.9 | 134.7 | 172.5 | 31.7 | 1191.1 | 7327.3 | 37 | 42.5 | 108.1 | 105.7 | 93.9 | 114.6 | 43.8 | 33.6 | 1982.4 | 1981 | 1186.9 | 2167.9 | 2249.5 | 1325.1 | 1.094 | 1.136 | 1.116 | 0.927 | 0.974 | 0.97 | 7.96 | 9.04 | 9.21 | 0.76 | 0.844 | 0.906 | -9.31 | 7.01 | 5.42 | 0.796 | 0.963 | 0.853 | 9.49 | -6.75 | -7.38 | 0.914 | 0.861 | 0.868 | 5.93 | 5.76 | 8.14 | Very Poor_Mixed | 1186.9 | 1325.1 | 1.094 | 0.974 | 9.21 | 0.963 | 9.49 | 0.1415 | 0.6544 | 0.1412 | 0.2591 | 1 | 0.0916 | 0.2024 | 0.3502 | 0.3502 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2246 | 811.6 | 608.1 | 102.6 | 123.7 | 16.4 | 907.9 | 6081.2 | 57.2 | 24.4 | 78.6 | 78.1 | 74 | 86.7 | 36.3 | 10 | 8434 | 8909.4 | 7928.4 | 15311.2 | 16513.2 | 13778.9 | 1.815 | 1.853 | 1.738 | 0.574 | 0.591 | 0.519 | 2.54 | -2.8 | 2.88 | 0.543 | 0.573 | 0.559 | -2.88 | -3.25 | 3.64 | 0.502 | 0.562 | 0.546 | 3.54 | 3.9 | -3.6 | 0.578 | 0.551 | 0.536 | 3.05 | -3.69 | 2.61 | Poor_DGA | 7928.4 | 13778.9 | 1.738 | 0.591 | 2.88 | 0.578 | 3.9 | 0.4207 | 0.8804 | 0.8353 | 1 | 1 | 0.7927 | 0.7393 | 0.7484 | 0.7484 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2247 | 1508.8 | 857.5 | 133.4 | 170.2 | 34.3 | 1244.1 | 8165.3 | 37 | 43.3 | 104.8 | 103.8 | 91.2 | 113.3 | 44.6 | 31 | 1509.1 | 1326.8 | 1859.6 | 1675.9 | 1471.4 | 2146.2 | 1.111 | 1.109 | 1.154 | 0.94 | 0.932 | 0.945 | 8.72 | 8.49 | 9.36 | 0.913 | 0.917 | 0.779 | 7.54 | 7.05 | -6.26 | 0.726 | 0.901 | 0.713 | 5.84 | 8.11 | -7.78 | 0.878 | 0.936 | 0.776 | -6.87 | -5.92 | 9.26 | Very Poor_Mixed | 1326.8 | 1471.4 | 1.109 | 0.945 | 9.36 | 0.936 | 9.26 | 0.119 | 0.6465 | 0.1859 | 0.3597 | 1 | 0.0974 | 0.2292 | 0.3588 | 0.3588 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2248 | 892.4 | 492.2 | 100.6 | 114.3 | 16.2 | 871.7 | 5082.9 | 46 | 32.7 | 90.9 | 94.1 | 84.2 | 100 | 41.3 | 27.1 | 6187.6 | 6059.5 | 4819.6 | 9587.7 | 9418.3 | 7226.2 | 1.55 | 1.554 | 1.499 | 0.726 | 0.72 | 0.714 | 5.67 | -4.96 | 5.04 | 0.738 | 0.679 | 0.662 | 4.53 | -6.25 | -3.41 | 0.715 | 0.753 | 0.683 | 5.26 | 3.82 | -4.58 | 0.669 | 0.65 | 0.698 | 4.98 | -4.58 | 3.47 | Poor_Mixed | 4819.6 | 7226.2 | 1.499 | 0.726 | 5.67 | 0.753 | 6.25 | 0.4541 | 0.7617 | 0.4577 | 0.5047 | 1 | 0.4584 | 0.4666 | 0.5841 | 0.5841 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2249 | 233.3 | 200.8 | 75.1 | 62.7 | 1 | 444.7 | 3151.6 | 58.5 | 21.7 | 78.1 | 77.9 | 71.2 | 82.1 | 35.5 | 10.8 | 7336.5 | 6098.1 | 5811.8 | 12647.6 | 9718.7 | 9419.7 | 1.724 | 1.594 | 1.621 | 0.618 | 0.599 | 0.627 | -3.72 | -2.73 | -4 | 0.543 | 0.542 | 0.539 | 2.4 | -2.87 | 2.3 | 0.518 | 0.539 | 0.529 | 2 | -2.77 | 2.87 | 0.537 | 0.526 | 0.549 | 2.41 | -2.46 | 2.66 | Fair_IR_PI | 5811.8 | 9419.7 | 1.594 | 0.627 | 4 | 0.549 | 2.87 | 0.9199 | 0.9355 | 0.8934 | 0.9892 | 1 | 0.6691 | 0.8045 | 0.8795 | 0.8795 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
2250 | 1016.3 | 620.7 | 103.6 | 129.8 | 22.8 | 909.4 | 5386.5 | 45.8 | 32.6 | 95.3 | 91.5 | 83.3 | 99.4 | 39.6 | 24.1 | 6096.3 | 5361.5 | 4853.3 | 10275.4 | 7929 | 6777.4 | 1.686 | 1.479 | 1.396 | 0.785 | 0.69 | 0.733 | 5.67 | 5.51 | 6.07 | 0.669 | 0.679 | 0.648 | 4.12 | 3.46 | -4.68 | 0.622 | 0.67 | 0.599 | 5 | 4.55 | 4.12 | 0.63 | 0.696 | 0.661 | 4.15 | 5.01 | -4.33 | Poor_Mixed | 4853.3 | 6777.4 | 1.396 | 0.785 | 6.07 | 0.696 | 5.01 | 0.3662 | 0.7629 | 0.4661 | 0.6108 | 1 | 0.4159 | 0.5238 | 0.5728 | 0.5728 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2251 | 1287.5 | 745.1 | 130.5 | 154.9 | 22.9 | 1199.6 | 7145 | 39.1 | 42.3 | 100.1 | 101.6 | 89.6 | 113.2 | 42.8 | 34.5 | 3451 | 2715.7 | 2457.7 | 4402.6 | 3492.5 | 2998.5 | 1.276 | 1.286 | 1.22 | 0.816 | 1.313 | 0.854 | 6.79 | -7.5 | 7.13 | 0.71 | 0.778 | 0.731 | 7.42 | -7.19 | 6.95 | 0.837 | 0.753 | 0.824 | 6.41 | -6.06 | 5.58 | 0.866 | 0.858 | 0.856 | 7.86 | -6.19 | 5.82 | Critical_Mixed | 2457.7 | 2998.5 | 1.22 | 1.313 | 7.5 | 0.866 | 7.86 | 0.2351 | 0.6564 | 0.2478 | 0.2237 | 1 | 0.222 | 0.2798 | 0.415 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
2252 | 1485.7 | 843.5 | 139.4 | 192.6 | 27.6 | 1283.1 | 8257.6 | 58.2 | 22 | 84 | 82.3 | 79 | 90.7 | 37.8 | 13.4 | 8369.5 | 8807 | 9261.3 | 15640.6 | 16384.8 | 17400.5 | 1.869 | 1.86 | 1.879 | 0.525 | 2.052 | 0.516 | 2.39 | 2.32 | -2.5 | 0.587 | 0.572 | 0.541 | -2.23 | 3.36 | 3.2 | 0.577 | 0.523 | 0.594 | 3.46 | -3.31 | 2.52 | 0.598 | 0.532 | 0.5 | 3.24 | 2.47 | -2.32 | Critical_DGA | 8369.5 | 15640.6 | 1.86 | 2.052 | 2.5 | 0.598 | 3.46 | 0.1239 | 0.9283 | 0.6894 | 0.9342 | 1 | 0.7326 | 0.7509 | 0.6557 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
2253 | 183.4 | 159.5 | 71.5 | 64 | 4.6 | 395 | 2877 | 57.9 | 22.8 | 76.7 | 75 | 71.1 | 82.2 | 36.7 | 13.4 | 8716.3 | 9138.3 | 8897.2 | 16645.6 | 18099 | 16906 | 1.91 | 1.981 | 1.9 | 0.564 | 0.54 | 0.521 | -2.65 | 2.44 | 2.18 | 0.535 | 0.564 | 0.506 | -2 | 2.69 | -2.07 | 0.557 | 0.553 | 0.515 | 2 | 2.62 | 2.91 | 0.502 | 0.512 | 0.553 | -2.11 | -2.23 | 2.67 | Good_Mixed | 8716.3 | 16645.6 | 1.9 | 0.564 | 2.65 | 0.564 | 2.91 | 0.8246 | 0.9108 | 0.9416 | 0.9342 | 1 | 0.8445 | 0.833 | 0.8845 | 0.8845 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2254 | 793.1 | 463.2 | 97.1 | 115.5 | 13.5 | 850.5 | 4605.1 | 49.1 | 31.3 | 85.8 | 88.1 | 81.5 | 93.8 | 39.5 | 20 | 6853.7 | 7785 | 6953.1 | 11802.3 | 13885.2 | 12042.2 | 1.722 | 1.784 | 1.732 | 0.647 | 0.644 | 0.655 | 4.33 | 3.64 | 4.6 | 0.674 | 0.563 | 0.621 | 4.52 | -4.14 | 4.79 | 0.69 | 0.591 | 0.634 | 4.91 | 3.27 | 3.18 | 0.608 | 0.612 | 0.689 | 4.45 | -4.97 | 5.47 | Poor_Mixed | 6853.7 | 11802.3 | 1.722 | 0.655 | 4.6 | 0.69 | 5.47 | 0.4925 | 0.7791 | 0.5914 | 0.7467 | 1 | 0.5873 | 0.5549 | 0.6552 | 0.6552 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2255 | 1753.2 | 964.6 | 148.3 | 193.1 | 33.6 | 1338.9 | 8506.3 | 51.8 | 26.8 | 77.9 | 83.9 | 74.8 | 86.3 | 36.3 | 16.6 | 8914.4 | 8450.8 | 9956.3 | 16864.6 | 15670.6 | 18952.8 | 1.892 | 1.854 | 1.904 | 0.508 | 1.893 | 0.506 | 2.65 | -2.27 | 2.58 | 0.58 | 0.561 | 0.542 | -3.57 | 2.62 | 2.91 | 0.585 | 0.5 | 0.567 | 3.24 | 3.66 | -3.36 | 0.562 | 0.567 | 0.589 | 3.24 | 2.07 | 3.08 | Critical_DGA | 8450.8 | 15670.6 | 1.854 | 1.893 | 2.65 | 0.589 | 3.66 | 0.0473 | 0.8412 | 0.7889 | 0.8493 | 1 | 0.7503 | 0.7324 | 0.631 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
2256 | 779.5 | 466.5 | 97.2 | 109.5 | 15.1 | 804.1 | 5813.5 | 48.8 | 30.9 | 92.7 | 90.4 | 83.9 | 96.6 | 40.2 | 23.8 | 7118.5 | 6295.7 | 6447 | 11581.2 | 10632.5 | 9982.2 | 1.627 | 1.689 | 1.548 | 0.702 | 0.662 | 0.756 | -5.85 | 4.52 | 6.02 | 0.612 | 0.698 | 0.728 | -4.64 | 4.04 | 5.66 | 0.625 | 0.707 | 0.7 | 5.42 | 5.53 | -3.34 | 0.722 | 0.57 | 0.577 | 4.45 | 5.34 | 4.39 | Poor_Mixed | 6295.7 | 9982.2 | 1.548 | 0.756 | 6.02 | 0.728 | 5.66 | 0.4814 | 0.7842 | 0.4959 | 0.6212 | 1 | 0.4587 | 0.5064 | 0.6105 | 0.6105 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2257 | 510.4 | 358.8 | 85.8 | 96.4 | 10.5 | 645 | 4058.2 | 51.2 | 27.7 | 84.6 | 87.7 | 78.4 | 91.8 | 38.8 | 20.1 | 8378.7 | 7335.4 | 8543.4 | 14999 | 12504.4 | 15572.1 | 1.79 | 1.705 | 1.823 | 0.691 | 0.687 | 0.636 | 5.11 | -5.2 | -4.13 | 0.646 | 0.586 | 0.667 | -3.59 | 3.86 | -4.32 | 0.611 | 0.67 | 0.554 | 3.38 | -4.43 | -3.15 | 0.584 | 0.678 | 0.682 | 3.5 | 4.7 | -4.43 | Fair_Mixed | 7335.4 | 12504.4 | 1.705 | 0.691 | 5.2 | 0.682 | 4.7 | 0.6104 | 0.8279 | 0.6379 | 0.7436 | 1 | 0.5284 | 0.5752 | 0.6904 | 0.6904 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2258 | 906.9 | 573.6 | 103.6 | 115.6 | 20.8 | 902.4 | 5415.9 | 58.9 | 20.6 | 77.1 | 77.3 | 71.7 | 82.1 | 36.1 | 12.6 | 10000 | 9236.4 | 8141.4 | 20000 | 17685.1 | 14739.6 | 2 | 1.915 | 1.81 | 0.551 | 0.512 | 0.564 | 2.06 | 2 | 2.16 | 0.561 | 0.573 | 0.55 | 3.53 | -2.7 | 3.26 | 0.611 | 0.55 | 0.623 | 2.88 | 2.57 | 2.83 | 0.589 | 0.507 | 0.522 | -2.29 | 3.49 | 3.15 | Poor_DGA | 8141.4 | 14739.6 | 1.81 | 0.564 | 2.16 | 0.623 | 3.53 | 0.4052 | 0.9672 | 0.9023 | 0.953 | 1 | 0.8756 | 0.7288 | 0.769 | 0.769 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2259 | 834.5 | 538.4 | 99.3 | 122.6 | 18.5 | 819.4 | 5650.4 | 47 | 33.3 | 90.4 | 89.6 | 83.3 | 99.9 | 39.8 | 26.4 | 4510.4 | 5257.3 | 6346.2 | 6719.7 | 8033.9 | 10134.6 | 1.49 | 1.528 | 1.597 | 0.755 | 0.762 | 0.745 | 5.99 | 6.02 | 6.2 | 0.59 | 0.706 | 0.629 | 4.29 | 5.62 | 4.42 | 0.703 | 0.659 | 0.62 | 5.61 | 3.68 | -3.64 | 0.573 | 0.696 | 0.675 | 3.27 | -3.94 | 5.06 | Poor_Mixed | 4510.4 | 6719.7 | 1.49 | 0.762 | 6.2 | 0.706 | 5.62 | 0.4324 | 0.7544 | 0.5059 | 0.5299 | 1 | 0.3818 | 0.5305 | 0.5847 | 0.5847 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2260 | 370.5 | 247.9 | 76.4 | 90.8 | 59.4 | 458.8 | 3014.7 | 59.1 | 21.4 | 83.4 | 84.9 | 76.4 | 90 | 37.3 | 11.7 | 9066.9 | 7740.5 | 6262.8 | 17592.7 | 14018.4 | 10292 | 1.94 | 1.811 | 1.643 | 0.61 | 0.537 | 0.627 | 3.13 | 2.83 | 4.36 | 0.526 | 0.949 | 0.597 | 2.87 | 9.82 | 3.05 | 0.554 | 0.571 | 0.614 | -2.82 | -3.62 | 3.12 | 0.633 | 0.568 | 0.596 | 3.4 | 2.67 | 2.86 | Critical_Bushing_TD_Cap | 6262.8 | 10292 | 1.643 | 0.627 | 4.36 | 0.949 | 9.82 | 0.5435 | 0.9432 | 0.6987 | 0.9724 | 1 | 0.7054 | 0.616 | 0.7372 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2261 | 961 | 556 | 102.8 | 120.2 | 19.9 | 801.4 | 5471.8 | 49.4 | 31.1 | 93.5 | 92.8 | 83.7 | 98.9 | 38.7 | 25.1 | 5975.3 | 5004.2 | 4273.5 | 9473 | 7588.7 | 6047.1 | 1.585 | 1.516 | 1.415 | 0.713 | 0.724 | 0.718 | 6.28 | 5.21 | 6.06 | 0.715 | 0.716 | 0.661 | 3.7 | -3.91 | 4.28 | 0.679 | 0.703 | 0.655 | 4.41 | 2.93 | 4.84 | 0.718 | 0.719 | 0.71 | -3.68 | 5.03 | 4.42 | Poor_Mixed | 4273.5 | 6047.1 | 1.415 | 0.724 | 6.28 | 0.719 | 5.03 | 0.4161 | 0.7817 | 0.4745 | 0.576 | 1 | 0.4251 | 0.4776 | 0.5796 | 0.5796 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2262 | 1119.6 | 656.3 | 117.9 | 141.3 | 24.4 | 961.4 | 7123.3 | 56.2 | 25.8 | 80.5 | 79.6 | 74.6 | 86.9 | 36.6 | 15.3 | 8948.6 | 9823.9 | 9649.5 | 17683.8 | 19647.9 | 19045.4 | 1.976 | 2 | 1.974 | 0.548 | 0.575 | 0.5 | 2.84 | 2.94 | 2.56 | 0.541 | 0.51 | 0.574 | 3.13 | 2.81 | -2.96 | 0.506 | 0.564 | 0.5 | 2.77 | 2.55 | 2.16 | 0.559 | 0.507 | 0.515 | 2.17 | 2.18 | 2.76 | Poor_DGA | 8948.6 | 17683.8 | 1.974 | 0.575 | 2.94 | 0.574 | 3.13 | 0.2989 | 0.8568 | 0.7971 | 0.8855 | 1 | 0.835 | 0.8323 | 0.7282 | 0.7282 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2263 | 293.4 | 205.3 | 68.6 | 158.5 | 74 | 403.3 | 2698.3 | 52.8 | 27.5 | 109.3 | 109.2 | 98.1 | 118.9 | 44.5 | 21.8 | 8536.3 | 9865 | 8480.5 | 15350 | 19512.7 | 16427.7 | 1.798 | 1.978 | 1.937 | 0.621 | 0.618 | 0.651 | 3.32 | -4.44 | 3.9 | 0.516 | 0.55 | 0.536 | 3 | 2.93 | -2.82 | 0.606 | 0.543 | 0.547 | 3.11 | 2.26 | 3.05 | 0.593 | 0.539 | 0.55 | 2.77 | -3.21 | 3.14 | Critical_Thermal | 8480.5 | 15350 | 1.798 | 0.651 | 4.44 | 0.606 | 3.21 | 0.5065 | 0.8308 | 0.066 | 0.6885 | 1 | 0.6262 | 0.7489 | 0.6498 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2264 | 100 | 120 | 66.5 | 50 | 1.5 | 350 | 2500 | 59.7 | 23 | 75.4 | 78.3 | 71.8 | 80 | 35.7 | 13 | 9425.4 | 9643.8 | 9327.3 | 18731.3 | 18747.5 | 17631.6 | 1.987 | 1.944 | 1.89 | 0.531 | 0.5 | 0.538 | 2.04 | -2.04 | 2.46 | 0.519 | 0.5 | 0.5 | 3.22 | -2.28 | -2.24 | 0.504 | 0.5 | 0.528 | -2.71 | 2 | -2.62 | 0.5 | 0.515 | 0.5 | 2.24 | 2.46 | -2.27 | Good_Mixed | 9327.3 | 17631.6 | 1.89 | 0.538 | 2.46 | 0.528 | 3.22 | 0.9515 | 0.9067 | 0.9251 | 0.9438 | 1 | 0.9112 | 0.926 | 0.9406 | 0.9406 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2265 | 1678.2 | 982.4 | 143.7 | 186.1 | 31.6 | 1353.9 | 8310.3 | 55.8 | 73.6 | 79.5 | 78.6 | 72 | 82.7 | 36.5 | 18.7 | 10000 | 9859 | 9172.8 | 19661.2 | 18095.7 | 17470.4 | 1.966 | 1.835 | 1.905 | 0.624 | 0.569 | 0.602 | 4.11 | -3.45 | 4 | 0.637 | 0.594 | 0.594 | 3.29 | -3.32 | 2.93 | 0.624 | 0.64 | 0.603 | -3.06 | -3.78 | 3.82 | 0.644 | 0.631 | 0.544 | 3.36 | 3.76 | 3.72 | Critical_DGA | 9172.8 | 17470.4 | 1.835 | 0.624 | 4.11 | 0.644 | 3.82 | 0.0699 | 0.5833 | 0.8582 | 0.7872 | 1 | 0.6657 | 0.6194 | 0.5773 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
2266 | 598.1 | 335.5 | 85.2 | 94 | 1 | 646.6 | 4562.1 | 54.2 | 26.5 | 78.1 | 78.6 | 75.3 | 83.7 | 35.5 | 14.1 | 1545.9 | 995.3 | 1615.9 | 1900.9 | 1042 | 1774 | 1.23 | 1.047 | 1.098 | 0.64 | 0.705 | 0.729 | 4.5 | 5.5 | 5.17 | 0.602 | 0.558 | 0.628 | 3.41 | 3.71 | 3.77 | 0.633 | 1.369 | 0.643 | -3.67 | 4.46 | -3.85 | 0.596 | 0.576 | 0.558 | 3.17 | 4.14 | 2.44 | Critical_IR_PI | 995.3 | 1042 | 1.047 | 0.729 | 5.5 | 1.369 | 4.46 | 0.7842 | 0.8458 | 0.8438 | 0.9169 | 1 | 0.4958 | 0.587 | 0.7628 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_LV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | Moisture_PPM
2267 | 1435 | 848.3 | 141.5 | 160.9 | 33.1 | 1183.7 | 8374.2 | 37.2 | 42.1 | 102.4 | 106.3 | 94.8 | 114.3 | 44.9 | 31.5 | 2280.4 | 2515.6 | 3707.4 | 2735.4 | 2943 | 4733.3 | 1.2 | 1.17 | 1.277 | 0.926 | 0.927 | 0.827 | -9.05 | 8.59 | 7.26 | 0.803 | 0.699 | 0.732 | 6.13 | -6.67 | 6.38 | 0.766 | 0.737 | 0.772 | 5.15 | -8.69 | 6.08 | 0.874 | 0.705 | 0.736 | 7.79 | 8.75 | 7.02 | Very Poor_Mixed | 2280.4 | 2735.4 | 1.17 | 0.927 | 9.05 | 0.874 | 8.75 | 0.136 | 0.6584 | 0.158 | 0.3406 | 1 | 0.1583 | 0.3117 | 0.3841 | 0.3841 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2268 | 1516 | 875.5 | 141 | 170.1 | 34.3 | 1289.3 | 8521 | 33.9 | 47.6 | 109.3 | 109.3 | 96.4 | 119.2 | 45 | 32.1 | 849.9 | 1560.7 | 1015.6 | 1200 | 1741.1 | 1200 | 1.412 | 1.116 | 1.182 | 0.976 | 0.99 | 0.937 | 9.61 | 9.05 | -8.89 | 0.791 | 0.757 | 0.876 | -6.83 | 6.19 | 9.51 | 0.897 | 0.707 | 0.913 | 7.66 | 8.61 | -9.16 | 0.796 | 0.758 | 0.77 | -8.8 | 5.72 | 8.65 | Very Poor_Mixed | 849.9 | 1200 | 1.116 | 0.99 | 9.61 | 0.913 | 9.51 | 0.1009 | 0.6053 | 0.0695 | 0.3175 | 1 | 0.0619 | 0.2333 | 0.3314 | 0.3314 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2269 | 522.5 | 420.4 | 89.1 | 90 | 1.2 | 652.2 | 4216.9 | 23.1 | 25.4 | 86.5 | 84.1 | 78.6 | 89.6 | 36.9 | 16.4 | 7928.6 | 6892.6 | 7194.1 | 14206.3 | 11433.6 | 12940.5 | 1.792 | 1.659 | 1.799 | 0.584 | 0.537 | 0.576 | 3.41 | 2.76 | 3.52 | 0.609 | 0.99 | 0.563 | -3.28 | -9.84 | 4.09 | 0.577 | 0.62 | 0.594 | -4.25 | 2.88 | 3.44 | 0.641 | 0.585 | 0.56 | -2 | 3.26 | 3.84 | Critical_Bushing_TD_Cap | 6892.6 | 11433.6 | 1.659 | 0.584 | 3.52 | 0.99 | 9.84 | 0.7533 | 0.28 | 0.6705 | 0.855 | 1 | 0.7496 | 0.5819 | 0.7014 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2270 | 946.4 | 616.1 | 102.6 | 130.5 | 23.4 | 829.3 | 5464.6 | 54.4 | 22.7 | 77.1 | 77.1 | 72 | 83.5 | 35.5 | 14.6 | 8375.5 | 10000 | 9208.9 | 15525.1 | 20000 | 17777.3 | 1.854 | 2 | 1.93 | 0.525 | 0.5 | 0.527 | -2.08 | 2.7 | 2.08 | 0.565 | 0.519 | 0.502 | 2 | -2.97 | 2.66 | 0.502 | 0.531 | 0.5 | -2.08 | 2 | -2 | 0.521 | 0.5 | 0.554 | 2 | 2 | 2.25 | Poor_DGA | 8375.5 | 15525.1 | 1.854 | 0.527 | 2.7 | 0.565 | 2.97 | 0.378 | 0.9129 | 0.8973 | 0.904 | 1 | 0.9137 | 0.8874 | 0.7866 | 0.7866 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2271 | 991.2 | 521 | 103 | 117.5 | 20.2 | 871 | 5289.4 | 47.4 | 34.6 | 90.9 | 89 | 83 | 96.5 | 38.7 | 25.1 | 4990.6 | 5691.6 | 4360.8 | 7564.9 | 8503.5 | 6111.1 | 1.516 | 1.494 | 1.401 | 0.721 | 0.735 | 0.724 | 6.34 | 5.32 | 5.85 | 0.704 | 0.731 | 0.732 | 6.24 | 4.03 | 5.92 | 0.725 | 0.688 | 0.73 | -5.64 | -5.04 | -5.24 | 0.679 | 0.705 | 0.627 | 5.99 | 5.54 | 5.13 | Poor_Mixed | 4360.8 | 6111.1 | 1.401 | 0.735 | 6.34 | 0.732 | 6.24 | 0.4117 | 0.7391 | 0.5323 | 0.576 | 1 | 0.4183 | 0.4244 | 0.5686 | 0.5686 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2272 | 1549.5 | 852.6 | 140.4 | 182.7 | 33.3 | 1329.3 | 8058 | 32 | 45.6 | 106.4 | 105.8 | 93.4 | 115.5 | 43.9 | 31.1 | 1669.2 | 1151.4 | 1499.8 | 1816.1 | 1209 | 1656 | 1.088 | 1.05 | 1.104 | 0.959 | 0.972 | 0.984 | 9.5 | 9.44 | 9.11 | 0.756 | 0.751 | 0.847 | 6.72 | 6.94 | 6 | 0.893 | 0.892 | 0.807 | 8.63 | 5.04 | 7.56 | 0.934 | 0.699 | 0.83 | 6.46 | 5.37 | 5.19 | Very Poor_Mixed | 1151.4 | 1209 | 1.05 | 0.984 | 9.5 | 0.934 | 8.63 | 0.097 | 0.6241 | 0.1475 | 0.3559 | 1 | 0.0507 | 0.2668 | 0.3468 | 0.3468 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2273 | 314.1 | 183.4 | 72.7 | 64.1 | 1 | 450.2 | 2957.6 | 42.8 | 38.2 | 81.7 | 76.7 | 73.6 | 83.5 | 35.8 | 15.3 | 5534.5 | 6852.6 | 6819.3 | 8567.1 | 11241 | 11502.5 | 1.548 | 1.64 | 1.687 | 0.651 | 0.583 | 0.58 | 3.91 | -3.77 | 2.88 | 0.535 | 0.538 | 0.552 | -2.51 | 2.93 | 3.48 | 0.558 | 0.524 | 0.523 | 2.63 | 2.28 | -2.97 | 0.541 | 0.534 | 0.501 | 2.35 | 2.36 | 3.03 | Poor_Oil | 5534.5 | 8567.1 | 1.548 | 0.651 | 3.91 | 0.558 | 3.48 | 0.9136 | 0.6989 | 0.8446 | 0.8855 | 1 | 0.6802 | 0.805 | 0.8411 | 0.8411 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2274 | 106 | 197.7 | 74.6 | 57.7 | 6.5 | 429.6 | 3400 | 58.7 | 21.8 | 77.1 | 76.2 | 70 | 80 | 36.2 | 15.6 | 10000 | 9751.7 | 9872.5 | 19710.1 | 17688.9 | 18960.6 | 1.971 | 1.814 | 1.921 | 0.518 | 0.507 | 0.509 | 2.09 | 2.03 | 2.1 | 0.5 | 0.509 | 0.5 | 2.34 | 2.54 | -2.17 | 0.5 | 0.51 | 0.5 | -2.47 | 2.63 | -2.16 | 0.518 | 0.543 | 0.543 | -2.49 | 2 | -2.62 | Good_Mixed | 9751.7 | 17688.9 | 1.814 | 0.518 | 2.1 | 0.543 | 2.63 | 0.8034 | 0.9331 | 0.9449 | 0.8773 | 1 | 0.9374 | 0.9044 | 0.9052 | 0.9052 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2275 | 100 | 193.6 | 65.6 | 50.3 | 1.8 | 370.3 | 2501.7 | 54.9 | 24.3 | 77.4 | 77.3 | 72.7 | 83.7 | 35.6 | 13.6 | 801.4 | 1498 | 1330.7 | 828.4 | 1665.1 | 1569.8 | 1.034 | 1.112 | 1.18 | 0.691 | 0.662 | 0.721 | 5.42 | 4.34 | 4.86 | 0.564 | 0.646 | 0.606 | -3.08 | 3.31 | -10.62 | 0.605 | 0.573 | 0.587 | 3.13 | 4.1 | 3.17 | 0.567 | 0.564 | 0.553 | 3.64 | 3.32 | 3.77 | Critical_IR_PI | 801.4 | 828.4 | 1.034 | 0.721 | 5.42 | 0.646 | 10.62 | 0.9236 | 0.8821 | 0.8843 | 0.9294 | 0.925 | 0.5054 | 0.6384 | 0.8053 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; Bushing_HV_B_CapChange_pct>=10% abs: critical bushing capacitance change | Winding_TV_TanDelta_pct
2276 | 1358.8 | 821.4 | 132.7 | 161.2 | 33.3 | 1175.7 | 8303.1 | 35.5 | 41.4 | 104 | 103.7 | 90.8 | 110.9 | 44.4 | 31.4 | 1811.9 | 1637.2 | 3193.5 | 2077 | 1884.1 | 4110.3 | 1.146 | 1.151 | 1.287 | 0.819 | 0.858 | 0.883 | 7.61 | 7.55 | 7.85 | 0.652 | 0.714 | 0.908 | 8.37 | 6.34 | -5.48 | 0.874 | 0.845 | 0.778 | -4.97 | -6.79 | 7.62 | 0.855 | 0.816 | 0.845 | 6.04 | 5.58 | 5.01 | Very Poor_Mixed | 1637.2 | 1884.1 | 1.146 | 0.883 | 7.85 | 0.908 | 8.37 | 0.1521 | 0.6655 | 0.2067 | 0.3444 | 1 | 0.2188 | 0.2872 | 0.3981 | 0.3981 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2277 | 777.8 | 508.7 | 102.6 | 124.5 | 19.4 | 724.2 | 5699.7 | 46.5 | 35.6 | 92.5 | 94.8 | 85.2 | 101.4 | 39.5 | 26.1 | 5395.4 | 5289.2 | 6491.3 | 9028.2 | 8367.9 | 10525.7 | 1.673 | 1.582 | 1.622 | 0.724 | 0.677 | 0.713 | 5.62 | 5.14 | -5.44 | 0.714 | 0.662 | 0.655 | 3.55 | 4.58 | 4.36 | 0.66 | 0.654 | 0.638 | 4.54 | 3.97 | -4.82 | 0.657 | 0.677 | 0.647 | 3.31 | -5.16 | 3.98 | Poor_Mixed | 5289.2 | 8367.9 | 1.582 | 0.724 | 5.62 | 0.714 | 5.16 | 0.4424 | 0.7276 | 0.4416 | 0.5407 | 1 | 0.4626 | 0.515 | 0.5866 | 0.5866 | Poor | 0 | 1 | Thermal | 0 |  | C2H2
2278 | 772.5 | 475.7 | 98 | 113.5 | 14.3 | 763.8 | 4928.8 | 44.5 | 35.4 | 92 | 85.6 | 79.9 | 97.2 | 39.5 | 23.7 | 5334.9 | 4600.4 | 5278.8 | 8088.7 | 6484.5 | 7677.3 | 1.516 | 1.41 | 1.454 | 0.76 | 0.728 | 0.77 | -6.58 | 6.33 | -5.75 | 0.684 | 0.736 | 0.689 | 5.47 | 4.12 | -3.25 | 0.677 | 0.593 | 0.569 | 5.46 | 4.17 | 5.51 | 0.664 | 0.741 | 0.7 | -3.8 | 5.11 | 5.29 | Poor_Mixed | 4600.4 | 6484.5 | 1.41 | 0.77 | 6.58 | 0.741 | 5.51 | 0.4962 | 0.7299 | 0.5605 | 0.6246 | 1 | 0.3751 | 0.4917 | 0.5999 | 0.5999 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2279 | 923.1 | 597.4 | 106.7 | 119.8 | 19.7 | 835.1 | 5881.8 | 45.9 | 33 | 91.8 | 89.7 | 80.4 | 97.1 | 39.6 | 24.3 | 6354.9 | 6470.4 | 5882.3 | 10112.6 | 10021.5 | 9211.6 | 1.591 | 1.549 | 1.566 | 0.664 | 0.712 | 0.68 | -4.28 | 5.49 | 5.62 | 0.74 | 0.679 | 0.615 | 3.57 | 4.47 | 3.31 | 0.69 | 0.676 | 0.714 | 3.88 | 4.67 | 4.26 | 0.743 | 0.616 | 0.666 | 5.03 | 4.97 | -5.06 | Poor_Mixed | 5882.3 | 9211.6 | 1.549 | 0.712 | 5.62 | 0.743 | 5.06 | 0.4046 | 0.7581 | 0.53 | 0.6039 | 1 | 0.4965 | 0.4892 | 0.5929 | 0.5929 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2280 | 302.2 | 186.2 | 79.8 | 54 | 7.1 | 523.9 | 2840 | 56.7 | 22.6 | 77.6 | 75.1 | 70.6 | 80 | 35.8 | 11.4 | 10000 | 8326.6 | 9494 | 19839.6 | 15208.6 | 17865.4 | 1.984 | 1.827 | 1.882 | 0.51 | 0.533 | 0.545 | 2 | 2.66 | 2.83 | 0.509 | 0.532 | 0.57 | -2.9 | 2 | 2.51 | 0.535 | 0.512 | 0.535 | -2.45 | -2.82 | 2 | 0.538 | 0.531 | 0.569 | 2.63 | 3.34 | 2.5 | Good_Mixed | 8326.6 | 15208.6 | 1.827 | 0.545 | 2.83 | 0.57 | 3.34 | 0.7678 | 0.915 | 0.9496 | 0.9783 | 1 | 0.8647 | 0.8058 | 0.8717 | 0.8717 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2281 | 1440.1 | 982.4 | 148.3 | 188.9 | 34.3 | 1379 | 8608.4 | 32.3 | 49 | 105.9 | 107.8 | 96.6 | 119.2 | 44.7 | 34.4 | 2457.7 | 1104.5 | 1808.1 | 2770 | 1200 | 2162.7 | 1.127 | 1.086 | 1.196 | 0.978 | 0.958 | 0.986 | 9.49 | 8.47 | -9.43 | 0.894 | 0.755 | 0.875 | 8.32 | 7.55 | -7.69 | 0.825 | 0.931 | 0.82 | 8.89 | 9.07 | 8.92 | 0.889 | 0.882 | 0.726 | 5.73 | 8.51 | 7.39 | Very Poor_Mixed | 1104.5 | 1200 | 1.086 | 0.986 | 9.49 | 0.931 | 9.07 | 0.0625 | 0.5924 | 0.0973 | 0.2276 | 1 | 0.0603 | 0.1947 | 0.3113 | 0.3113 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2282 | 1564.3 | 849 | 137.1 | 169.7 | 28.5 | 1215.9 | 7765 | 37.1 | 44.2 | 102 | 102.8 | 93.8 | 113.2 | 43.5 | 30.4 | 2659.9 | 1348.6 | 1362.4 | 3398.1 | 1524.9 | 1538.4 | 1.278 | 1.131 | 1.129 | 0.939 | 0.924 | 0.937 | 8.81 | -9.38 | 8.28 | 0.71 | 0.897 | 0.841 | 5.7 | -6.93 | -5.44 | 0.811 | 0.813 | 0.787 | -5.89 | 7.23 | -7.32 | 0.885 | 0.791 | 0.752 | 6.37 | -4.65 | -7.81 | Very Poor_Mixed | 1348.6 | 1524.9 | 1.129 | 0.939 | 9.38 | 0.897 | 7.81 | 0.1478 | 0.6376 | 0.2011 | 0.3825 | 1 | 0.1029 | 0.2802 | 0.3776 | 0.3776 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2283 | 1563.2 | 913.5 | 133.4 | 181.9 | 29.5 | 1260.7 | 7929.6 | 52.9 | 26.9 | 78.6 | 77.1 | 73.9 | 82.8 | 37 | 13.8 | 8762.6 | 7946.7 | 9699.8 | 16146.9 | 14036.2 | 18455.4 | 1.843 | 1.766 | 1.903 | 0.598 | 0.592 | 0.628 | -11.29 | 3.29 | 3.86 | 0.5 | 0.541 | 0.513 | 2.47 | 3.38 | 2.95 | 0.594 | 0.526 | 0.511 | 2 | -2.78 | 3.29 | 0.5 | 0.599 | 0.615 | 3.39 | 3.15 | 3.45 | Critical_DGA | 7946.7 | 14036.2 | 1.766 | 0.628 | 11.29 | 0.615 | 3.45 | 0.1219 | 0.8397 | 0.8623 | 0.9244 | 1 | 0.557 | 0.7931 | 0.6444 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_HV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
2284 | 220.4 | 190.1 | 72.2 | 63.1 | 3.3 | 438.5 | 2914.4 | 51.8 | 25.3 | 82.1 | 82.3 | 74.2 | 86.2 | 37.4 | 13 | 8446.3 | 7483.3 | 7268.5 | 15227.2 | 14078 | 13001.3 | 1.803 | 1.881 | 1.789 | 0.851 | 0.837 | 0.83 | 7.15 | -7.95 | 7.07 | 0.554 | 0.5 | 0.526 | 2.7 | 3.04 | 2.93 | 0.557 | 0.552 | 0.522 | 2.73 | -2.7 | 2.12 | 0.523 | 0.521 | 0.558 | 2.84 | 2.72 | 2.88 | Poor_Winding_TD_Cap | 7268.5 | 13001.3 | 1.789 | 0.851 | 7.95 | 0.558 | 3.04 | 0.8308 | 0.865 | 0.7637 | 0.9438 | 1 | 0.2437 | 0.8061 | 0.7743 | 0.7743 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2285 | 1482.7 | 833.9 | 134.5 | 176.6 | 34.3 | 1227.9 | 8029.6 | 32 | 46 | 106.6 | 101.2 | 94.5 | 114.4 | 44 | 29.2 | 1665.5 | 2097.4 | 2017.6 | 1903.1 | 2455.9 | 2169.3 | 1.143 | 1.171 | 1.075 | 0.938 | 0.844 | 0.898 | 8.81 | 8.18 | 8.27 | 0.858 | 0.808 | 0.758 | 6.25 | 5.66 | 8.29 | 0.83 | 0.746 | 0.851 | -5.74 | 6.98 | 6.46 | 0.803 | 0.731 | 0.806 | 8.99 | 7.01 | 7.35 | Very Poor_Mixed | 1665.5 | 1903.1 | 1.075 | 0.938 | 8.81 | 0.858 | 8.99 | 0.1207 | 0.6203 | 0.171 | 0.4276 | 1 | 0.1516 | 0.2695 | 0.3728 | 0.3728 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2286 | 1005.5 | 531.2 | 105.1 | 123.7 | 19.1 | 921 | 5574.8 | 43.5 | 34 | 89.4 | 88.2 | 81.6 | 98.6 | 40.2 | 26.6 | 5308.7 | 4697.7 | 5089.2 | 7681.1 | 6651.8 | 7403.6 | 1.447 | 1.416 | 1.455 | 0.714 | 0.734 | 0.741 | 5.5 | -5.49 | 5.52 | 0.648 | 0.628 | 0.733 | 4.32 | 4.18 | 5.18 | 0.599 | 0.607 | 0.763 | -5.95 | 6.03 | 5.24 | 0.652 | 0.62 | 0.697 | 4.99 | 5.96 | 4.35 | Poor_Mixed | 4697.7 | 6651.8 | 1.416 | 0.741 | 5.52 | 0.763 | 6.03 | 0.3994 | 0.7461 | 0.5367 | 0.5228 | 1 | 0.4341 | 0.4888 | 0.5779 | 0.5779 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2287 | 475.7 | 325.9 | 91.9 | 145 | 4.6 | 570.4 | 4609.7 | 54.3 | 24.5 | 101 | 103.2 | 90.7 | 110.7 | 43.4 | 15.8 | 7763.8 | 7324.9 | 7456.6 | 14240 | 12197.9 | 12642.1 | 1.834 | 1.665 | 1.695 | 0.567 | 0.561 | 0.634 | -3.32 | 3.17 | 4.15 | 0.629 | 0.554 | 2.416 | 3.35 | -4.39 | 2.92 | 0.572 | 0.52 | 0.611 | 3.79 | -3.22 | 2.76 | 0.606 | 0.573 | 0.548 | 3.01 | 2.93 | 3.79 | Critical_Thermal | 7324.9 | 12197.9 | 1.665 | 0.634 | 4.15 | 2.416 | 4.39 | 0.6354 | 0.8786 | 0.2354 | 0.8718 | 1 | 0.7006 | 0.6353 | 0.7038 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_B_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
2288 | 450.5 | 310.4 | 78.1 | 82.6 | 3.5 | 570.7 | 3746.7 | 34.2 | 44.3 | 77.8 | 78.5 | 73.4 | 86 | 36.2 | 16.9 | 4821.4 | 6582.6 | 217.7 | 7251.9 | 10303.6 | 343.9 | 1.504 | 1.565 | 1.58 | 0.606 | 0.641 | 0.641 | 4.03 | -4.06 | 3.86 | 0.58 | 0.571 | 0.618 | 2.46 | -3.46 | 2.49 | 0.524 | 0.548 | 0.511 | 3.14 | 2.35 | -3.2 | 0.62 | 0.621 | 0.586 | 3.45 | 2.57 | -3.74 | Critical_Oil | 217.7 | 343.9 | 1.504 | 0.641 | 4.06 | 0.621 | 3.74 | 0.736 | 0.6367 | 0.8481 | 0.8407 | 0.85 | 0.6206 | 0.7087 | 0.7377 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Moisture_PPM
2289 | 1463 | 871.5 | 133.5 | 170.6 | 33.4 | 1262.6 | 7366.9 | 33.3 | 46.5 | 102.3 | 101.1 | 89.4 | 111.3 | 43.2 | 29.2 | 2548.7 | 1447.4 | 1956.4 | 3202.3 | 1572.1 | 2344.6 | 1.256 | 1.086 | 1.198 | 0.89 | 0.889 | 0.855 | 7.58 | 8.61 | 8.11 | 0.785 | 0.878 | 0.846 | 6.96 | 5.96 | -6.69 | 0.757 | 0.802 | 0.785 | -6.87 | 7.13 | 4.76 | 0.821 | 0.881 | 0.751 | 5.6 | 7.32 | 6.27 | Very Poor_Mixed | 1447.4 | 1572.1 | 1.086 | 0.89 | 8.61 | 0.881 | 7.32 | 0.1323 | 0.6156 | 0.2458 | 0.4276 | 1 | 0.1786 | 0.2763 | 0.3876 | 0.3876 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2290 | 852.7 | 604.1 | 101.3 | 119.3 | 20.1 | 798.1 | 5283.9 | 47.5 | 34.6 | 91.1 | 88.6 | 82.4 | 99 | 39.4 | 25.8 | 4399.7 | 5117.4 | 4823.5 | 6251.4 | 7559.2 | 6689.4 | 1.421 | 1.477 | 1.387 | 0.721 | 0.756 | 0.702 | 5.99 | 5.7 | 4.67 | 0.713 | 0.648 | 0.748 | 5.15 | 5.31 | -4.28 | 0.623 | 0.66 | 0.659 | 5.45 | 5.63 | 4.86 | 0.628 | 0.689 | 0.638 | 4.67 | 4.39 | 4.66 | Poor_Mixed | 4399.7 | 6251.4 | 1.387 | 0.756 | 5.99 | 0.748 | 5.63 | 0.4224 | 0.7391 | 0.5207 | 0.5513 | 1 | 0.4405 | 0.4849 | 0.5829 | 0.5829 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2291 | 1615.5 | 958.3 | 139.6 | 186 | 32.3 | 1237.7 | 8283.6 | 30.6 | 45.5 | 107.1 | 104.9 | 94.4 | 116 | 43.7 | 33.7 | 2103.2 | 1889.9 | 1417 | 2313.9 | 2429.9 | 1487.8 | 1.1 | 1.286 | 1.05 | 0.967 | 0.951 | 0.976 | -9.73 | -9.08 | 9.62 | 0.953 | 0.909 | 0.951 | 8.25 | 9.53 | 9.5 | 0.942 | 0.791 | 0.945 | 6.84 | 9.41 | 8.48 | 0.777 | 0.876 | 0.951 | 6.32 | 8.19 | 7.51 | Very Poor_Mixed | 1417 | 1487.8 | 1.05 | 0.976 | 9.73 | 0.953 | 9.53 | 0.0902 | 0.6251 | 0.142 | 0.2552 | 1 | 0.0491 | 0.1388 | 0.3164 | 0.3164 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2292 | 880.3 | 482.8 | 102.4 | 112.9 | 16.1 | 824.4 | 4958.7 | 56.6 | 22.2 | 78.8 | 80.7 | 73 | 85.4 | 36 | 12.2 | 8610.3 | 8519.1 | 8616.2 | 16129.5 | 15227.8 | 15803.3 | 1.873 | 1.787 | 1.834 | 0.595 | 0.507 | 0.522 | 2.97 | -2.27 | 2 | 0.581 | 0.575 | 0.528 | 2.76 | -2.89 | 3.41 | 0.568 | 0.535 | 0.58 | 2.03 | -2.84 | 2 | 0.592 | 0.537 | 0.516 | 3 | 4.09 | -2 | Poor_DGA | 8519.1 | 15227.8 | 1.787 | 0.595 | 2.97 | 0.592 | 4.09 | 0.464 | 0.9238 | 0.826 | 0.9618 | 1 | 0.8584 | 0.7521 | 0.7731 | 0.7731 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2293 | 638 | 363 | 94.2 | 84 | 10.9 | 638.8 | 4345.7 | 51.3 | 28.5 | 84.9 | 84.8 | 76.3 | 88.1 | 37.9 | 18 | 8580.7 | 8676.4 | 9264.2 | 16118.8 | 16903.6 | 16954.4 | 1.878 | 1.948 | 1.83 | 0.624 | 0.621 | 0.638 | -4.56 | 3.86 | 4.2 | 0.572 | 0.583 | 0.592 | -3.28 | -3.63 | -3.53 | 0.542 | 0.588 | 0.56 | 2.5 | 3.6 | 3.38 | 0.645 | 0.568 | 0.541 | -2.21 | 3.56 | 3.22 | Fair_Mixed | 8580.7 | 16118.8 | 1.83 | 0.638 | 4.56 | 0.645 | 3.63 | 0.6022 | 0.8164 | 0.695 | 0.8084 | 1 | 0.6087 | 0.6894 | 0.7278 | 0.7278 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2294 | 912.8 | 513.5 | 114.1 | 134.7 | 22 | 957.5 | 5859.9 | 54.3 | 24.4 | 76.5 | 75.2 | 74 | 86.3 | 35.8 | 11.7 | 8616.9 | 8007.2 | 9733.4 | 16031.4 | 14964 | 18717.7 | 1.86 | 1.869 | 1.923 | 0.523 | 0.582 | 0.542 | -3.03 | -2.88 | -2.94 | 0.518 | 0.502 | 0.5 | 2.35 | 2.47 | 2.84 | 0.5 | 0.538 | 0.52 | 2.09 | 2.98 | -2.52 | 0.5 | 0.526 | 0.5 | -2.08 | -2.61 | 2.22 | Poor_DGA | 8007.2 | 14964 | 1.86 | 0.582 | 3.03 | 0.538 | 2.98 | 0.3675 | 0.8804 | 0.8969 | 0.9724 | 1 | 0.7952 | 0.9069 | 0.7704 | 0.7704 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2295 | 1442.5 | 852.3 | 131.9 | 175.9 | 32.6 | 1253.5 | 7872.4 | 38.4 | 41.5 | 102.8 | 103.3 | 92.7 | 110.8 | 42.7 | 30.3 | 3058.1 | 3456.6 | 3521 | 3737.1 | 4331 | 4496.8 | 1.222 | 1.253 | 1.277 | 0.868 | 0.85 | 0.898 | 7.43 | 7.49 | 8.41 | 0.771 | 0.725 | 0.696 | 7.8 | 6.58 | 6.36 | 0.866 | 0.703 | 0.797 | 6.85 | 5.33 | 6.88 | 0.771 | 0.812 | 0.833 | -4.85 | 6.45 | 8.13 | Very Poor_Mixed | 3058.1 | 3737.1 | 1.222 | 0.898 | 8.41 | 0.866 | 8.13 | 0.1308 | 0.6645 | 0.2176 | 0.3863 | 1 | 0.1996 | 0.3075 | 0.3968 | 0.3968 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2296 | 319.6 | 136.1 | 80.3 | 60.2 | 2.2 | 428.1 | 2832.8 | 30.6 | 48.1 | 78.1 | 76.2 | 71.8 | 82.2 | 35.3 | 13.2 | 4731.9 | 4773.3 | 5168.3 | 7256.2 | 6654.8 | 8140.3 | 1.533 | 1.394 | 1.575 | 0.624 | 0.642 | 0.669 | 4.52 | -4.85 | 5.03 | 0.52 | 0.572 | 0.5 | 22.36 | 3.4 | 2.52 | 0.575 | 0.563 | 0.547 | 3.31 | 2.23 | -3.01 | 0.607 | 0.638 | 0.546 | 2.95 | 2.8 | 2.42 | Critical_Oil | 4731.9 | 6654.8 | 1.394 | 0.669 | 5.03 | 0.638 | 22.36 | 0.8538 | 0.6007 | 0.9065 | 0.939 | 1 | 0.5554 | 0.7179 | 0.7901 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_R_CapChange_pct>=10% abs: critical bushing capacitance change | Moisture_PPM
2297 | 1142 | 650.4 | 113.4 | 141.3 | 22.9 | 868.5 | 6090.8 | 46.7 | 32 | 95.2 | 93 | 82.9 | 99.1 | 40.4 | 23.9 | 6030 | 5210.6 | 6140.4 | 9997.1 | 7598.6 | 10216.1 | 1.658 | 1.458 | 1.664 | 0.749 | 0.742 | 0.749 | -5.43 | 5.43 | 5.8 | 0.673 | 0.685 | 0.76 | 5.05 | 5.28 | 5.78 | 0.662 | 0.576 | 0.675 | 4.74 | 4.62 | 5.89 | 0.677 | 0.652 | 0.732 | 5.12 | 4.34 | 3.95 | Poor_Mixed | 5210.6 | 7598.6 | 1.458 | 0.749 | 5.8 | 0.76 | 5.89 | 0.3324 | 0.7703 | 0.456 | 0.6177 | 1 | 0.4165 | 0.4734 | 0.5556 | 0.5556 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2298 | 561.8 | 365.7 | 87.5 | 91.8 | 49.5 | 634 | 4520.5 | 55.8 | 24.3 | 80.7 | 81.9 | 75.9 | 87 | 36.5 | 15.5 | 8791.7 | 8435.3 | 8966 | 16435.8 | 15610.5 | 16487.4 | 1.869 | 1.851 | 1.839 | 0.59 | 0.583 | 0.651 | 3.48 | 3.43 | 4.08 | 0.61 | 0.616 | 0.956 | -2.79 | 3.16 | 9.84 | 0.619 | 0.608 | 0.571 | 3.18 | 3.94 | -3.73 | 0.53 | 0.655 | 0.553 | 2.56 | 2.58 | -2.63 | Critical_Bushing_TD_Cap | 8435.3 | 15610.5 | 1.839 | 0.651 | 4.08 | 0.956 | 9.84 | 0.4668 | 0.8821 | 0.7662 | 0.88 | 1 | 0.6664 | 0.5967 | 0.7039 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2299 | 187.2 | 149.4 | 67.8 | 50 | 1 | 407.2 | 3047.6 | 60 | 20 | 76.4 | 75 | 72.2 | 80 | 36.1 | 13.2 | 10000 | 9639.7 | 9988.6 | 19930.6 | 19279.5 | 19618.3 | 1.993 | 2 | 1.964 | 0.556 | 0.5 | 0.5 | 2.31 | 2.71 | 2.6 | 0.52 | 0.516 | 0.5 | -2.2 | 2.36 | -2.14 | 0.52 | 0.5 | 0.525 | 2.48 | 2.11 | 2.5 | 0.53 | 0.511 | 0.515 | 2.53 | 2.48 | 3.03 | Good_Mixed | 9639.7 | 19279.5 | 1.964 | 0.556 | 2.71 | 0.53 | 3.03 | 0.9677 | 1 | 0.9486 | 0.939 | 1 | 0.9054 | 0.8816 | 0.9492 | 0.9492 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
2300 | 873.5 | 482.1 | 93.7 | 110.8 | 19.5 | 810.8 | 5330.2 | 45.4 | 33.2 | 87.9 | 89.8 | 81.5 | 95.3 | 39 | 24.5 | 6194.8 | 4873.8 | 5709.6 | 9941.7 | 6863.5 | 9099.2 | 1.605 | 1.408 | 1.594 | 0.747 | 0.763 | 0.783 | 6.35 | 6.06 | -6.36 | 0.653 | 0.706 | 0.675 | 5.09 | 5.75 | -4.67 | 0.706 | 0.672 | 0.677 | 5.22 | -4.8 | 3.67 | 0.62 | 0.671 | 0.664 | 4.37 | 4.89 | -3.31 | Poor_Mixed | 4873.8 | 6863.5 | 1.408 | 0.783 | 6.36 | 0.706 | 5.75 | 0.4496 | 0.7556 | 0.5608 | 0.597 | 1 | 0.3631 | 0.4896 | 0.588 | 0.588 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2301 | 1527.1 | 843.6 | 137 | 167.7 | 31.9 | 1203 | 7740.2 | 35.2 | 46 | 108.3 | 106.5 | 94.3 | 119.2 | 45.3 | 30.6 | 1305.3 | 2048.4 | 3363.6 | 1473.6 | 2348.2 | 4145.9 | 1.129 | 1.146 | 1.233 | 0.946 | 0.944 | 0.97 | 9.11 | -9.26 | 9.02 | 0.756 | 0.728 | 0.721 | -5.56 | 8.53 | -6.92 | 0.827 | 0.863 | 0.718 | 7.89 | 7.35 | 7.46 | 0.844 | 0.77 | 0.836 | 7.29 | 6.07 | -6.6 | Very Poor_Mixed | 1305.3 | 1473.6 | 1.129 | 0.97 | 9.26 | 0.863 | 8.53 | 0.139 | 0.6203 | 0.0995 | 0.3749 | 1 | 0.0739 | 0.2808 | 0.3588 | 0.3588 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2302 | 1521.7 | 849.2 | 135.4 | 184.3 | 34.3 | 1244.2 | 8272.3 | 31.9 | 48 | 105 | 106.9 | 91.7 | 116.2 | 43.5 | 31.2 | 690 | 1311.8 | 782.4 | 1200 | 1473.2 | 1200 | 1.739 | 1.123 | 1.534 | 0.912 | 0.949 | 0.926 | 8.89 | 9.17 | 9.64 | 0.832 | 0.828 | 0.92 | 6.85 | -8.76 | 8.24 | 0.854 | 0.929 | 0.902 | 7.15 | 6.4 | 6.89 | 0.945 | 0.712 | 0.811 | 8.9 | 7 | 7.85 | Very Poor_Mixed | 690 | 1200 | 1.123 | 0.949 | 9.64 | 0.945 | 8.9 | 0.1042 | 0.6016 | 0.1582 | 0.3521 | 1 | 0.0853 | 0.1956 | 0.3388 | 0.3388 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2303 | 604.5 | 328.9 | 90.5 | 95.5 | 2.1 | 652.9 | 3866.5 | 58 | 22.4 | 80.1 | 83 | 77.1 | 87.1 | 36.8 | 11 | 9325.5 | 258.5 | 8120.5 | 18650.9 | 411.5 | 14673.2 | 2 | 1.592 | 1.807 | 0.514 | 0.526 | 0.524 | 2.68 | 2.61 | -2.36 | 0.537 | 0.643 | 0.958 | 2.4 | 2.99 | 9.84 | 0.55 | 0.569 | 0.603 | -2.29 | 3.04 | 2.94 | 0.57 | 0.52 | 0.561 | 3.17 | -2.56 | -3.6 | Critical_Bushing_TD_Cap | 258.5 | 411.5 | 1.592 | 0.526 | 2.68 | 0.958 | 9.84 | 0.7161 | 0.9193 | 0.7519 | 0.9858 | 0.85 | 0.8724 | 0.6462 | 0.7883 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2304 | 1473.2 | 838.5 | 135.9 | 179.7 | 33.6 | 1229.9 | 7485.4 | 37.5 | 45 | 102.1 | 100.8 | 91.8 | 111.8 | 44.2 | 33 | 1412 | 1382.9 | 1652.6 | 1544.5 | 1452.1 | 1987 | 1.094 | 1.05 | 1.202 | 0.941 | 0.906 | 0.865 | 9.26 | 8.76 | 8 | 0.872 | 0.869 | 0.751 | 9.25 | -7.37 | 5.47 | 0.89 | 0.855 | 0.803 | 7.64 | -6.56 | 6.58 | 0.801 | 0.929 | 0.854 | 8.58 | 7.44 | 6.93 | Very Poor_Mixed | 1382.9 | 1452.1 | 1.05 | 0.941 | 9.26 | 0.929 | 9.25 | 0.1269 | 0.6299 | 0.2252 | 0.2826 | 1 | 0.1311 | 0.2133 | 0.3607 | 0.3607 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2305 | 364.2 | 229.4 | 79.6 | 72.2 | 1 | 462.8 | 3588.7 | 51.8 | 29.7 | 75.7 | 76.6 | 72.5 | 83.5 | 35.9 | 13.5 | 8743.7 | 7613.7 | 9160.7 | 15710.5 | 13275.2 | 17046.8 | 1.797 | 1.744 | 1.861 | 0.594 | 0.541 | 0.551 | -2.81 | 2.26 | 2.92 | 0.527 | 0.564 | 0.5 | 2 | 2.38 | -2.17 | 0.516 | 0.54 | 0.545 | -2.23 | 2.13 | -2.31 | 0.5 | 0.5 | 0.5 | 2 | 2.94 | 2.86 | Fair_Oil | 7613.7 | 13275.2 | 1.744 | 0.594 | 2.92 | 0.564 | 2.94 | 0.8819 | 0.8 | 0.9137 | 0.9318 | 1 | 0.7942 | 0.8858 | 0.8851 | 0.8851 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2306 | 850.5 | 563.9 | 104.3 | 112.6 | 20.7 | 866 | 5389.9 | 57.9 | 21.2 | 78.3 | 78.2 | 71.1 | 80.5 | 36.3 | 11.2 | 9178 | 8962.9 | 8304.6 | 17134.8 | 17454.3 | 15198.6 | 1.867 | 1.947 | 1.83 | 0.562 | 0.575 | 0.612 | 2.42 | 2.67 | 3.4 | 0.5 | 0.597 | 0.5 | -2.96 | -2.44 | 2.04 | 0.501 | 0.5 | 0.533 | 2.47 | -2.38 | 2.23 | 0.529 | 0.504 | 0.516 | 2 | -2.2 | 2.17 | Fair_DGA | 8304.6 | 15198.6 | 1.83 | 0.612 | 3.4 | 0.597 | 2.96 | 0.4184 | 0.9486 | 0.8939 | 0.9821 | 1 | 0.7524 | 0.8936 | 0.7831 | 0.7831 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2307 | 1585.4 | 941.7 | 148.3 | 191.6 | 34.2 | 1346.2 | 8609.3 | 58.2 | 23.5 | 83 | 82.8 | 74.5 | 85.6 | 36.7 | 17.4 | 6654 | 7553.1 | 443 | 10869.3 | 13306.1 | 544.9 | 1.633 | 1.762 | 1.23 | 0.572 | 0.543 | 0.61 | 4.1 | -3.29 | -3.77 | 0.605 | 0.581 | 0.611 | 2.67 | 4.05 | 3.16 | 0.608 | 0.653 | 0.613 | -3.11 | 3.84 | 3.28 | 0.565 | 0.603 | 0.559 | -3.84 | 3.19 | 3.45 | Critical_DGA | 443 | 544.9 | 1.23 | 0.61 | 4.1 | 0.653 | 4.05 | 0.0581 | 0.8969 | 0.7571 | 0.8262 | 0.85 | 0.7058 | 0.6403 | 0.5893 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2308 | 1673 | 867.4 | 144.1 | 186 | 29.7 | 1321.4 | 7941.5 | 33.1 | 48.9 | 106.4 | 104.1 | 91.6 | 115.4 | 44.1 | 32.5 | 1666.9 | 1227 | 2017.7 | 1771.5 | 1288.4 | 2305.9 | 1.063 | 1.05 | 1.143 | 0.966 | 0.948 | 0.899 | 9.44 | -8.62 | 8.9 | 0.941 | 0.827 | 0.869 | 5.39 | 6.16 | 5.53 | 0.879 | 0.929 | 0.839 | -5.8 | 7.18 | -6.95 | 0.937 | 0.863 | 0.957 | -7.68 | -6.47 | -9.54 | Very Poor_Mixed | 1227 | 1288.4 | 1.05 | 0.966 | 9.44 | 0.957 | 9.54 | 0.0995 | 0.5933 | 0.1662 | 0.302 | 1 | 0.0919 | 0.1909 | 0.335 | 0.335 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2309 | 110.9 | 158.1 | 70.5 | 60 | 4 | 353 | 2728.4 | 56.3 | 23 | 78.2 | 78.4 | 71.3 | 85.1 | 36.1 | 14.3 | 8192.5 | 7948.8 | 8094.8 | 14224.6 | 14812.3 | 14891.9 | 1.736 | 1.863 | 1.84 | 0.555 | 0.622 | 0.587 | -3.85 | 3.08 | 4 | 0.537 | 0.5 | 0.529 | 2.52 | 2.52 | 2.92 | 0.724 | 0.584 | 0.554 | 6.24 | 3.32 | 2.27 | 0.522 | 0.55 | 0.598 | 2.7 | -3.22 | -3.77 | Poor_Bushing_TD_Cap | 7948.8 | 14224.6 | 1.736 | 0.622 | 4 | 0.724 | 6.24 | 0.8601 | 0.9067 | 0.8688 | 0.9118 | 1 | 0.6929 | 0.7298 | 0.8447 | 0.8447 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2310 | 698.1 | 328.7 | 90.5 | 88.7 | 3.6 | 716.4 | 4256.2 | 55.8 | 23.9 | 81.4 | 79.4 | 76.1 | 88.3 | 37 | 16.3 | 8476.9 | 7994.8 | 9103.4 | 15486.1 | 14699.4 | 16639 | 1.827 | 1.839 | 1.828 | 0.956 | 1.349 | 0.961 | 9.7 | -9.69 | -8.99 | 0.527 | 0.633 | 0.621 | -3.88 | -3.9 | 3.7 | 0.572 | 0.513 | 0.641 | 3.33 | -3.17 | 2.93 | 0.553 | 0.608 | 0.623 | 3.81 | 4.07 | 3.22 | Critical_Winding_TD_Cap | 7994.8 | 14699.4 | 1.827 | 1.349 | 9.7 | 0.641 | 4.07 | 0.6718 | 0.8894 | 0.771 | 0.8578 | 1 | 0.0449 | 0.6625 | 0.6802 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_TanDelta_pct>=1.0%: critical winding tan delta | C2H2
2311 | 956.1 | 512.6 | 106.8 | 130.2 | 20.5 | 825.4 | 5658.8 | 60 | 22.5 | 75.9 | 75.3 | 70 | 80 | 35.9 | 14.1 | 9998.3 | 9263.9 | 9387.3 | 19522.3 | 18098.3 | 18546.9 | 1.953 | 1.954 | 1.976 | 0.503 | 0.537 | 0.513 | 2.18 | 2 | 2.02 | 0.609 | 0.545 | 0.526 | 2.91 | 2.2 | 2.89 | 0.509 | 0.54 | 0.523 | 2.61 | 3.26 | 3.24 | 0.5 | 0.531 | 0.514 | -2.68 | 2.8 | -2.59 | Fair_DGA | 9263.9 | 18098.3 | 1.953 | 0.537 | 2.18 | 0.609 | 3.26 | 0.4005 | 0.9171 | 0.9735 | 0.9169 | 1 | 0.9272 | 0.8136 | 0.7896 | 0.7896 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2312 | 1516.1 | 858.3 | 133.7 | 176.8 | 34.3 | 1131.2 | 8338.4 | 31.5 | 45.7 | 108.1 | 104.7 | 94.1 | 114.3 | 44.5 | 29.6 | 1382.8 | 1821.1 | 1521.9 | 1559.9 | 2157.4 | 1654.5 | 1.128 | 1.185 | 1.087 | 0.939 | 0.899 | 0.888 | -9.4 | -8.9 | 9.26 | 0.871 | 0.831 | 0.666 | 4.96 | -5.73 | 6.73 | 0.753 | 0.801 | 0.719 | 6.72 | -6.33 | 5.91 | 0.86 | 0.826 | 0.782 | -6.15 | 5.39 | 7.29 | Very Poor_Mixed | 1382.8 | 1559.9 | 1.087 | 0.939 | 9.4 | 0.871 | 7.29 | 0.1229 | 0.6232 | 0.1421 | 0.4126 | 1 | 0.1017 | 0.3082 | 0.3701 | 0.3701 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2313 | 192.7 | 124.6 | 71.2 | 50 | 3.7 | 439.3 | 2655.6 | 57.2 | 22.3 | 76.8 | 76.8 | 71.2 | 82.6 | 35.4 | 14.8 | 9504.8 | 10000 | 9270.1 | 19009.6 | 20000 | 17903.7 | 2 | 2 | 1.931 | 0.583 | 0.5 | 0.514 | -2.3 | 2.33 | 2.31 | 0.551 | 0.5 | 0.5 | -2 | 2.65 | -2 | 0.507 | 0.509 | 0.5 | -2 | 2 | 2 | 0.574 | 0.558 | 0.537 | 2.09 | -2.44 | 2 | Good_Mixed | 9270.1 | 17903.7 | 1.931 | 0.583 | 2.33 | 0.574 | 2.65 | 0.8623 | 0.9215 | 0.9165 | 0.8988 | 1 | 0.8887 | 0.8836 | 0.9062 | 0.9062 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2314 | 1539.5 | 803.2 | 135.2 | 171.8 | 34 | 1176.2 | 7961.8 | 33.8 | 43.9 | 100.2 | 100.5 | 90.2 | 107.5 | 44.3 | 31.1 | 1435.9 | 1353.7 | 3102.1 | 1606.6 | 1475.4 | 3843.7 | 1.119 | 1.09 | 1.239 | 0.961 | 0.94 | 0.839 | 8.98 | 8.79 | 8.18 | 0.936 | 0.733 | 0.854 | -6.73 | 6.29 | 7.25 | 0.826 | 0.741 | 0.827 | 8.12 | 6.77 | 7.42 | 0.858 | 0.839 | 0.656 | 7.7 | 6.66 | 8.26 | Very Poor_Mixed | 1353.7 | 1475.4 | 1.09 | 0.961 | 8.98 | 0.936 | 8.26 | 0.1314 | 0.6406 | 0.2678 | 0.3559 | 1 | 0.1264 | 0.2551 | 0.3779 | 0.3779 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2315 | 1190.4 | 659.2 | 109.8 | 133.1 | 27.1 | 972.6 | 6208.6 | 46.6 | 32.7 | 90.9 | 90.4 | 81.8 | 98.2 | 40.6 | 25.5 | 5746.3 | 6263.4 | 5348.3 | 9072.9 | 9871 | 7852.2 | 1.579 | 1.576 | 1.468 | 0.738 | 0.683 | 0.757 | 5.74 | 4.96 | 5.63 | 0.699 | 0.669 | 0.587 | 4.81 | 4.96 | 5.74 | 0.725 | 0.639 | 0.638 | 4.29 | -4.78 | 4.4 | 0.726 | 0.701 | 0.606 | 4.85 | -4.47 | 5.01 | Poor_Mixed | 5348.3 | 7852.2 | 1.468 | 0.757 | 5.74 | 0.726 | 5.74 | 0.3026 | 0.7617 | 0.5101 | 0.562 | 1 | 0.4415 | 0.4934 | 0.5568 | 0.5568 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2316 | 579.9 | 375.9 | 88.2 | 94.2 | 11.7 | 659.2 | 4092.4 | 57.5 | 21.2 | 78.6 | 77.6 | 72.2 | 81.3 | 35 | 14.5 | 9148.5 | 9311.2 | 9546.2 | 17881.4 | 18212.8 | 18753.5 | 1.955 | 1.956 | 1.964 | 0.532 | 0.553 | 0.5 | -2.12 | -2.67 | 2.33 | 0.545 | 0.54 | 0.519 | 2.99 | 2.49 | 2 | 0.572 | 0.52 | 0.501 | 3.07 | 2.36 | -2.47 | 0.569 | 0.546 | 0.515 | 3.14 | -2.42 | 2.54 | Fair_DGA | 9148.5 | 17881.4 | 1.955 | 0.553 | 2.67 | 0.572 | 3.14 | 0.5911 | 0.9486 | 0.8878 | 0.9067 | 1 | 0.8858 | 0.8093 | 0.8254 | 0.8254 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2317 | 133.3 | 120.2 | 65.4 | 50 | 1.2 | 350 | 2500 | 58.4 | 20 | 78.8 | 76.3 | 71.5 | 80.1 | 35.6 | 10.4 | 9717.1 | 8483.8 | 9749.7 | 19434.3 | 15525.6 | 19056.2 | 2 | 1.83 | 1.955 | 0.532 | 0.547 | 0.5 | -2.05 | 2.56 | 2.35 | 0.582 | 0.539 | 0.536 | 2 | 2 | -2 | 0.539 | 0.567 | 0.506 | -2.74 | 2 | 2.79 | 0.5 | 0.532 | 0.524 | -2.48 | -2.22 | -2 | Good_Mixed | 8483.8 | 15525.6 | 1.83 | 0.547 | 2.56 | 0.582 | 2.79 | 0.9632 | 1 | 0.9108 | 0.9955 | 1 | 0.8934 | 0.8347 | 0.937 | 0.937 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2318 | 762.4 | 512.9 | 101.8 | 116.2 | 14.6 | 791.1 | 5301.6 | 57.6 | 22.4 | 77.8 | 81 | 71.9 | 82.7 | 37.2 | 10 | 9478.6 | 9057.4 | 8771.3 | 18309.8 | 17696.9 | 16863.5 | 1.932 | 1.954 | 1.923 | 0.611 | 0.537 | 0.594 | 3.38 | 2.1 | -3.18 | 0.5 | 0.513 | 0.5 | 2.23 | 2.51 | 2.99 | 0.542 | 0.523 | 0.51 | 2.39 | -2.51 | 2.11 | 0.501 | 0.5 | 0.502 | 2.49 | -2.59 | 2.04 | Fair_DGA | 8771.3 | 16863.5 | 1.923 | 0.611 | 3.38 | 0.542 | 2.99 | 0.4781 | 0.9193 | 0.8503 | 1 | 1 | 0.7558 | 0.9122 | 0.7949 | 0.7949 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2319 | 692.2 | 362.9 | 87 | 91.6 | 1.4 | 647.6 | 3950.5 | 31.3 | 48.6 | 76.7 | 81.3 | 72.6 | 86.8 | 36.8 | 16.2 | 4403.9 | 4590.1 | 4435.9 | 6336.8 | 6678.4 | 6672.6 | 1.439 | 1.455 | 1.504 | 0.68 | 0.659 | 0.603 | 4.45 | -22.65 | 4.54 | 0.599 | 0.566 | 0.548 | 2.84 | 3.52 | -2.68 | 0.528 | 0.605 | 0.536 | -2 | 2.12 | 2.79 | 0.549 | 0.513 | 0.523 | 3.28 | 2.23 | 2.88 | Critical_Oil | 4403.9 | 6336.8 | 1.439 | 0.68 | 22.65 | 0.605 | 3.52 | 0.7365 | 0.5961 | 0.8349 | 0.8607 | 1 | 0.4745 | 0.7668 | 0.7466 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | Moisture_PPM
2320 | 1208.2 | 639.3 | 121.4 | 149.3 | 22.8 | 920.8 | 6296.9 | 57.8 | 20.2 | 77.8 | 75.8 | 70 | 81.5 | 35.4 | 13.7 | 8074.8 | 9391.3 | 7582.5 | 15306.7 | 18438.9 | 14212.2 | 1.896 | 1.963 | 1.874 | 0.627 | 0.62 | 0.594 | 4.06 | 3.88 | 3.78 | 0.527 | 0.536 | 0.536 | 3.01 | 3.1 | 2.78 | 0.514 | 0.55 | 0.514 | 2.81 | 3.11 | 2.09 | 0.547 | 0.577 | 0.535 | 3.66 | -2.89 | -2.83 | Poor_DGA | 7582.5 | 14212.2 | 1.874 | 0.627 | 4.06 | 0.577 | 3.66 | 0.3074 | 0.984 | 0.9389 | 0.9269 | 1 | 0.643 | 0.7849 | 0.7265 | 0.7265 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2321 | 778.3 | 373.6 | 86.5 | 90.4 | 10.4 | 673.4 | 4235.5 | 53.6 | 25.3 | 83.4 | 85.7 | 77.5 | 91.1 | 38.3 | 19.9 | 7256.8 | 8867.9 | 7057 | 12620.8 | 16489.8 | 11669.3 | 1.739 | 1.859 | 1.654 | 0.615 | 0.595 | 0.579 | 4.14 | 3.94 | -3.97 | 0.582 | 0.565 | 0.563 | -2.73 | 3.69 | -3.61 | 0.61 | 0.603 | 0.539 | 3.08 | 3.76 | -3.5 | 0.561 | 0.626 | 0.615 | 2.81 | 2.59 | 4.5 | Fair_Mixed | 7057 | 11669.3 | 1.654 | 0.615 | 4.14 | 0.626 | 4.5 | 0.588 | 0.865 | 0.6738 | 0.7499 | 1 | 0.6572 | 0.6681 | 0.7279 | 0.7279 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2322 | 274.3 | 214.3 | 69.2 | 59.7 | 1 | 460.5 | 3169.3 | 59.7 | 21.2 | 75.3 | 78.9 | 70.9 | 80.5 | 35.9 | 14 | 7146.8 | 8519.2 | 8193.7 | 12224.6 | 14381.9 | 14355 | 1.71 | 1.688 | 1.752 | 0.546 | 0.528 | 0.557 | 2.79 | -2.96 | -3.16 | 0.515 | 0.539 | 0.501 | -2.22 | -2 | 2.49 | 0.531 | 0.572 | 0.529 | 3.06 | -2 | -2.69 | 0.522 | 0.547 | 0.529 | 2.91 | 2.17 | -2.45 | Fair_IR_PI | 7146.8 | 12224.6 | 1.688 | 0.557 | 3.16 | 0.572 | 3.06 | 0.9192 | 0.9486 | 0.9267 | 0.9194 | 1 | 0.8 | 0.8283 | 0.9034 | 0.9034 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_TV_TanDelta_pct
2323 | 1507.4 | 956.6 | 136.6 | 189.5 | 34.3 | 1267.5 | 8103.4 | 57 | 24.9 | 82.2 | 84.7 | 76.1 | 91.7 | 35 | 15.2 | 8841.5 | 8375.4 | 8006.1 | 6979.8 | 15283.2 | 13818.4 | 0.789 | 1.825 | 1.726 | 0.588 | 0.54 | 0.57 | 3.3 | 2.73 | 2.35 | 0.584 | 0.513 | 0.594 | -3.49 | 3.13 | 3.22 | 0.559 | 0.606 | 0.594 | -3.94 | -3.83 | -2.68 | 0.541 | 0.584 | 0.548 | 2.99 | -2.88 | -2.81 | Critical_DGA | 8006.1 | 6979.8 | 0.789 | 0.588 | 3.3 | 0.606 | 3.94 | 0.088 | 0.8717 | 0.7137 | 0.8882 | 0.8187 | 0.7788 | 0.705 | 0.6093 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
2324 | 390.4 | 291.5 | 82.2 | 67.7 | 1 | 510.7 | 3502.7 | 45.4 | 36.2 | 76.5 | 75 | 73.7 | 81.4 | 35.5 | 12.6 | 7368.1 | 8134 | 7130.8 | 12240.3 | 14192.2 | 12704.1 | 1.661 | 1.745 | 1.782 | 0.557 | 0.549 | 0.618 | 2.42 | 3.55 | 3.85 | 0.58 | 0.599 | 0.605 | 2.68 | 2.83 | 3.16 | 0.515 | 0.542 | 0.575 | 2.85 | 2.08 | 2.26 | 0.563 | 0.514 | 0.538 | -3.09 | 3.63 | 2.38 | Poor_Oil | 7130.8 | 12240.3 | 1.661 | 0.618 | 3.85 | 0.605 | 3.63 | 0.8694 | 0.7208 | 0.9303 | 0.953 | 1 | 0.7365 | 0.7487 | 0.8424 | 0.8424 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2325 | 117.1 | 138.9 | 70.7 | 51.4 | 2.8 | 417.5 | 2500 | 60 | 20.6 | 75.1 | 76.3 | 72.5 | 82.2 | 36 | 13.7 | 4904.5 | 6129.5 | 4582.1 | 7581.9 | 9540.2 | 6516.1 | 1.546 | 1.556 | 1.422 | 0.623 | 0.563 | 0.586 | 3.79 | 3.18 | 2.48 | 0.504 | 0.51 | 0.5 | 2.4 | -2.08 | -2.42 | 0.539 | 0.5 | 0.5 | -2.1 | -2 | 2.52 | 0.534 | 0.547 | 0.509 | 2.05 | 2.25 | 2.21 | Poor_IR_PI | 4582.1 | 6516.1 | 1.422 | 0.623 | 3.79 | 0.547 | 2.52 | 0.8862 | 0.9672 | 0.9335 | 0.9269 | 1 | 0.7215 | 0.9027 | 0.9008 | 0.9008 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2326 | 517.7 | 217.7 | 83.3 | 73.3 | 77.8 | 576.3 | 3756.7 | 30.6 | 49.4 | 82.5 | 84.1 | 76.8 | 88.4 | 37.8 | 19 | 4404.9 | 5045.7 | 5085.7 | 5967.4 | 7458.3 | 7514.5 | 1.355 | 1.478 | 1.478 | 0.672 | 0.702 | 0.727 | 4.39 | 5.18 | 5.76 | 0.549 | 0.556 | 0.567 | -2.25 | 2.77 | 3.27 | 0.569 | 0.56 | 0.573 | -2.75 | 3.03 | 2.84 | 0.518 | 0.521 | 0.509 | 2.85 | 2.08 | 3.25 | Critical_Oil | 4404.9 | 5967.4 | 1.355 | 0.727 | 5.76 | 0.573 | 3.27 | 0.5271 | 0.5888 | 0.7139 | 0.778 | 1 | 0.4835 | 0.7714 | 0.6793 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2327 | 620.3 | 441.2 | 89.3 | 101.5 | 13.8 | 756.3 | 4506.3 | 49.2 | 32 | 90.7 | 91.5 | 80.8 | 96.4 | 39.2 | 22 | 7327.4 | 5359.5 | 5330.9 | 12587.5 | 8837.7 | 8227.4 | 1.718 | 1.649 | 1.543 | 0.631 | 0.74 | 0.652 | -5.02 | 6.7 | 4.46 | 0.655 | 0.702 | 0.635 | 4.51 | 4.59 | 4.75 | 0.579 | 0.592 | 0.635 | 4.64 | 4.64 | 4.08 | 0.664 | 0.578 | 0.601 | -4.83 | 3.36 | -4.3 | Poor_Mixed | 5330.9 | 8227.4 | 1.543 | 0.74 | 6.7 | 0.702 | 4.83 | 0.5393 | 0.7703 | 0.5287 | 0.6819 | 1 | 0.4948 | 0.5604 | 0.6444 | 0.6444 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2328 | 208.3 | 180.5 | 78.3 | 71.1 | 2.7 | 411.3 | 2578.6 | 60 | 21.3 | 75 | 75.1 | 70.1 | 80 | 35 | 11.9 | 7001.3 | 7559 | 7353.6 | 11277.3 | 12444.2 | 12733.1 | 1.611 | 1.646 | 1.732 | 0.573 | 0.603 | 0.566 | 2.51 | -3.5 | -3.25 | 0.521 | 0.529 | 0.554 | 2 | 2.8 | -2.28 | 0.564 | 0.566 | 0.551 | 2.24 | 2.35 | -3.1 | 0.584 | 0.564 | 0.547 | 2.92 | -2.63 | 2.7 | Fair_IR_PI | 7001.3 | 11277.3 | 1.611 | 0.603 | 3.5 | 0.584 | 3.1 | 0.8371 | 0.9458 | 0.9948 | 0.9682 | 1 | 0.7374 | 0.7649 | 0.8716 | 0.8716 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2329 | 432.7 | 240.9 | 82.2 | 80.8 | 1 | 567.9 | 4304.2 | 56.5 | 76.6 | 80.5 | 81.5 | 73.1 | 84 | 35.7 | 13.2 | 7525.4 | 7661.3 | 7360.1 | 12701.9 | 13553 | 12997.3 | 1.688 | 1.769 | 1.766 | 0.99 | 0.935 | 0.915 | 9.78 | -8.61 | 7.97 | 0.556 | 0.593 | 0.604 | 2.87 | 3.09 | -3.25 | 0.556 | 0.512 | 0.591 | -2.91 | 3.77 | 3.57 | 0.608 | 0.608 | 0.606 | -2.28 | 3.53 | 3.23 | Critical_Winding_TD_Cap | 7360.1 | 12701.9 | 1.688 | 0.99 | 9.78 | 0.608 | 3.77 | 0.84 | 0.5833 | 0.8118 | 0.939 | 1 | 0.0962 | 0.6857 | 0.705 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2330 | 265.4 | 213.2 | 71.5 | 57.4 | 1.3 | 466.8 | 3059.2 | 56 | 25.6 | 78.8 | 80.8 | 72.1 | 82.1 | 35.7 | 13.5 | 9102.3 | 9858.8 | 10000 | 17971.7 | 19144.4 | 20000 | 1.974 | 1.942 | 2 | 0.586 | 0.504 | 0.546 | 3.04 | 2.12 | 2.27 | 0.664 | 0.546 | 0.571 | 2.23 | 2.52 | -2.42 | 0.552 | 0.536 | 0.592 | 2 | -2.12 | -2 | 0.506 | 0.718 | 0.54 | 2.36 | -5.86 | 2.57 | Poor_Bushing_TD_Cap | 9102.3 | 17971.7 | 1.942 | 0.586 | 3.04 | 0.718 | 5.86 | 0.8843 | 0.86 | 0.8509 | 0.9318 | 1 | 0.845 | 0.7281 | 0.8653 | 0.8653 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2331 | 840.3 | 593.3 | 98.4 | 130.1 | 19.1 | 829.2 | 5534.4 | 47.6 | 34.2 | 94.5 | 88.4 | 83.4 | 98.4 | 39.2 | 26.1 | 5255.6 | 6269.6 | 5580.5 | 8239.8 | 9961.3 | 8371.7 | 1.568 | 1.589 | 1.5 | 0.643 | 0.735 | 0.694 | -4.88 | -6.16 | 5.3 | 0.647 | 0.691 | 0.593 | -5 | 4.88 | 4.78 | 0.651 | 0.64 | 0.622 | -4.54 | 3.78 | -5.48 | 0.668 | 0.712 | 0.628 | 4.77 | 3.99 | -4.2 | Poor_Mixed | 5255.6 | 8239.8 | 1.5 | 0.735 | 6.16 | 0.712 | 5.48 | 0.4157 | 0.7438 | 0.4984 | 0.5407 | 1 | 0.4744 | 0.5192 | 0.5899 | 0.5899 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2332 | 1710.8 | 937.1 | 148.3 | 197 | 34.3 | 1375.8 | 8534.7 | 31.5 | 47.3 | 105.1 | 104.4 | 95.2 | 115.6 | 45 | 31 | 1218.5 | 1144.1 | 1021.7 | 1363.4 | 1210.2 | 1200 | 1.119 | 1.058 | 1.175 | 0.965 | 0.955 | 0.953 | 9.22 | -9.73 | 9.65 | 0.831 | 0.767 | 0.738 | 5.89 | 6.34 | 8.53 | 0.879 | 0.741 | 0.772 | 6.26 | -6.74 | 6.74 | 0.8 | 0.86 | 0.748 | -7.41 | 7.12 | 6.96 | Very Poor_Mixed | 1021.7 | 1200 | 1.058 | 0.965 | 9.73 | 0.879 | 8.53 | 0.0428 | 0.6081 | 0.1439 | 0.3597 | 1 | 0.0509 | 0.2783 | 0.3333 | 0.3333 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2333 | 899.5 | 540.5 | 98.9 | 112.9 | 20.6 | 742.1 | 5249.6 | 46.6 | 33.8 | 89.6 | 92.3 | 81.1 | 98 | 39.8 | 23 | 4435.3 | 5602.2 | 5916.4 | 6720.9 | 9006 | 8724.1 | 1.515 | 1.608 | 1.475 | 0.747 | 0.705 | 0.753 | 6.2 | 6.12 | -6.06 | 0.68 | 0.678 | 0.572 | -4.51 | -4.3 | 3.82 | 0.613 | 0.581 | 0.662 | 4.2 | 4.66 | 5.03 | 0.725 | 0.658 | 0.603 | 4.26 | 4.64 | -4.04 | Poor_Mixed | 4435.3 | 6720.9 | 1.475 | 0.753 | 6.2 | 0.725 | 5.03 | 0.4384 | 0.7485 | 0.5171 | 0.6484 | 1 | 0.3953 | 0.5423 | 0.5965 | 0.5965 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2334 | 1720.8 | 943.3 | 144.8 | 197 | 34.3 | 1260.8 | 8261.7 | 32.8 | 47 | 108.5 | 102.5 | 93.9 | 112.2 | 44.7 | 33.4 | 2048.7 | 690 | 898.2 | 2446.2 | 1200 | 1200 | 1.194 | 1.739 | 1.336 | 0.986 | 0.988 | 0.99 | 9.68 | -9.55 | -9.67 | 0.963 | 0.937 | 0.739 | -6.67 | 7.36 | -9.39 | 0.795 | 0.789 | 0.932 | -9.32 | -7.36 | 8.62 | 0.777 | 0.828 | 0.951 | 5.84 | 6.84 | 8.98 | Very Poor_Mixed | 690 | 1200 | 1.194 | 0.99 | 9.68 | 0.963 | 9.39 | 0.0603 | 0.6109 | 0.1624 | 0.267 | 1 | 0.0259 | 0.1908 | 0.3159 | 0.3159 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2335 | 784.5 | 526 | 94.9 | 100.7 | 15.5 | 833.9 | 4978.2 | 46.9 | 33.7 | 88.2 | 87.1 | 80.6 | 95.2 | 38.9 | 22.4 | 7420 | 6289.1 | 7739.4 | 12152.6 | 10608.9 | 12862.9 | 1.638 | 1.687 | 1.662 | 0.706 | 0.68 | 0.696 | -5.29 | -5.08 | 5.07 | 0.625 | 0.593 | 0.671 | 3.3 | -4.65 | 3.66 | 0.654 | 0.649 | 0.676 | -4.04 | 4.65 | -3.97 | 0.562 | 0.585 | 0.569 | -4.63 | 4.53 | 4.73 | Poor_Mixed | 6289.1 | 10608.9 | 1.638 | 0.706 | 5.29 | 0.676 | 4.73 | 0.4871 | 0.7497 | 0.5841 | 0.6686 | 1 | 0.4865 | 0.5772 | 0.6356 | 0.6356 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2336 | 569.5 | 386.6 | 87.2 | 90.7 | 3.5 | 2270 | 21315.5 | 57.8 | 21.3 | 76.5 | 77.4 | 71 | 80 | 36.1 | 18.7 | 690 | 1031.7 | 1139.8 | 767.1 | 1101.4 | 1166.3 | 1.112 | 1.068 | 1.023 | 0.772 | 0.68 | 0.765 | -5.5 | 5.38 | 5.8 | 0.529 | 0.506 | 0.554 | 2.59 | -2.34 | 2.82 | 0.505 | 0.537 | 0.537 | 2 | 3.55 | 2.45 | 0.561 | 0.529 | 0.557 | 2.11 | 2.38 | 2.2 | Critical_IR_PI | 690 | 767.1 | 1.023 | 0.772 | 5.8 | 0.561 | 3.55 | 0.5291 | 0.9458 | 0.9254 | 0.7872 | 0.925 | 0.4241 | 0.8162 | 0.732 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation; IR_Min_10min<1000 Mohm: critical insulation resistance | CO
2337 | 1691 | 869.3 | 134.3 | 176.2 | 33.2 | 1270.4 | 7296.5 | 36.5 | 43.1 | 103.8 | 104.4 | 90.9 | 111.8 | 43 | 32.6 | 1390.7 | 1829.7 | 1698.9 | 1523.6 | 1998.5 | 1863 | 1.096 | 1.092 | 1.097 | 0.952 | 0.901 | 0.986 | 9.18 | 8.71 | -9.84 | 0.836 | 0.819 | 0.66 | -5.73 | 6.32 | 5.46 | 0.827 | 0.839 | 0.709 | 7.47 | 5.49 | -7.48 | 0.896 | 0.734 | 0.753 | 4.71 | -8 | 6.05 | Very Poor_Mixed | 1390.7 | 1523.6 | 1.092 | 0.986 | 9.84 | 0.896 | 8 | 0.1118 | 0.6484 | 0.2088 | 0.2982 | 1 | 0.0734 | 0.3078 | 0.3672 | 0.3672 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2338 | 1433.5 | 776.6 | 133 | 170.5 | 27.9 | 1178.1 | 7525.2 | 36.1 | 71.5 | 101.5 | 101.6 | 88.3 | 109.2 | 42.4 | 35.2 | 4089.8 | 2173.2 | 2198 | 5504.6 | 2684.5 | 2682.1 | 1.346 | 1.235 | 1.22 | 0.869 | 0.868 | 0.865 | 8.65 | 7.93 | 7.63 | 0.643 | 0.836 | 0.807 | 6.69 | 4.79 | 5.05 | 0.722 | 0.712 | 0.815 | 5.04 | 7.12 | 7.64 | 0.789 | 0.801 | 0.743 | -7.1 | 5.4 | 6.64 | Critical_Mixed | 2173.2 | 2682.1 | 1.22 | 0.869 | 8.65 | 0.836 | 7.64 | 0.1778 | 0.5833 | 0.2701 | 0.1958 | 1 | 0.1877 | 0.3346 | 0.3978 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | C2H2
2339 | 1766 | 902 | 148.3 | 197 | 34.3 | 1379 | 8783.2 | 19.2 | 26.8 | 82.6 | 86.8 | 79.3 | 90.3 | 37.5 | 17.2 | 6716.5 | 6676.3 | 7497.4 | 11059.7 | 11265.9 | 12737.6 | 1.647 | 1.687 | 1.699 | 0.568 | 0.565 | 0.615 | 3.61 | 3.14 | 4.38 | 0.54 | 0.577 | 0.551 | 3.44 | -2.28 | 3.44 | 0.531 | 0.559 | 0.508 | -2.57 | 3.2 | 3 | 0.549 | 0.555 | 0.627 | 3.07 | 3.2 | -2.39 | Critical_DGA | 6676.3 | 11059.7 | 1.647 | 0.615 | 4.38 | 0.627 | 3.44 | 0.039 | 0.2579 | 0.6684 | 0.832 | 1 | 0.6952 | 0.7466 | 0.5409 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | C2H2
2340 | 783.6 | 399.9 | 94.7 | 112.5 | 16.2 | 725.3 | 4688.6 | 49.2 | 33.9 | 91.6 | 91.1 | 82.3 | 95 | 40.2 | 22.5 | 5111.1 | 5571.7 | 6324.1 | 7497.2 | 8741.3 | 9896.3 | 1.467 | 1.569 | 1.565 | 0.737 | 0.717 | 0.703 | -5.34 | 5.64 | 5.53 | 0.704 | 0.616 | 0.715 | 4.74 | 5.63 | 3.2 | 0.654 | 0.657 | 0.641 | -4.46 | -2.65 | 5.45 | 0.702 | 0.636 | 0.623 | 3.79 | 5.07 | -5.21 | Poor_Mixed | 5111.1 | 7497.2 | 1.467 | 0.737 | 5.64 | 0.715 | 5.63 | 0.5015 | 0.7473 | 0.5164 | 0.6652 | 1 | 0.4436 | 0.5117 | 0.6142 | 0.6142 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2341 | 1031.4 | 551.9 | 110.9 | 130.2 | 21.9 | 877.8 | 5719.3 | 48.6 | 35 | 92.1 | 92.2 | 84 | 99.7 | 39.8 | 27.4 | 5565.9 | 5604 | 6298.1 | 8517.3 | 8724.3 | 9805.2 | 1.53 | 1.557 | 1.557 | 0.738 | 0.734 | 0.714 | 5.9 | -5.45 | 5.48 | 0.691 | 0.666 | 0.606 | 4.22 | -5 | 5.17 | 0.634 | 0.664 | 0.671 | 6.04 | 5.15 | -4.28 | 0.684 | 0.654 | 0.668 | -5.51 | 4.94 | 5 | Poor_Mixed | 5565.9 | 8517.3 | 1.53 | 0.738 | 5.9 | 0.691 | 6.04 | 0.3723 | 0.7345 | 0.4745 | 0.4938 | 1 | 0.429 | 0.4896 | 0.5615 | 0.5615 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2342 | 164.2 | 120 | 70.7 | 64.4 | 1.2 | 405.4 | 2787.1 | 58.2 | 22.9 | 75 | 75 | 71.5 | 80 | 35.7 | 10.4 | 8662.3 | 9349.6 | 9814.1 | 16678.1 | 18071.6 | 19198.5 | 1.925 | 1.933 | 1.956 | 0.778 | 0.803 | 0.737 | -6.97 | 6.57 | 6.3 | 0.552 | 0.505 | 0.539 | 2 | 3.13 | 2.67 | 0.567 | 0.525 | 0.532 | -2.03 | 2 | 2.25 | 0.542 | 0.548 | 0.534 | 2.58 | 2.46 | 2.14 | Poor_Winding_TD_Cap | 8662.3 | 16678.1 | 1.925 | 0.803 | 6.97 | 0.567 | 3.13 | 0.9151 | 0.9088 | 0.9793 | 0.9955 | 1 | 0.3374 | 0.8125 | 0.839 | 0.839 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
2343 | 593 | 289.4 | 82.7 | 83.4 | 11.2 | 572.2 | 4046 | 51.6 | 27.4 | 84 | 81.6 | 76.9 | 92.1 | 37.2 | 15.5 | 8330.8 | 8243.2 | 8507.7 | 14971 | 14609 | 15008.9 | 1.797 | 1.772 | 1.764 | 0.53 | 0.63 | 0.641 | -2.98 | 3.97 | -3.47 | 0.578 | 0.607 | 0.556 | -2.52 | 3.31 | -3.57 | 0.625 | 0.567 | 0.531 | 2.96 | 3.66 | 3.16 | 0.564 | 0.573 | 0.58 | 3.41 | 3.38 | -3.34 | Fair_Mixed | 8243.2 | 14609 | 1.764 | 0.641 | 3.97 | 0.625 | 3.66 | 0.6324 | 0.8323 | 0.706 | 0.88 | 1 | 0.6942 | 0.6882 | 0.7536 | 0.7536 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2344 | 249.5 | 260.3 | 71.7 | 56.9 | 1.1 | 350 | 3445 | 55.2 | 24.6 | 83.5 | 83.1 | 75.7 | 86.5 | 36.3 | 15.5 | 7807.9 | 154.2 | 7735.3 | 13873.8 | 195.8 | 13665.1 | 1.777 | 1.27 | 1.767 | 0.921 | 0.99 | 0.915 | -9.23 | 9.24 | 8.62 | 0.615 | 0.633 | 0.518 | -3.44 | 2.83 | 3.58 | 0.564 | 0.594 | 0.517 | 3.6 | 3.37 | 2.36 | 0.559 | 0.562 | 0.571 | 2.95 | 3.43 | 3.53 | Critical_Winding_TD_Cap | 154.2 | 195.8 | 1.27 | 0.99 | 9.24 | 0.633 | 3.6 | 0.9176 | 0.8768 | 0.7393 | 0.88 | 0.85 | 0.0869 | 0.7053 | 0.7277 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | Winding_LV_TanDelta_pct
2345 | 1463.9 | 819.2 | 135.2 | 175.7 | 30.6 | 1246.8 | 8274.1 | 34.1 | 45.1 | 101.8 | 102.1 | 89.8 | 112.5 | 43.7 | 29.9 | 1815.5 | 2728 | 2566.7 | 2062.6 | 3468.8 | 3347.8 | 1.136 | 1.272 | 1.304 | 0.919 | 0.938 | 0.949 | 8.59 | -8.64 | 9.26 | 0.798 | 0.77 | 0.852 | 7.84 | 7.61 | 6.59 | 0.815 | 0.849 | 0.678 | 6.81 | 5.6 | 7.71 | 0.766 | 0.895 | 0.86 | 5.63 | -7.04 | 7.4 | Very Poor_Mixed | 1815.5 | 2062.6 | 1.136 | 0.949 | 9.26 | 0.895 | 7.84 | 0.135 | 0.6289 | 0.2311 | 0.4014 | 1 | 0.1012 | 0.2628 | 0.3739 | 0.3739 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2346 | 1130.3 | 671.3 | 121.3 | 153.8 | 28.2 | 1055.1 | 6705 | 37.5 | 41.5 | 100.1 | 100.2 | 89.2 | 109.4 | 43.1 | 35.1 | 3770.4 | 439.4 | 3156 | 5016.7 | 720.1 | 4211.5 | 1.331 | 1.639 | 1.334 | 0.838 | 0.795 | 0.838 | -7.44 | 7.66 | 6.66 | 0.741 | 0.736 | 0.822 | 5.92 | 5.18 | 6.69 | 0.789 | 0.788 | 0.844 | 5.9 | 5.56 | 5.49 | 0.801 | 0.834 | 0.729 | 7.53 | 5.55 | 5.88 | Critical_Mixed | 439.4 | 720.1 | 1.331 | 0.838 | 7.66 | 0.844 | 7.53 | 0.2578 | 0.6645 | 0.2751 | 0.1998 | 0.85 | 0.2629 | 0.3146 | 0.4111 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_1min<500 Mohm: critical insulation resistance; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2347 | 1691.5 | 982.4 | 144.3 | 197 | 34.3 | 1379 | 8849.5 | 57.5 | 23.7 | 86 | 84.1 | 77.8 | 91.7 | 37.3 | 12.6 | 8174.8 | 8137.9 | 8984.9 | 15451.7 | 14785.5 | 17447.8 | 1.89 | 1.817 | 1.942 | 0.51 | 0.528 | 0.516 | 2 | -22.17 | 2.53 | 0.551 | 0.587 | 0.575 | 2.81 | 3 | 3.03 | 0.581 | 0.611 | 0.607 | -2.82 | 3.26 | 2.53 | 0.574 | 0.605 | 0.592 | 2.82 | -3.76 | -3.32 | Critical_DGA | 8137.9 | 14785.5 | 1.817 | 0.528 | 22.17 | 0.611 | 3.76 | 0.0379 | 0.8931 | 0.6669 | 0.953 | 1 | 0.7584 | 0.6759 | 0.6188 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Winding_LV_CapChange_pct>=10% abs: critical winding capacitance change | C2H2
2348 | 741.9 | 484.5 | 96 | 119.9 | 20.4 | 802.7 | 5466.1 | 47.3 | 30.5 | 94.2 | 93.2 | 82.1 | 99.4 | 40 | 22 | 7370.2 | 5472 | 8135.5 | 12302 | 8715.6 | 13654.6 | 1.669 | 1.593 | 1.678 | 0.706 | 0.757 | 0.734 | -5.77 | 5.92 | 5.7 | 0.657 | 0.741 | 0.704 | -4.16 | 5.11 | 4.16 | 0.689 | 0.7 | 0.642 | -5.31 | 3.35 | 4.67 | 0.713 | 0.718 | 0.673 | 4.99 | 5.15 | 4.9 | Poor_Mixed | 5472 | 8715.6 | 1.593 | 0.757 | 5.92 | 0.741 | 5.31 | 0.4436 | 0.7894 | 0.4671 | 0.6819 | 1 | 0.4157 | 0.4634 | 0.588 | 0.588 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2349 | 1433.9 | 840.7 | 129.2 | 155.1 | 25.1 | 1191.1 | 8064.6 | 35.9 | 43.5 | 102.2 | 103.7 | 91 | 109.3 | 43.2 | 32.3 | 1492.1 | 2864.7 | 2065.9 | 1640.7 | 3599.8 | 2316.7 | 1.1 | 1.257 | 1.121 | 0.836 | 0.868 | 0.906 | 8.05 | 7.94 | 8.39 | 0.686 | 0.722 | 0.712 | 5.68 | 7.07 | 6.06 | 0.788 | 0.903 | 0.851 | 5.59 | -5.88 | 4.81 | 0.779 | 0.867 | 0.696 | 7.32 | -6.81 | -7.71 | Very Poor_Mixed | 1492.1 | 1640.7 | 1.1 | 0.906 | 8.39 | 0.903 | 7.71 | 0.1926 | 0.6445 | 0.2323 | 0.3098 | 1 | 0.1831 | 0.3147 | 0.4065 | 0.4065 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2350 | 126.1 | 178.8 | 71.8 | 54.5 | 3.1 | 421.1 | 2972.1 | 59 | 20.7 | 75 | 75 | 70 | 81 | 36.5 | 19.1 | 8403 | 9157.3 | 9263.7 | 15912.7 | 17890 | 18527.4 | 1.894 | 1.954 | 2 | 0.536 | 0.534 | 0.584 | 2.14 | 2.51 | -3.01 | 0.5 | 0.5 | 0.553 | -2.68 | 2 | 2.56 | 0.566 | 0.517 | 0.545 | -2.36 | 2.81 | 3.29 | 0.533 | 0.522 | 0.5 | 3.21 | 2 | 2.72 | Fair_Age | 8403 | 15912.7 | 1.894 | 0.584 | 3.01 | 0.566 | 3.29 | 0.8639 | 0.9638 | 0.9887 | 0.7749 | 1 | 0.8198 | 0.8509 | 0.8972 | 0.8972 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2351 | 822.8 | 434.9 | 98.5 | 97.3 | 16.1 | 643.4 | 4672.8 | 51.5 | 29 | 85.1 | 86.2 | 78.7 | 92.8 | 37.9 | 21.5 | 7599.1 | 7425.2 | 7694.7 | 12995.3 | 12419.5 | 12803.6 | 1.71 | 1.673 | 1.664 | 0.653 | 0.733 | 0.625 | 4.36 | 5.61 | 4.4 | 0.666 | 0.636 | 0.637 | 4.15 | -4.06 | 3.76 | 0.61 | 0.642 | 0.66 | 3.97 | -4.44 | 5.05 | 0.638 | 0.615 | 0.674 | 3.4 | 4.79 | 4.01 | Fair_Mixed | 7425.2 | 12419.5 | 1.664 | 0.733 | 5.61 | 0.674 | 5.05 | 0.5192 | 0.8095 | 0.643 | 0.6984 | 1 | 0.5324 | 0.545 | 0.6588 | 0.6588 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2352 | 256.6 | 204.3 | 77.6 | 113.5 | 1.1 | 350 | 2759.4 | 55.7 | 24.4 | 95.2 | 91.5 | 84.9 | 100.5 | 41.4 | 11.3 | 9749 | 10000 | 10000 | 18648.2 | 20000 | 20000 | 1.913 | 2 | 2 | 0.542 | 0.5 | 0.547 | 2.33 | -2.35 | -2 | 0.504 | 0.502 | 0.5 | 2.35 | 2.47 | 2 | 0.507 | 0.5 | 0.519 | -2 | 2 | 2.95 | 0.524 | 0.547 | 0.528 | 2 | 2 | 2 | Poor_Thermal | 9749 | 18648.2 | 1.913 | 0.547 | 2.35 | 0.547 | 2.95 | 0.8561 | 0.8804 | 0.4395 | 0.9802 | 1 | 0.8953 | 0.9065 | 0.8611 | 0.8611 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2353 | 761.9 | 573.5 | 101.8 | 113 | 14.3 | 784.3 | 5165.7 | 44.9 | 38.2 | 88.5 | 89.7 | 82.9 | 96 | 38.8 | 25.4 | 6094.4 | 7155.3 | 5920 | 9799.3 | 12617.1 | 9602.5 | 1.608 | 1.763 | 1.622 | 0.715 | 0.73 | 0.72 | -4.51 | 6.37 | -5.79 | 0.636 | 0.761 | 0.694 | -4.08 | 4.46 | 5.22 | 0.708 | 0.707 | 0.694 | -4.63 | -5.8 | -5.07 | 0.692 | 0.691 | 0.591 | 4.51 | -4.72 | 4.44 | Poor_Mixed | 5920 | 9602.5 | 1.608 | 0.73 | 6.37 | 0.761 | 5.8 | 0.4789 | 0.6989 | 0.5461 | 0.5655 | 1 | 0.4388 | 0.4689 | 0.5923 | 0.5923 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2354 | 221.3 | 178.2 | 72.7 | 83 | 1.4 | 360.1 | 2748.3 | 59.4 | 21 | 89.8 | 88.7 | 80.2 | 98.1 | 39.6 | 12.1 | 9055.3 | 9355.7 | 9482.6 | 17780.9 | 16811.1 | 18844.7 | 1.964 | 1.797 | 1.987 | 0.54 | 0.542 | 0.592 | 2.89 | -2.82 | 2.51 | 0.595 | 0.5 | 0.518 | 2.56 | 2 | 2 | 0.514 | 0.504 | 0.512 | 2.36 | 2.54 | 2 | 0.51 | 0.51 | 0.57 | 2 | -2 | 2.04 | Fair_Thermal | 9055.3 | 16811.1 | 1.797 | 0.592 | 2.89 | 0.595 | 2.56 | 0.8748 | 0.9543 | 0.5461 | 0.964 | 1 | 0.7945 | 0.8744 | 0.8647 | 0.8647 | Good | 1 | 0 | No_Anomaly | 0 |  | WTI_HV
2355 | 1424.2 | 911.3 | 141.3 | 166.9 | 28.1 | 1320.8 | 7898.8 | 35.2 | 47.5 | 103.9 | 105.1 | 93.6 | 112 | 43.6 | 31.4 | 2032.9 | 1749.2 | 1173.1 | 2321.9 | 1890.6 | 1427.9 | 1.142 | 1.081 | 1.217 | 0.94 | 0.971 | 0.897 | 9.46 | 9.45 | 8.57 | 0.871 | 0.872 | 0.766 | 7.64 | 8.94 | 8.24 | 0.797 | 0.832 | 0.872 | 7.23 | 9.68 | 6.81 | 0.909 | 0.942 | 0.878 | 7.72 | 7.83 | -5.51 | Very Poor_Mixed | 1173.1 | 1427.9 | 1.081 | 0.971 | 9.46 | 0.942 | 9.68 | 0.1389 | 0.6062 | 0.1838 | 0.3444 | 1 | 0.0844 | 0.1883 | 0.3488 | 0.3488 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2356 | 145.6 | 184.3 | 67.6 | 65.8 | 1.6 | 436.2 | 3038.7 | 57.2 | 24.4 | 79.4 | 76.2 | 73.3 | 86.3 | 35.5 | 13.3 | 7380.5 | 7536.3 | 8588.5 | 12811.4 | 13582.8 | 16053 | 1.736 | 1.802 | 1.869 | 0.647 | 0.716 | 0.699 | 4.4 | 5.44 | -4.57 | 0.573 | 0.516 | 0.558 | -2.16 | -2.27 | 2.65 | 0.527 | 0.527 | 0.574 | 2 | -2.59 | 2 | 0.546 | 0.522 | 0.507 | 2.79 | 2.91 | 2.48 | Poor_Winding_TD_Cap | 7380.5 | 12811.4 | 1.736 | 0.716 | 5.44 | 0.574 | 2.91 | 0.8813 | 0.8804 | 0.8599 | 0.9367 | 1 | 0.5136 | 0.8099 | 0.8365 | 0.8365 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_LV_TanDelta_pct
2357 | 510.2 | 408.3 | 89.5 | 89.3 | 11 | 623.6 | 4325.7 | 51.4 | 27.6 | 85.8 | 86.7 | 77.5 | 90.7 | 38.5 | 18 | 6890.1 | 7818.8 | 6799.9 | 11147.5 | 13957.9 | 12103.7 | 1.618 | 1.785 | 1.78 | 0.657 | 0.581 | 0.681 | 4.39 | 3.97 | 4.33 | 0.649 | 0.636 | 0.592 | -2.54 | 4.39 | -3.93 | 0.64 | 0.573 | 0.589 | 3.67 | -3.01 | 3.58 | 0.63 | 0.632 | 0.548 | 3.2 | -4.07 | 2.54 | Fair_Mixed | 6799.9 | 11147.5 | 1.618 | 0.681 | 4.39 | 0.649 | 4.39 | 0.6065 | 0.8293 | 0.6497 | 0.8084 | 1 | 0.5972 | 0.6251 | 0.7127 | 0.7127 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2358 | 173.8 | 120 | 65 | 50 | 1 | 350 | 2500 | 48.3 | 32.1 | 76.6 | 75 | 70.4 | 82.5 | 35 | 10.6 | 7472.5 | 7881.1 | 7588.3 | 12955.8 | 14140.1 | 12878.5 | 1.734 | 1.794 | 1.697 | 0.537 | 0.555 | 0.556 | 3.09 | 2.38 | 2.96 | 0.573 | 0.516 | 0.525 | 2.14 | 2.85 | 2 | 0.579 | 0.52 | 0.54 | -3.05 | 2.34 | -2.4 | 0.525 | 0.516 | 0.5 | 2.22 | 2.06 | 2.92 | Poor_Oil | 7472.5 | 12878.5 | 1.697 | 0.556 | 3.09 | 0.579 | 3.05 | 0.9903 | 0.7691 | 0.9565 | 0.9925 | 1 | 0.8015 | 0.8312 | 0.907 | 0.907 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2359 | 376.9 | 214.5 | 80.7 | 73.6 | 2.5 | 461.5 | 2947 | 47 | 32.7 | 78.5 | 80.8 | 73.7 | 81.9 | 35.8 | 12.7 | 7788 | 7805.4 | 8223.1 | 13419 | 13389.5 | 14454 | 1.723 | 1.715 | 1.758 | 0.543 | 0.534 | 0.578 | 3 | -3.31 | -3.13 | 0.615 | 0.548 | 0.56 | 2.42 | 3.51 | 2.87 | 0.531 | 0.556 | 0.539 | 3.29 | 2.98 | -3.24 | 0.539 | 0.584 | 0.634 | -3.63 | 2.94 | 3.97 | Poor_Oil | 7788 | 13389.5 | 1.715 | 0.578 | 3.31 | 0.634 | 3.97 | 0.8059 | 0.7617 | 0.8407 | 0.9507 | 1 | 0.7759 | 0.7091 | 0.8207 | 0.8207 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2360 | 529.8 | 211.4 | 81.5 | 86.8 | 6.8 | 556.4 | 3469.7 | 56.1 | 21.9 | 82.6 | 81.1 | 75.7 | 87 | 36.5 | 16.3 | 8036 | 7440.2 | 9729.3 | 14611.4 | 12785.1 | 18140.7 | 1.818 | 1.718 | 1.865 | 0.581 | 0.602 | 0.592 | 3.51 | 3.52 | 2.93 | 0.523 | 0.594 | 0.592 | 3.07 | -4.09 | 3.67 | 0.616 | 0.553 | 0.55 | -2.93 | 3.35 | 3.39 | 0.576 | 0.541 | 0.615 | 3.12 | 2.98 | -2.03 | Fair_Mixed | 7440.2 | 12785.1 | 1.718 | 0.602 | 3.52 | 0.616 | 4.09 | 0.6924 | 0.9307 | 0.7588 | 0.8578 | 1 | 0.7065 | 0.6994 | 0.7884 | 0.7884 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2361 | 187.4 | 150.8 | 69 | 55.5 | 1.5 | 499.2 | 2838.7 | 56.7 | 23.9 | 76.6 | 78.1 | 71.2 | 81.5 | 36.2 | 10 | 9014.9 | 8897.8 | 8921.4 | 17886.6 | 15671.7 | 17842.8 | 1.984 | 1.761 | 2 | 0.586 | 0.629 | 0.601 | 3.57 | -4.17 | 3.26 | 0.532 | 0.57 | 0.531 | -3.08 | 2.48 | -2.07 | 0.5 | 0.52 | 0.535 | 2.62 | 2.23 | 2 | 0.5 | 0.506 | 0.5 | -2 | 2.27 | 2.17 | Fair_Winding_TD_Cap | 8897.8 | 15671.7 | 1.761 | 0.629 | 4.17 | 0.57 | 3.08 | 0.8909 | 0.8894 | 0.9071 | 1 | 1 | 0.6683 | 0.8805 | 0.8822 | 0.8822 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2362 | 899.3 | 480.2 | 101.6 | 126.5 | 16.4 | 818.5 | 5539 | 47.4 | 31.8 | 91.7 | 91.2 | 84.2 | 101.4 | 40.6 | 25.5 | 5948.2 | 4823.8 | 4682 | 9216.1 | 7182.8 | 7080.8 | 1.549 | 1.489 | 1.512 | 0.757 | 0.706 | 0.744 | 6.1 | -5.97 | 4.38 | 0.697 | 0.601 | 0.643 | -4.79 | 5.31 | 3.8 | 0.654 | 0.637 | 0.732 | 4.35 | 4.57 | 5.02 | 0.667 | 0.682 | 0.653 | 3.72 | -5.65 | 3.8 | Poor_Mixed | 4682 | 7080.8 | 1.489 | 0.757 | 6.1 | 0.732 | 5.65 | 0.4431 | 0.7728 | 0.4686 | 0.562 | 1 | 0.431 | 0.5047 | 0.5896 | 0.5896 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2363 | 1141.7 | 624.7 | 119.3 | 147.9 | 22.6 | 1077.8 | 6621 | 58.9 | 23.6 | 76.5 | 80.1 | 71.5 | 85.7 | 35.9 | 10.5 | 8721.9 | 8230.7 | 9628.3 | 15929.4 | 14941.3 | 18327.1 | 1.826 | 1.815 | 1.903 | 0.596 | 0.604 | 0.573 | 2.94 | 3.15 | 3.6 | 0.524 | 0.571 | 0.544 | 2.36 | 3.49 | 2.12 | 0.5 | 0.553 | 0.5 | 2.77 | 2.6 | -3.92 | 0.597 | 0.501 | 0.551 | -3 | 3.09 | 2.02 | Poor_DGA | 8230.7 | 14941.3 | 1.815 | 0.604 | 3.6 | 0.597 | 3.92 | 0.2957 | 0.895 | 0.8674 | 0.994 | 1 | 0.7135 | 0.8135 | 0.7241 | 0.7241 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2364 | 812.9 | 504.8 | 102.4 | 114.3 | 17.1 | 816.3 | 5420.3 | 48.3 | 32.2 | 90.5 | 95.9 | 82 | 99.3 | 40.3 | 24.4 | 5119.8 | 5258.3 | 5920 | 8054.3 | 8158.8 | 9152.1 | 1.573 | 1.552 | 1.546 | 0.735 | 0.695 | 0.693 | -6.04 | 5.57 | 4.85 | 0.684 | 0.609 | 0.659 | 5.09 | -4.38 | 4.07 | 0.604 | 0.635 | 0.714 | 4.42 | 4.78 | 3.8 | 0.724 | 0.707 | 0.692 | -5.14 | -5.62 | 4.08 | Poor_Mixed | 5119.8 | 8054.3 | 1.546 | 0.735 | 6.04 | 0.724 | 5.62 | 0.4553 | 0.7678 | 0.4732 | 0.6005 | 1 | 0.4552 | 0.4953 | 0.5962 | 0.5962 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2365 | 100 | 163.8 | 65 | 51.4 | 4 | 351.1 | 2505.5 | 58.6 | 22.5 | 76.2 | 75.6 | 70 | 80.2 | 35 | 12.3 | 10000 | 9030.6 | 9731 | 20000 | 17899.8 | 19393.2 | 2 | 1.982 | 1.993 | 0.552 | 0.5 | 0.5 | -2.71 | 2.1 | -2.16 | 0.538 | 0.557 | 0.574 | -2.51 | 2.07 | 2.43 | 0.5 | 0.513 | 0.51 | 2 | -2.59 | -2.19 | 0.509 | 0.506 | 0.53 | 2.86 | 2 | 2.22 | Good_Mixed | 9030.6 | 17899.8 | 1.982 | 0.552 | 2.71 | 0.574 | 2.86 | 0.8815 | 0.9171 | 0.9672 | 0.9597 | 1 | 0.925 | 0.858 | 0.9191 | 0.9191 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2366 | 780.8 | 540 | 107.1 | 122.4 | 17.1 | 819.8 | 5493.4 | 49.2 | 32.4 | 96.1 | 93.7 | 85.5 | 102.2 | 38.8 | 22.2 | 6676.6 | 5214 | 5463.8 | 10303.4 | 7836.5 | 8806.9 | 1.543 | 1.503 | 1.612 | 0.736 | 0.709 | 0.745 | 5.96 | 5.31 | -5.75 | 0.718 | 0.641 | 0.551 | 4.96 | -3.45 | 5.67 | 0.654 | 0.643 | 0.679 | -3.75 | 4.66 | 5.05 | 0.723 | 0.691 | 0.698 | 5.87 | -4.67 | 4.5 | Poor_Mixed | 5214 | 7836.5 | 1.503 | 0.745 | 5.96 | 0.723 | 5.87 | 0.4415 | 0.7654 | 0.4246 | 0.6753 | 1 | 0.4245 | 0.4972 | 0.5874 | 0.5874 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2367 | 116.4 | 223.6 | 69.2 | 99.2 | 1 | 420.4 | 2559.4 | 57.8 | 21.2 | 91.1 | 90.1 | 80.3 | 94.5 | 39.8 | 11.7 | 9297.8 | 8251.1 | 9234 | 18543.7 | 15567.7 | 18088.9 | 1.994 | 1.887 | 1.959 | 0.556 | 0.542 | 0.615 | 3.07 | 3.49 | 3.49 | 0.508 | 0.603 | 0.571 | -3.08 | -2.9 | 2.47 | 0.509 | 0.5 | 0.5 | 3.06 | 3.37 | 2.08 | 0.534 | 0.544 | 0.529 | 2.95 | 2.47 | -2.75 | Poor_Thermal | 8251.1 | 15567.7 | 1.887 | 0.615 | 3.49 | 0.603 | 3.37 | 0.8967 | 0.9486 | 0.5443 | 0.9724 | 1 | 0.7355 | 0.8238 | 0.8523 | 0.8523 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2368 | 930.9 | 528.3 | 99.8 | 110.6 | 16.4 | 747 | 5725.3 | 47.3 | 33.8 | 94.5 | 90.9 | 81.6 | 99.8 | 39.7 | 27.8 | 5577 | 5754.3 | 5295.6 | 8279 | 8801.7 | 8186.4 | 1.484 | 1.53 | 1.546 | 0.735 | 0.724 | 0.76 | -6.19 | 5.48 | 5.92 | 0.708 | 0.669 | 0.737 | 6.53 | 5.54 | 6.26 | 0.634 | 0.597 | 0.64 | 5.36 | 5.87 | 5.33 | 0.692 | 0.74 | 0.646 | -5.23 | 4.33 | 5.11 | Poor_Mixed | 5295.6 | 8186.4 | 1.484 | 0.76 | 6.19 | 0.74 | 6.53 | 0.4591 | 0.7485 | 0.4831 | 0.4793 | 1 | 0.4056 | 0.4576 | 0.576 | 0.576 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2369 | 486.6 | 352.2 | 91.5 | 92.3 | 64 | 605.4 | 4077 | 49.2 | 30.5 | 77.4 | 76 | 70 | 81.3 | 35.3 | 16.8 | 1194.4 | 1823.9 | 1396.2 | 1325.7 | 2051 | 1424.2 | 1.11 | 1.125 | 1.02 | 0.764 | 0.728 | 0.674 | 5.53 | -5.83 | 5.32 | 0.569 | 0.515 | 0.573 | -2.76 | -3.15 | 2 | 0.542 | 0.571 | 0.5 | 3.7 | 2.86 | 2.73 | 0.503 | 0.595 | 0.516 | 3.14 | 2 | 2 | Critical_IR_PI | 1194.4 | 1325.7 | 1.02 | 0.764 | 5.83 | 0.595 | 3.7 | 0.4795 | 0.7894 | 0.9417 | 0.8436 | 1 | 0.4388 | 0.8021 | 0.7168 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2370 | 116.8 | 194.2 | 74.7 | 59.8 | 5.7 | 391.4 | 2856 | 58.7 | 20 | 76.2 | 77.1 | 70 | 82.3 | 35.2 | 12.7 | 9851.1 | 10000 | 9687.2 | 19566.9 | 19598.2 | 19374.4 | 1.986 | 1.96 | 2 | 0.5 | 0.5 | 0.524 | 2 | 2.56 | 2.47 | 0.528 | 0.5 | 0.514 | -2 | 2 | 2.21 | 0.552 | 0.542 | 0.5 | 2.43 | -2.03 | 2.21 | 0.565 | 0.5 | 0.509 | 2.21 | 2.13 | 2 | Good_Mixed | 9687.2 | 19374.4 | 1.96 | 0.524 | 2.56 | 0.565 | 2.43 | 0.8189 | 1 | 0.9377 | 0.9507 | 1 | 0.9411 | 0.8867 | 0.9174 | 0.9174 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2371 | 618.6 | 389.7 | 89.4 | 93.5 | 10.6 | 615.8 | 4369.4 | 51.1 | 28.3 | 82.6 | 85.3 | 76.8 | 91.8 | 39 | 20.2 | 6743.3 | 8260.6 | 7852.5 | 11113 | 14277.5 | 13986 | 1.648 | 1.728 | 1.781 | 0.677 | 0.649 | 0.667 | 4.93 | 4.73 | 5.05 | 0.623 | 0.644 | 0.631 | 5.01 | 3.71 | 4.25 | 0.605 | 0.623 | 0.5 | 3.7 | 2.84 | 4.56 | 0.571 | 0.616 | 0.63 | 4.22 | 3.82 | -3.59 | Fair_Mixed | 6743.3 | 11113 | 1.648 | 0.677 | 5.05 | 0.644 | 5.01 | 0.5989 | 0.8193 | 0.6801 | 0.7404 | 1 | 0.5292 | 0.6233 | 0.6994 | 0.6994 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2372 | 1383.2 | 825.8 | 131.2 | 183 | 33.1 | 1262.8 | 8015.7 | 35.9 | 44.3 | 104.6 | 99.1 | 93.6 | 114.3 | 44 | 30.4 | 690 | 1546.7 | 1513.4 | 1200 | 1755.1 | 1617.9 | 1.739 | 1.135 | 1.069 | 0.904 | 0.906 | 0.849 | 8.83 | 8.79 | -6.93 | 0.821 | 0.79 | 0.893 | 6.78 | 7.26 | 8.01 | 0.711 | 0.866 | 0.788 | -6.73 | 9.14 | -6.76 | 0.764 | 0.7 | 0.811 | 6.07 | 5.36 | 6.14 | Very Poor_Mixed | 690 | 1200 | 1.069 | 0.906 | 8.83 | 0.893 | 9.14 | 0.1276 | 0.6367 | 0.1998 | 0.3825 | 1 | 0.1689 | 0.2778 | 0.3811 | 0.3811 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2373 | 1532.5 | 821.7 | 135.7 | 171.1 | 34.3 | 1247.7 | 7545.3 | 30.8 | 47.9 | 103.6 | 103.5 | 92.2 | 112.5 | 44.2 | 31.8 | 2307.4 | 1449.3 | 3315.4 | 2682.3 | 1681.8 | 4012.7 | 1.162 | 1.16 | 1.21 | 0.903 | 0.936 | 0.925 | 8.27 | 9.69 | -8.4 | 0.726 | 0.852 | 0.791 | -7.69 | 6.5 | 8.9 | 0.925 | 0.86 | 0.849 | 8.78 | 7.9 | 7.2 | 0.789 | 0.775 | 0.854 | 9.24 | -7.35 | 5.86 | Very Poor_Mixed | 1449.3 | 1681.8 | 1.16 | 0.936 | 9.69 | 0.925 | 9.24 | 0.1261 | 0.6025 | 0.1955 | 0.3291 | 1 | 0.1132 | 0.2216 | 0.3556 | 0.3556 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2374 | 876.3 | 510.6 | 98.2 | 110.3 | 13.7 | 837.2 | 5154.9 | 45.5 | 32.1 | 93.4 | 88.5 | 84.1 | 99.8 | 40.6 | 26.3 | 6690.5 | 5855.8 | 6865.1 | 10397.8 | 9988.6 | 10460.6 | 1.554 | 1.706 | 1.524 | 0.744 | 0.644 | 0.811 | 5.65 | 5.51 | 6.49 | 0.701 | 0.625 | 0.593 | -5.68 | 4.8 | 5.22 | 0.731 | 0.796 | 0.747 | -5.2 | 4.97 | 3.64 | 0.649 | 0.637 | 0.691 | 4.69 | 4.45 | -5.12 | Poor_Mixed | 5855.8 | 9988.6 | 1.524 | 0.811 | 6.49 | 0.796 | 5.68 | 0.4799 | 0.7691 | 0.4843 | 0.5335 | 1 | 0.414 | 0.4684 | 0.5896 | 0.5896 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2375 | 809 | 478 | 105.4 | 111.6 | 15.6 | 828.2 | 4579.6 | 48.2 | 32 | 89.7 | 88.2 | 79.8 | 96 | 38.5 | 26 | 7241.3 | 6284.8 | 7810.5 | 12447 | 10137.2 | 13094.7 | 1.719 | 1.613 | 1.677 | 0.733 | 0.712 | 0.698 | 5.79 | 4.74 | 5.31 | 0.598 | 0.606 | 0.56 | 3.66 | 3.71 | -4.51 | 0.679 | 0.674 | 0.666 | 4.63 | 5.17 | 4.29 | 0.654 | 0.664 | 0.614 | 4.17 | 4.2 | -4 | Poor_Mixed | 6284.8 | 10137.2 | 1.613 | 0.733 | 5.79 | 0.679 | 5.17 | 0.4758 | 0.7703 | 0.5701 | 0.5442 | 1 | 0.4606 | 0.5546 | 0.6199 | 0.6199 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2376 | 560.2 | 363.5 | 85.6 | 94.3 | 12.8 | 651 | 4656.4 | 53 | 26.5 | 81.4 | 83.1 | 72.8 | 87.1 | 37.6 | 19.6 | 8781.4 | 8311 | 7483.5 | 16303.6 | 15137.8 | 12002.2 | 1.857 | 1.821 | 1.604 | 0.625 | 0.627 | 0.633 | -3.94 | 4.51 | 4.19 | 0.556 | 0.589 | 0.588 | 3.54 | 4.11 | 3.96 | 0.614 | 0.571 | 0.606 | 3.72 | -3.34 | 3.58 | 0.555 | 0.608 | 0.643 | 3.47 | 3.2 | 3.78 | Fair_Mixed | 7483.5 | 12002.2 | 1.604 | 0.633 | 4.51 | 0.643 | 4.11 | 0.5834 | 0.8458 | 0.769 | 0.7593 | 1 | 0.6075 | 0.6428 | 0.723 | 0.723 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2377 | 917.1 | 590.9 | 106.1 | 122.8 | 19.1 | 935 | 5568.7 | 47.2 | 32.9 | 90.3 | 87.9 | 82.6 | 97.7 | 41 | 25.7 | 7350.7 | 4771.1 | 4819.9 | 12556.8 | 6812.8 | 7221.7 | 1.708 | 1.428 | 1.498 | 0.686 | 0.78 | 0.675 | -4.86 | 5.83 | -5.53 | 0.657 | 0.656 | 0.619 | 5 | 4.77 | 4.42 | 0.683 | 0.662 | 0.626 | 4.29 | -5.18 | 4.76 | 0.67 | 0.717 | 0.69 | 3.7 | 4.13 | 3.17 | Poor_Mixed | 4771.1 | 6812.8 | 1.428 | 0.78 | 5.83 | 0.717 | 5.18 | 0.3981 | 0.7593 | 0.5256 | 0.5549 | 1 | 0.4556 | 0.5087 | 0.5863 | 0.5863 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2378 | 877.1 | 661.6 | 105.4 | 125.8 | 20.1 | 805.7 | 5389.5 | 58.7 | 20 | 76.4 | 78.4 | 73.7 | 81.4 | 36.1 | 12 | 9915 | 9943.8 | 9890.9 | 19829.9 | 19872 | 19781.9 | 2 | 1.998 | 2 | 0.594 | 0.565 | 0.521 | 3.11 | 2.51 | 2 | 0.537 | 0.522 | 0.5 | 2.58 | 2 | 2 | 0.52 | 0.515 | 0.5 | 2.72 | 2 | -2.33 | 0.535 | 0.532 | 0.533 | -2.75 | -2.02 | 2.15 | Poor_DGA | 9890.9 | 19781.9 | 1.998 | 0.594 | 3.11 | 0.537 | 2.75 | 0.4028 | 1 | 0.8853 | 0.9661 | 1 | 0.8115 | 0.8721 | 0.7881 | 0.7881 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2379 | 679 | 321.9 | 87.2 | 86.6 | 5.4 | 671.5 | 3693.5 | 26.2 | 23.3 | 78.4 | 79.4 | 74.2 | 86 | 37 | 19.3 | 9013.8 | 8856.1 | 9200.2 | 17445.3 | 16607.2 | 17072.1 | 1.935 | 1.875 | 1.856 | 0.593 | 0.571 | 0.564 | 3.32 | 3.26 | 3.17 | 0.571 | 0.578 | 0.603 | 3.51 | 2.39 | -4.15 | 0.525 | 0.98 | 0.519 | 3.44 | 9.78 | 3.24 | 0.529 | 0.539 | 0.55 | 3.69 | 3.06 | 4.25 | Critical_Bushing_TD_Cap | 8856.1 | 16607.2 | 1.856 | 0.593 | 3.32 | 0.98 | 9.78 | 0.6624 | 0.3174 | 0.8233 | 0.7687 | 1 | 0.7317 | 0.6513 | 0.7041 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2380 | 100 | 148.5 | 66.1 | 52.6 | 4.4 | 362.5 | 2500 | 60 | 21 | 76.5 | 75.8 | 71.2 | 80 | 35 | 13.5 | 9101.9 | 9712.6 | 9548.3 | 17564.9 | 19087.1 | 18596.5 | 1.93 | 1.965 | 1.948 | 0.5 | 0.5 | 0.5 | 2 | -2 | 2.53 | 0.548 | 0.514 | 0.5 | 2.81 | 2.55 | 2 | 0.5 | 0.527 | 0.5 | 2.61 | 2.41 | 2.36 | 0.502 | 0.5 | 0.538 | 2.32 | -2 | 2.14 | Good_Mixed | 9101.9 | 17564.9 | 1.93 | 0.5 | 2.53 | 0.548 | 2.81 | 0.8705 | 0.9543 | 0.9465 | 0.9318 | 1 | 0.9846 | 0.9062 | 0.9344 | 0.9344 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2381 | 1519.4 | 858.3 | 143.2 | 168.3 | 29.5 | 1256 | 7885.1 | 30.6 | 49.4 | 106.2 | 109.3 | 96.3 | 116.6 | 45.1 | 32.6 | 690 | 1161.2 | 2583.3 | 1200 | 1270.8 | 2977.7 | 1.739 | 1.094 | 1.153 | 0.99 | 0.99 | 0.975 | 9.24 | 9.58 | -9.48 | 0.849 | 0.808 | 0.866 | 7.55 | 7.85 | -7.92 | 0.746 | 0.918 | 0.812 | -6.61 | 6.81 | 8.69 | 0.752 | 0.842 | 0.876 | 6.67 | 8.96 | 6.4 | Very Poor_Mixed | 690 | 1200 | 1.094 | 0.99 | 9.58 | 0.918 | 8.96 | 0.1357 | 0.5888 | 0.0992 | 0.2982 | 1 | 0.0378 | 0.2233 | 0.3349 | 0.3349 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2382 | 774.3 | 568.9 | 106.1 | 112.3 | 14.3 | 871.5 | 5136.4 | 48.5 | 36.4 | 90 | 90.8 | 82.1 | 98.1 | 38.7 | 24.3 | 4657.1 | 5779.5 | 6428.4 | 6782.5 | 8543.7 | 9938.2 | 1.456 | 1.478 | 1.546 | 0.73 | 0.7 | 0.741 | -5.36 | 5 | -6.15 | 0.744 | 0.626 | 0.657 | 4.57 | 4.38 | 4.69 | 0.615 | 0.701 | 0.617 | 4.64 | 4.1 | 4.85 | 0.669 | 0.719 | 0.664 | 4.22 | 5.72 | 4.18 | Poor_Mixed | 4657.1 | 6782.5 | 1.456 | 0.741 | 6.15 | 0.744 | 5.72 | 0.4654 | 0.7186 | 0.524 | 0.6039 | 1 | 0.4398 | 0.4973 | 0.5963 | 0.5963 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2383 | 295.2 | 196.4 | 71 | 70.8 | 1.1 | 493.6 | 3432.8 | 59.6 | 20.5 | 75.3 | 76.9 | 70 | 81.3 | 35 | 10.9 | 6251.9 | 6876.2 | 7338.4 | 9670.6 | 11100.7 | 12534.3 | 1.547 | 1.614 | 1.708 | 0.603 | 0.589 | 0.506 | 3.11 | 3.61 | 2.18 | 0.529 | 0.54 | 0.572 | 2.02 | -2.98 | 2.44 | 0.5 | 0.554 | 0.539 | 2.55 | 2.33 | -2.46 | 0.53 | 0.564 | 0.504 | 2 | -2.53 | -2 | Fair_IR_PI | 6251.9 | 9670.6 | 1.547 | 0.603 | 3.61 | 0.572 | 2.98 | 0.8722 | 0.9709 | 0.9583 | 0.9875 | 1 | 0.7802 | 0.825 | 0.8975 | 0.8975 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_TanDelta_pct
2384 | 843.2 | 572.1 | 105.8 | 120.9 | 20.7 | 841.6 | 5506.9 | 59.4 | 20 | 76 | 77.7 | 71.6 | 85.5 | 35.7 | 14.4 | 7729.8 | 9849.1 | 9333.9 | 14278.1 | 19208.2 | 18667.8 | 1.847 | 1.95 | 2 | 0.522 | 0.527 | 0.506 | 2.04 | 2.03 | -2.05 | 0.589 | 0.558 | 0.515 | -2.56 | -2.22 | 2.73 | 0.574 | 0.533 | 0.5 | 3.17 | 2.86 | 2.78 | 0.5 | 0.566 | 0.509 | 3.01 | 2.74 | 2.48 | Poor_DGA | 7729.8 | 14278.1 | 1.847 | 0.527 | 2.05 | 0.589 | 3.17 | 0.4107 | 1 | 0.8968 | 0.9092 | 1 | 0.9239 | 0.8126 | 0.7934 | 0.7934 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2385 | 321.1 | 207.9 | 81.5 | 139.9 | 3.4 | 456.6 | 3488.4 | 56.1 | 73.8 | 106.7 | 107.9 | 93.2 | 113.3 | 45 | 17.6 | 7468.1 | 8542.7 | 7795.7 | 13212.5 | 15795.8 | 14182.4 | 1.769 | 1.849 | 1.819 | 0.532 | 0.598 | 0.562 | 2.09 | 3.22 | 2.63 | 0.543 | 0.551 | 0.572 | 2.32 | 3.14 | 2.05 | 0.519 | 0.577 | 0.545 | -2.9 | 2.18 | 2.52 | 0.549 | 0.604 | 0.595 | 2.77 | 2.42 | 2.75 | Critical_Thermal | 7468.1 | 13212.5 | 1.769 | 0.598 | 3.22 | 0.604 | 3.14 | 0.7213 | 0.5833 | 0.1384 | 0.8203 | 1 | 0.7949 | 0.7493 | 0.7113 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2386 | 264.1 | 229.3 | 72.1 | 57.9 | 4.4 | 508.9 | 3282.3 | 60 | 20.4 | 75.8 | 79.2 | 70 | 80.8 | 35 | 13.2 | 10000 | 9992.7 | 9711.8 | 18866.8 | 19770.2 | 19400.4 | 1.887 | 1.978 | 1.998 | 0.5 | 0.525 | 0.5 | -2 | 2.69 | 2.32 | 0.5 | 0.5 | 0.524 | 2 | 2.21 | -2.63 | 0.506 | 0.543 | 0.5 | -2 | 2.57 | -2 | 0.515 | 0.5 | 0.5 | 2.64 | 2.25 | -2 | Good_Mixed | 9711.8 | 18866.8 | 1.887 | 0.525 | 2.69 | 0.543 | 2.64 | 0.7977 | 0.9748 | 0.9303 | 0.939 | 1 | 0.9411 | 0.9303 | 0.9156 | 0.9156 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2387 | 209.2 | 120 | 65 | 50 | 1.6 | 352.6 | 2827.3 | 47.3 | 33.8 | 75.4 | 75.4 | 70.9 | 80.2 | 35 | 10 | 8469.6 | 8418.8 | 8797.7 | 15493.9 | 15506.2 | 16123.7 | 1.829 | 1.842 | 1.833 | 0.573 | 0.6 | 0.502 | -3.03 | -3.56 | 2.67 | 0.543 | 0.5 | 0.506 | -2.02 | -2 | 2.53 | 0.537 | 0.506 | 0.507 | 2.14 | 2.25 | -2.09 | 0.5 | 0.511 | 0.5 | 2.25 | 2.19 | -2.74 | Fair_Oil | 8418.8 | 15493.9 | 1.829 | 0.6 | 3.56 | 0.543 | 2.74 | 0.9321 | 0.7485 | 0.9694 | 1 | 1 | 0.7848 | 0.9135 | 0.9041 | 0.9041 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2388 | 1635.4 | 860.7 | 140.4 | 176.5 | 29.5 | 1223.2 | 7938.5 | 33.4 | 45.3 | 101.1 | 98.8 | 89.8 | 109 | 43 | 30.6 | 2608.9 | 2599.3 | 2357.1 | 3287.3 | 3014.7 | 2789 | 1.26 | 1.16 | 1.183 | 0.966 | 0.886 | 0.978 | 9.16 | 8.81 | 9.39 | 0.725 | 0.723 | 0.773 | 6.96 | 6.81 | 5.82 | 0.903 | 0.826 | 0.831 | 5.53 | 4.36 | 6.46 | 0.842 | 0.897 | 0.747 | 6.78 | 6.65 | 6.89 | Very Poor_Mixed | 2357.1 | 2789 | 1.16 | 0.978 | 9.39 | 0.903 | 6.96 | 0.1254 | 0.627 | 0.2767 | 0.3749 | 1 | 0.0816 | 0.287 | 0.3761 | 0.3761 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2389 | 1714.4 | 917.7 | 145.3 | 181 | 34.3 | 1328.3 | 9034.5 | 51.2 | 31 | 85.2 | 85.5 | 77.8 | 89.9 | 37.2 | 15.9 | 8704.3 | 8294.3 | 8409.5 | 16728 | 15700.8 | 15023.1 | 1.922 | 1.893 | 1.786 | 0.572 | 0.52 | 0.524 | 3.28 | 2 | -2 | 0.538 | 0.611 | 0.527 | 2.51 | 2.52 | -2.24 | 0.543 | 0.525 | 0.572 | 2.51 | 2.71 | 2.27 | 0.559 | 1.421 | 0.547 | -2.68 | 2.81 | 2.56 | Critical_DGA | 8294.3 | 15023.1 | 1.786 | 0.572 | 3.28 | 1.421 | 2.81 | 0.0584 | 0.7829 | 0.6719 | 0.869 | 1 | 0.8568 | 0.7125 | 0.6274 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_TV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
2390 | 927 | 390.2 | 106.6 | 118.8 | 15.9 | 806 | 5232.1 | 47.3 | 33.6 | 90.4 | 92.6 | 83.5 | 100.8 | 39.3 | 23.7 | 5813.7 | 5510.8 | 6142 | 9361.4 | 8171.2 | 9738.3 | 1.61 | 1.483 | 1.586 | 0.709 | 0.712 | 0.757 | 5.7 | 5.49 | 5.73 | 0.695 | 0.717 | 0.66 | -4.5 | 4.24 | 4.07 | 0.65 | 0.606 | 0.708 | 4.19 | 4.2 | 5.08 | 0.658 | 0.654 | 0.656 | -5.03 | -4.66 | 3.73 | Poor_Mixed | 5510.8 | 8171.2 | 1.483 | 0.757 | 5.73 | 0.717 | 5.08 | 0.4629 | 0.7509 | 0.4837 | 0.6246 | 1 | 0.43 | 0.5041 | 0.5964 | 0.5964 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2391 | 942.3 | 502.1 | 111.7 | 132.1 | 21.5 | 864.6 | 5669.1 | 45.6 | 35.3 | 91.3 | 91.9 | 83.6 | 99.8 | 40 | 24.3 | 5820.9 | 4609 | 6194.2 | 9002 | 6522 | 9829.3 | 1.546 | 1.415 | 1.587 | 0.751 | 0.695 | 0.735 | 5.38 | 5.6 | 5.95 | 0.719 | 0.704 | 0.679 | -5.65 | -4.73 | -5.07 | 0.629 | 0.733 | 0.701 | 4.81 | 4.88 | 5.21 | 0.675 | 0.726 | 0.668 | 5.01 | 5.12 | 5.51 | Poor_Mixed | 4609 | 6522 | 1.415 | 0.751 | 5.95 | 0.733 | 5.65 | 0.3867 | 0.731 | 0.4823 | 0.6039 | 1 | 0.429 | 0.4464 | 0.5632 | 0.5632 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2392 | 917.2 | 500.7 | 110.6 | 128.7 | 18.9 | 852.9 | 5325.8 | 45.2 | 32.5 | 89.7 | 89.4 | 81.1 | 95.5 | 39.8 | 23.4 | 4954.8 | 5450.1 | 5808.6 | 7582.8 | 8474.6 | 9427.1 | 1.53 | 1.555 | 1.623 | 0.701 | 0.693 | 0.722 | -5.3 | -5.43 | 5.21 | 0.713 | 0.605 | 0.723 | -5.44 | 5.36 | 4.22 | 0.687 | 0.693 | 0.716 | -5.09 | 4.5 | 5 | 0.624 | 0.66 | 0.663 | 5.41 | 4.21 | 4.79 | Poor_Mixed | 4954.8 | 7582.8 | 1.53 | 0.722 | 5.43 | 0.723 | 5.44 | 0.413 | 0.7641 | 0.5479 | 0.6348 | 1 | 0.4666 | 0.4758 | 0.5924 | 0.5924 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2393 | 353 | 250.8 | 75.2 | 58.2 | 1 | 468.7 | 2748.7 | 26.4 | 23.5 | 82.9 | 79.1 | 74.1 | 85.7 | 35.8 | 12.4 | 8705.9 | 8841.2 | 9155.5 | 16177.9 | 17304.7 | 17870.8 | 1.858 | 1.957 | 1.952 | 0.929 | 0.99 | 0.99 | 9.55 | 9.84 | 9.73 | 0.509 | 0.538 | 0.577 | 3.44 | 3.84 | 3.41 | 0.557 | 0.579 | 0.592 | 3.03 | 2.72 | 3.25 | 0.575 | 0.528 | 0.573 | 2.77 | 2 | -2.88 | Critical_Winding_TD_Cap | 8705.9 | 16177.9 | 1.858 | 0.99 | 9.84 | 0.592 | 3.84 | 0.9073 | 0.3136 | 0.7959 | 0.9575 | 1 | 0.0345 | 0.7353 | 0.6891 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2394 | 890.9 | 523.3 | 107.3 | 128.7 | 19.9 | 809.1 | 6155.4 | 45.8 | 34.8 | 88 | 84.1 | 83.3 | 94.9 | 39.6 | 25 | 5433.4 | 4926.8 | 7092.6 | 8006.8 | 7546.3 | 11475.2 | 1.474 | 1.532 | 1.618 | 0.737 | 0.75 | 0.781 | 5.66 | 5.87 | -6.5 | 0.762 | 0.608 | 0.683 | 4.41 | -5.28 | -4.77 | 0.642 | 0.701 | 0.671 | 4.92 | 4.87 | -4.53 | 0.721 | 0.642 | 0.683 | 4.24 | 4.64 | 5.14 | Poor_Mixed | 4926.8 | 7546.3 | 1.474 | 0.781 | 6.5 | 0.762 | 5.28 | 0.4055 | 0.7368 | 0.587 | 0.5796 | 1 | 0.3837 | 0.4771 | 0.5771 | 0.5771 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2395 | 1653.5 | 815.7 | 138.4 | 169.8 | 32.2 | 1214.2 | 7752.3 | 35.5 | 45 | 106 | 105.9 | 93 | 115.3 | 43.4 | 32.4 | 2574.7 | 1830.4 | 2014.9 | 3122.8 | 2079.5 | 2501.4 | 1.213 | 1.136 | 1.241 | 0.859 | 0.872 | 0.828 | 7.72 | 7.75 | 7.8 | 0.899 | 0.719 | 0.852 | 4.99 | -5.32 | 7.93 | 0.793 | 0.69 | 0.869 | -5.27 | 6.6 | 7.15 | 0.851 | 0.743 | 0.797 | -8.36 | 6.97 | 8.28 | Very Poor_Mixed | 1830.4 | 2079.5 | 1.136 | 0.872 | 7.8 | 0.899 | 8.36 | 0.1274 | 0.6299 | 0.156 | 0.3059 | 1 | 0.2144 | 0.2766 | 0.3781 | 0.3781 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2396 | 1535.5 | 892.3 | 133.5 | 178.3 | 31 | 1163.8 | 7572.7 | 37.3 | 44.2 | 102.3 | 100.9 | 92.3 | 111.3 | 42.7 | 34.7 | 2581 | 3622 | 2755.3 | 3027.2 | 3179 | 3463.9 | 1.173 | 0.878 | 1.257 | 0.945 | 0.872 | 0.902 | 8.78 | 8.33 | 8.42 | 0.764 | 0.752 | 0.828 | 5.84 | -4.57 | 6.5 | 0.763 | 0.779 | 0.733 | 6.88 | 5.08 | 5.83 | 0.824 | 0.754 | 0.762 | 7.55 | 6.94 | 7.34 | Critical_Mixed | 2581 | 3027.2 | 0.878 | 0.945 | 8.78 | 0.828 | 7.55 | 0.1374 | 0.6376 | 0.2339 | 0.2157 | 0.8187 | 0.1376 | 0.3175 | 0.3525 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | C2H2
2397 | 798.6 | 503.2 | 100.8 | 119.1 | 16.1 | 816.5 | 5223.4 | 48.3 | 32.2 | 90.7 | 94.7 | 82.5 | 97.8 | 40.4 | 23.1 | 4987.8 | 5635.2 | 5651.9 | 7664.8 | 9145.2 | 8832.7 | 1.537 | 1.623 | 1.563 | 0.704 | 0.668 | 0.718 | 5.52 | 5.14 | 5.79 | 0.643 | 0.634 | 0.719 | -4.75 | 5.21 | -5.73 | 0.644 | 0.707 | 0.701 | 4.12 | 5.07 | -4.15 | 0.718 | 0.692 | 0.627 | 4.6 | 5.18 | 3.8 | Poor_Mixed | 4987.8 | 7664.8 | 1.537 | 0.718 | 5.79 | 0.719 | 5.73 | 0.4616 | 0.7678 | 0.4829 | 0.645 | 1 | 0.4655 | 0.4812 | 0.5999 | 0.5999 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2398 | 979.4 | 664.6 | 105.9 | 127.8 | 19.9 | 899.7 | 5993.1 | 45.3 | 34.7 | 89.9 | 90.5 | 82.8 | 97.5 | 40.2 | 27.2 | 4695.8 | 5742.2 | 6113.8 | 7389.2 | 9325 | 9932.5 | 1.574 | 1.624 | 1.625 | 0.805 | 0.726 | 0.705 | 5.84 | 5.76 | 5.61 | 0.709 | 0.69 | 0.694 | 4.49 | -4.8 | -5.29 | 0.678 | 0.64 | 0.648 | -4.1 | 5.19 | 3.96 | 0.677 | 0.651 | 0.587 | -5.25 | 4.78 | 5.01 | Poor_Mixed | 4695.8 | 7389.2 | 1.574 | 0.805 | 5.84 | 0.709 | 5.29 | 0.3754 | 0.7379 | 0.5158 | 0.5011 | 1 | 0.4087 | 0.4957 | 0.5655 | 0.5655 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2399 | 1172.3 | 687.4 | 124.5 | 152.3 | 26 | 1015.1 | 6963.8 | 58.6 | 24.3 | 78.7 | 76.9 | 73.8 | 85.2 | 35.8 | 13.7 | 8543.6 | 10000 | 9077.5 | 16754.4 | 19167.7 | 17528.8 | 1.961 | 1.917 | 1.931 | 0.507 | 0.531 | 0.562 | -2.02 | 2.1 | 2.42 | 0.516 | 0.52 | 0.58 | -2.56 | 2 | -2.7 | 0.548 | 0.534 | 0.532 | -2.46 | 2.38 | 3.38 | 0.617 | 0.5 | 0.535 | 3.39 | 2.42 | 3.46 | Poor_DGA | 8543.6 | 16754.4 | 1.917 | 0.562 | 2.42 | 0.617 | 3.46 | 0.2641 | 0.8821 | 0.8583 | 0.9269 | 1 | 0.8842 | 0.7942 | 0.7308 | 0.7308 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2400 | 1542.8 | 882.3 | 139.4 | 186.6 | 34.3 | 1223.7 | 8007.5 | 36.4 | 44.1 | 103 | 107.8 | 91.7 | 112.6 | 43.7 | 30.5 | 2184.1 | 1415.9 | 2751 | 2552.4 | 1576.2 | 3398.7 | 1.169 | 1.113 | 1.235 | 0.97 | 0.965 | 0.964 | 9.23 | 9.84 | 9.65 | 0.877 | 0.71 | 0.688 | -7.25 | 7.13 | 8.59 | 0.962 | 0.832 | 0.774 | 7.18 | 7.67 | 7.5 | 0.795 | 0.855 | 0.851 | -7.52 | 9.05 | 7.77 | Very Poor_Mixed | 1415.9 | 1576.2 | 1.113 | 0.97 | 9.84 | 0.962 | 9.05 | 0.0997 | 0.6386 | 0.181 | 0.3787 | 1 | 0.0431 | 0.2308 | 0.3462 | 0.3462 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2401 | 1615.9 | 850.2 | 137 | 178.6 | 34.3 | 1271.2 | 8071.2 | 33.6 | 45.8 | 107.4 | 106.3 | 94.4 | 119.2 | 45.3 | 32.7 | 2375.1 | 2342 | 1511.7 | 2673.9 | 2793.8 | 1679.7 | 1.126 | 1.193 | 1.111 | 0.952 | 0.927 | 0.918 | 8.63 | 8.94 | 8.88 | 0.861 | 0.806 | 0.877 | 8.05 | 5.8 | 5.43 | 0.767 | 0.856 | 0.823 | 6.73 | 8.53 | 8.32 | 0.909 | 0.914 | 0.858 | 6.25 | 8.39 | 7.15 | Very Poor_Mixed | 1511.7 | 1679.7 | 1.111 | 0.952 | 8.94 | 0.914 | 8.53 | 0.1005 | 0.6222 | 0.1049 | 0.2943 | 1 | 0.1039 | 0.2126 | 0.3378 | 0.3378 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2402 | 831 | 453.4 | 101.4 | 119 | 16.3 | 842.8 | 5132.2 | 47.2 | 33.7 | 89.5 | 87.8 | 81.7 | 97.6 | 40 | 25.4 | 5535.3 | 5407.1 | 5951.7 | 8772.3 | 8578.6 | 9373.8 | 1.585 | 1.587 | 1.575 | 0.742 | 0.719 | 0.759 | -5.92 | -4.85 | 6.49 | 0.74 | 0.579 | 0.657 | 3.68 | 5.19 | -4.36 | 0.71 | 0.69 | 0.682 | 4.04 | 3.91 | 3.97 | 0.656 | 0.696 | 0.691 | 5.71 | -4.22 | -5.08 | Poor_Mixed | 5407.1 | 8578.6 | 1.575 | 0.759 | 6.49 | 0.74 | 5.71 | 0.4606 | 0.7497 | 0.5444 | 0.5655 | 1 | 0.4118 | 0.4907 | 0.5938 | 0.5938 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2403 | 744.6 | 538.1 | 104.5 | 114.6 | 18.9 | 836.1 | 5380.4 | 45.1 | 35.2 | 89.4 | 89.9 | 81.4 | 97.5 | 40 | 23.9 | 4790.8 | 6077 | 4769.2 | 7255.5 | 9333.8 | 7396.8 | 1.514 | 1.536 | 1.551 | 0.727 | 0.696 | 0.708 | 6.01 | 4.93 | 5.42 | 0.651 | 0.654 | 0.731 | 4.17 | 3.22 | -3.56 | 0.672 | 0.616 | 0.647 | -4.15 | 5.23 | 5.45 | 0.672 | 0.674 | 0.607 | 3.9 | 5.78 | 4.69 | Poor_Mixed | 4769.2 | 7255.5 | 1.514 | 0.727 | 6.01 | 0.731 | 5.78 | 0.442 | 0.7322 | 0.5333 | 0.6177 | 1 | 0.4544 | 0.5146 | 0.5988 | 0.5988 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2404 | 319 | 216.7 | 77.6 | 67 | 1 | 481.8 | 3530.3 | 56.4 | 21.4 | 77.4 | 75 | 70.4 | 84.7 | 36.3 | 12.6 | 8334.5 | 8607.4 | 10000 | 15514.1 | 16162.8 | 19543.4 | 1.861 | 1.878 | 1.954 | 0.662 | 0.682 | 0.69 | 5.15 | 4.95 | 4.58 | 0.512 | 0.5 | 0.535 | -3.45 | 3.14 | 2.32 | 0.565 | 0.528 | 0.543 | 2.2 | 3.47 | 2.57 | 0.544 | 0.57 | 0.52 | 2.62 | 2.89 | 2.66 | Fair_Winding_TD_Cap | 8334.5 | 15514.1 | 1.861 | 0.69 | 5.15 | 0.57 | 3.47 | 0.8932 | 0.9432 | 0.9314 | 0.953 | 1 | 0.5164 | 0.8035 | 0.8542 | 0.8542 | Good | 1 | 1 | Winding_TD_Cap | 0 |  | Winding_TV_TanDelta_pct
2405 | 1107.6 | 636.4 | 118 | 133 | 25.4 | 982.7 | 6287.3 | 58.1 | 22.9 | 76.4 | 78.2 | 71 | 81.6 | 35.7 | 13.7 | 10000 | 9715.8 | 9200.2 | 20000 | 18936.2 | 17872 | 2 | 1.949 | 1.943 | 0.51 | 0.527 | 0.558 | 2.21 | -2.64 | 2.71 | 0.554 | 0.554 | 0.526 | 3.39 | 2 | 3.11 | 0.515 | 0.61 | 0.5 | 2.11 | 3.17 | -2.42 | 0.577 | 0.594 | 0.545 | 2.49 | 2.46 | 2.19 | Poor_DGA | 9200.2 | 17872 | 1.943 | 0.558 | 2.71 | 0.61 | 3.39 | 0.3117 | 0.9088 | 0.9124 | 0.9269 | 1 | 0.858 | 0.7792 | 0.7449 | 0.7449 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2406 | 835.2 | 562.5 | 106.6 | 113.5 | 16.3 | 793.1 | 6024.3 | 47.8 | 31.8 | 91.5 | 93.8 | 81.4 | 99.7 | 40 | 24.9 | 4792.4 | 5685.9 | 4813.8 | 7275.1 | 8838.5 | 7396.8 | 1.518 | 1.554 | 1.537 | 0.717 | 0.721 | 0.76 | 5.87 | 5.81 | 5.86 | 0.706 | 0.616 | 0.632 | -5.15 | 4.32 | 5.39 | 0.664 | 0.821 | 0.633 | -5.81 | 5.01 | 5.51 | 0.679 | 0.679 | 0.648 | -5.02 | 5.56 | -3.75 | Poor_Mixed | 4792.4 | 7275.1 | 1.518 | 0.76 | 5.87 | 0.821 | 5.81 | 0.4465 | 0.7728 | 0.4834 | 0.5831 | 1 | 0.4126 | 0.4727 | 0.5847 | 0.5847 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2407 | 1401.5 | 812 | 132.8 | 166 | 29.6 | 1145.1 | 7272.1 | 31.4 | 46.7 | 101.5 | 103.9 | 90.5 | 109.8 | 43.1 | 33 | 3359.2 | 3584.6 | 2450.5 | 4209.9 | 4408.8 | 2934.7 | 1.253 | 1.23 | 1.198 | 0.904 | 0.902 | 0.832 | 8 | 8.45 | -8.09 | 0.779 | 0.857 | 0.746 | 6.86 | 6.7 | 7.33 | 0.88 | 0.812 | 0.811 | 5.44 | 6.8 | 7.87 | 0.849 | 0.748 | 0.786 | -5.88 | 5.73 | 6.81 | Very Poor_Mixed | 2450.5 | 2934.7 | 1.198 | 0.904 | 8.45 | 0.88 | 7.87 | 0.1791 | 0.6137 | 0.2363 | 0.2826 | 1 | 0.1737 | 0.2732 | 0.3897 | 0.3897 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2408 | 320.1 | 177.3 | 77.9 | 76.5 | 2.6 | 424.2 | 3041.9 | 51.6 | 26.5 | 76.2 | 77 | 70.4 | 81.3 | 35.3 | 10.6 | 7898 | 9245 | 8108 | 14910.6 | 16391.7 | 14546.7 | 1.888 | 1.773 | 1.794 | 0.545 | 0.516 | 0.565 | 2.7 | -2.55 | 2.94 | 0.531 | 0.542 | 0.509 | 2.74 | 2.84 | 2.41 | 0.532 | 0.538 | 0.548 | 2.31 | 2.77 | 2.21 | 0.519 | 0.511 | 0.5 | 2.58 | 2.58 | 2.25 | Fair_Oil | 7898 | 14546.7 | 1.773 | 0.565 | 2.94 | 0.548 | 2.84 | 0.8175 | 0.8458 | 0.9371 | 0.9925 | 1 | 0.8223 | 0.8416 | 0.8758 | 0.8758 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2409 | 894.9 | 563.5 | 115.5 | 125 | 15.7 | 859.8 | 5893.5 | 45.4 | 38.7 | 94.3 | 88.6 | 84.9 | 102.2 | 40.1 | 26.2 | 5014.2 | 5625 | 5291.4 | 7520.9 | 8260 | 8261.7 | 1.5 | 1.468 | 1.561 | 0.825 | 0.706 | 0.792 | 6.64 | 5.24 | 6.69 | 0.674 | 0.602 | 0.709 | -4.22 | -5.3 | 4.91 | 0.708 | 0.654 | 0.671 | 4.18 | -4.99 | -4.47 | 0.61 | 0.703 | 0.591 | -5.87 | 5.67 | 3.81 | Poor_Mixed | 5014.2 | 7520.9 | 1.468 | 0.825 | 6.69 | 0.709 | 5.87 | 0.421 | 0.6936 | 0.4643 | 0.5371 | 1 | 0.3604 | 0.5026 | 0.5627 | 0.5627 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2410 | 1706.7 | 952.2 | 133.5 | 174.5 | 26.2 | 1191.5 | 8205.7 | 34.7 | 45.7 | 104 | 104 | 92.2 | 113.1 | 41.9 | 31.2 | 2530.2 | 1841.8 | 690 | 3102 | 2193.1 | 1200 | 1.226 | 1.191 | 1.739 | 0.89 | 0.981 | 0.948 | 8.52 | 8.38 | 8.91 | 0.731 | 0.889 | 0.724 | -7.17 | 5.48 | 7.49 | 0.794 | 0.829 | 0.863 | 5.56 | 5.18 | -9.14 | 0.852 | 0.839 | 0.828 | 6.91 | 7.85 | 7.47 | Very Poor_Mixed | 690 | 1200 | 1.191 | 0.981 | 8.91 | 0.889 | 9.14 | 0.1335 | 0.6232 | 0.2037 | 0.3521 | 1 | 0.1101 | 0.2555 | 0.3675 | 0.3675 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2411 | 171.7 | 175.4 | 65 | 50.6 | 2.8 | 395.3 | 2545.9 | 58.1 | 20 | 75.9 | 75.5 | 70.1 | 80.2 | 35.5 | 13.4 | 9060.7 | 9988.9 | 9504.7 | 17050.7 | 19743.3 | 18228.2 | 1.882 | 1.977 | 1.918 | 0.5 | 0.5 | 0.5 | -2 | 2 | 2.38 | 0.533 | 0.527 | 0.5 | -2.02 | 2 | 2.66 | 0.5 | 0.532 | 0.554 | 2 | 2.72 | 2.56 | 0.5 | 0.55 | 0.541 | -2.5 | 2.74 | 2.86 | Good_Mixed | 9060.7 | 17050.7 | 1.882 | 0.5 | 2.38 | 0.554 | 2.86 | 0.884 | 1 | 0.9688 | 0.9342 | 1 | 0.9884 | 0.8575 | 0.9373 | 0.9373 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2412 | 569.9 | 304.2 | 87.1 | 88.9 | 11.3 | 656 | 4554.2 | 53.4 | 27.5 | 86.1 | 87.6 | 80.1 | 93 | 37.7 | 19.1 | 6507 | 7530.7 | 7292.6 | 10606.9 | 13017.4 | 12238.2 | 1.63 | 1.729 | 1.678 | 0.682 | 0.736 | 0.676 | 5.33 | -5.1 | 4.13 | 0.648 | 0.575 | 0.552 | 4.07 | -3.77 | -4.08 | 0.625 | 0.658 | 0.54 | 4.06 | 3.96 | 3.17 | 0.595 | 0.678 | 0.555 | -4.84 | 3.04 | 4.77 | Fair_Mixed | 6507 | 10606.9 | 1.63 | 0.736 | 5.33 | 0.678 | 4.84 | 0.6064 | 0.8308 | 0.6167 | 0.7749 | 1 | 0.5005 | 0.6179 | 0.693 | 0.693 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2413 | 933.2 | 537 | 108.1 | 121 | 21 | 912.9 | 5377.9 | 44.5 | 32.8 | 94.2 | 89.8 | 82.8 | 98.7 | 39.7 | 24.7 | 6497.4 | 5368.6 | 6052.1 | 10485.8 | 8564.8 | 9394.4 | 1.614 | 1.595 | 1.552 | 0.695 | 0.702 | 0.673 | 5.4 | 5.86 | 4.85 | 0.724 | 0.658 | 0.692 | 4.05 | -4.33 | 4.13 | 0.719 | 0.621 | 0.714 | -5.84 | 5.95 | -3.71 | 0.743 | 0.702 | 0.622 | -5.04 | 3.81 | 4.35 | Poor_Mixed | 5368.6 | 8564.8 | 1.552 | 0.702 | 5.86 | 0.743 | 5.95 | 0.3967 | 0.7605 | 0.49 | 0.59 | 1 | 0.4779 | 0.4732 | 0.581 | 0.581 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2414 | 1507.8 | 891.3 | 139.2 | 182 | 32.9 | 1290.6 | 7358.3 | 30.6 | 45.5 | 106.2 | 109.3 | 95.6 | 115.2 | 44.6 | 32.3 | 1045.1 | 938.8 | 1842.4 | 1200 | 1200 | 2009.1 | 1.148 | 1.278 | 1.09 | 0.937 | 0.907 | 0.923 | 8.6 | 8.7 | 8.65 | 0.801 | 0.855 | 0.931 | 8.64 | 8.68 | -7.54 | 0.987 | 0.824 | 0.748 | 6.56 | 5.36 | -7.1 | 0.853 | 0.766 | 0.903 | -6.91 | 7.68 | 7.78 | Very Poor_Mixed | 938.8 | 1200 | 1.09 | 0.937 | 8.7 | 0.987 | 8.68 | 0.1121 | 0.6251 | 0.1137 | 0.3098 | 1 | 0.1192 | 0.2088 | 0.3442 | 0.3442 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2415 | 1471.1 | 979.2 | 134.9 | 172.3 | 28.6 | 1174.4 | 7658.1 | 31.6 | 49.4 | 101.1 | 103.1 | 91.9 | 112.4 | 43.4 | 31.8 | 2637.2 | 2497.7 | 1997.8 | 3109.2 | 3131.5 | 2269.9 | 1.179 | 1.254 | 1.136 | 0.931 | 0.898 | 0.928 | 8.67 | -7.99 | 8 | 0.984 | 0.842 | 0.857 | 9.5 | 5.95 | 6.69 | 0.837 | 0.807 | 0.886 | 6.56 | 7.46 | 7.15 | 0.912 | 0.933 | 0.852 | 7.27 | 6.37 | 8.1 | Very Poor_Mixed | 1997.8 | 2269.9 | 1.136 | 0.931 | 8.67 | 0.984 | 9.5 | 0.1455 | 0.5888 | 0.22 | 0.3291 | 1 | 0.1435 | 0.1876 | 0.3593 | 0.3593 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2416 | 918 | 544.6 | 97.1 | 124.6 | 18.7 | 723.3 | 5968.8 | 46.4 | 32.6 | 89.2 | 88.5 | 81.6 | 95.3 | 39.5 | 24.4 | 6250.7 | 7217 | 5443.8 | 10387.2 | 11806.2 | 8394.6 | 1.662 | 1.636 | 1.542 | 0.8 | 0.736 | 0.72 | 6.58 | 5.71 | 5.45 | 0.756 | 0.664 | 0.728 | -5.33 | 4.74 | 5.24 | 0.705 | 0.678 | 0.694 | -3.4 | 5.55 | 5.33 | 0.652 | 0.691 | 0.596 | 4.09 | 3.8 | 5.19 | Poor_Mixed | 5443.8 | 8394.6 | 1.542 | 0.8 | 6.58 | 0.756 | 5.55 | 0.4324 | 0.7629 | 0.557 | 0.6005 | 1 | 0.3931 | 0.4715 | 0.5853 | 0.5853 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2417 | 1207.8 | 710.1 | 123.8 | 150.8 | 25.2 | 2911.3 | 10413.7 | 41.5 | 38.9 | 99.6 | 102.7 | 91 | 110.2 | 42.6 | 33.7 | 3247.9 | 2790.6 | 3707.7 | 4089.9 | 3449.2 | 4638.9 | 1.259 | 1.236 | 1.251 | 0.843 | 0.851 | 0.848 | 7.1 | 7.71 | 7.59 | 0.682 | 0.726 | 0.767 | -7.53 | 7.47 | 4.77 | 0.738 | 0.784 | 0.707 | 5.01 | 5.6 | 5.21 | 0.888 | 0.817 | 0.857 | 6.35 | 6.78 | -5.47 | Critical_Mixed | 2790.6 | 3449.2 | 1.236 | 0.851 | 7.71 | 0.888 | 7.53 | 0.1817 | 0.6914 | 0.2527 | 0.2552 | 1 | 0.2336 | 0.3285 | 0.4183 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation | C2H2
2418 | 1434.2 | 814.1 | 132.5 | 177.5 | 31.1 | 1179.7 | 7224.1 | 34.1 | 45.6 | 104.8 | 106.7 | 92.6 | 114 | 43.5 | 32 | 2397.1 | 2771.8 | 2947.6 | 2739.4 | 3237 | 3479.6 | 1.143 | 1.168 | 1.18 | 0.852 | 0.876 | 0.904 | 7.97 | 7.95 | 9.06 | 0.817 | 0.887 | 0.774 | 7.69 | -8.23 | 6.66 | 0.851 | 0.798 | 0.714 | 6.95 | -8.33 | 7.94 | 0.819 | 0.751 | 0.823 | -7.77 | 6.01 | 8.14 | Very Poor_Mixed | 2397.1 | 2739.4 | 1.143 | 0.904 | 9.06 | 0.887 | 8.33 | 0.1568 | 0.6241 | 0.1663 | 0.3214 | 1 | 0.1675 | 0.2468 | 0.3747 | 0.3747 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2419 | 188.3 | 169 | 75.6 | 62.1 | 3.2 | 475.9 | 3125.6 | 58.2 | 20.9 | 75.9 | 76.6 | 72.8 | 80 | 35 | 10.4 | 8438 | 8637.7 | 8085.7 | 15801.1 | 15143.8 | 14793.4 | 1.873 | 1.753 | 1.83 | 0.638 | 0.532 | 0.592 | 3.99 | 2.44 | 3.27 | 0.5 | 0.51 | 0.507 | 2.67 | -2 | 2.46 | 0.5 | 0.562 | 0.552 | 2.27 | 2.28 | 2.79 | 0.538 | 0.529 | 0.506 | 2.52 | 3.03 | -2 | Fair_IR_PI | 8085.7 | 14793.4 | 1.753 | 0.638 | 3.99 | 0.562 | 3.03 | 0.8307 | 0.9574 | 0.9292 | 0.9955 | 1 | 0.7256 | 0.8666 | 0.8828 | 0.8828 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2420 | 774.1 | 475.3 | 97.9 | 108.6 | 14.9 | 800.8 | 5421.1 | 43.7 | 34.7 | 92.2 | 90.4 | 81.8 | 97.3 | 39.7 | 25.3 | 5358 | 5238.2 | 5637.2 | 8609.7 | 7871 | 8603.9 | 1.607 | 1.503 | 1.526 | 0.711 | 0.709 | 0.743 | 6.03 | 5.89 | 5.38 | 0.723 | 0.634 | 0.718 | 4.44 | 5.14 | 5.12 | 0.656 | 0.661 | 0.685 | -4.09 | -4.89 | 4.46 | 0.671 | 0.748 | 0.653 | -4.45 | 5.67 | -5.87 | Poor_Mixed | 5238.2 | 7871 | 1.503 | 0.743 | 6.03 | 0.748 | 5.87 | 0.4872 | 0.7379 | 0.5121 | 0.569 | 1 | 0.4273 | 0.466 | 0.5937 | 0.5937 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2421 | 861.7 | 521.3 | 105.9 | 115.7 | 16.4 | 776.4 | 5634.8 | 45.4 | 34.7 | 90.2 | 93.2 | 83.4 | 100.4 | 39.5 | 24.8 | 4985.1 | 6220.7 | 5366.4 | 7146 | 9702.4 | 7930.3 | 1.433 | 1.56 | 1.478 | 0.688 | 0.761 | 0.713 | -4.76 | -6.11 | -5.02 | 0.641 | 0.697 | 0.612 | -5.91 | 4.92 | -3.75 | 0.715 | 0.711 | 0.753 | -4.24 | 4.11 | 3.64 | 0.621 | 0.698 | 0.645 | -4.13 | -5.67 | 4.42 | Poor_Mixed | 4985.1 | 7146 | 1.433 | 0.761 | 6.11 | 0.753 | 5.91 | 0.453 | 0.7379 | 0.4826 | 0.5865 | 1 | 0.4547 | 0.4893 | 0.5911 | 0.5911 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2422 | 100 | 194.1 | 73.5 | 62 | 2.1 | 507.2 | 3540.3 | 28.9 | 20.7 | 78.1 | 81.5 | 73.7 | 84.3 | 36.9 | 12.4 | 7577.8 | 8399.2 | 8363.9 | 13257.1 | 15309.2 | 14812.4 | 1.749 | 1.823 | 1.771 | 0.886 | 0.876 | 0.911 | 8.54 | 8.6 | 7.78 | 0.544 | 0.586 | 0.514 | 2.56 | 2.63 | 3.07 | 0.5 | 0.576 | 0.526 | 2.35 | -2 | 2.6 | 0.552 | 0.591 | 0.519 | 3.01 | -2.78 | 2.67 | Critical_Winding_TD_Cap | 7577.8 | 13257.1 | 1.749 | 0.911 | 8.6 | 0.591 | 3.07 | 0.8576 | 0.3804 | 0.8213 | 0.9575 | 1 | 0.1586 | 0.7924 | 0.7149 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2423 | 112.4 | 120 | 65 | 55.9 | 1 | 414.8 | 3219.3 | 33 | 45.7 | 82.6 | 81.5 | 75.3 | 85.1 | 36.5 | 12.7 | 6592.8 | 6120.1 | 4941.7 | 3790.6 | 9401.9 | 7603.3 | 0.575 | 1.536 | 1.539 | 0.632 | 0.632 | 0.665 | 4.07 | 4.04 | 4.22 | 0.611 | 0.637 | 0.662 | 4.46 | 3.91 | 4.12 | 0.674 | 0.608 | 0.601 | 4.51 | 3.58 | -4.23 | 0.583 | 0.614 | 0.647 | 4.21 | 4.53 | 2.71 | Critical_Oil | 4941.7 | 3790.6 | 0.575 | 0.665 | 4.22 | 0.674 | 4.53 | 0.9653 | 0.6232 | 0.768 | 0.9507 | 0.8187 | 0.598 | 0.5742 | 0.7585 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | PI_Min<1.0: critical polarization index | Moisture_PPM
2424 | 200.7 | 179.6 | 70 | 58.9 | 3 | 358.9 | 2500 | 59.3 | 22.6 | 77.6 | 81.1 | 73.4 | 85.8 | 36.6 | 13.3 | 10000 | 8503 | 8597.4 | 20000 | 16104.7 | 16477.5 | 2 | 1.894 | 1.917 | 0.58 | 0.602 | 0.547 | 3.83 | -3.72 | 3.28 | 0.532 | 0.706 | 0.507 | 2.74 | 5.38 | -2.28 | 0.572 | 0.558 | 0.537 | -2.44 | 2.25 | 2.31 | 0.507 | 0.5 | 0.514 | 2.49 | 2.41 | -2.36 | Poor_Bushing_TD_Cap | 8503 | 16104.7 | 1.894 | 0.602 | 3.83 | 0.706 | 5.38 | 0.8655 | 0.915 | 0.8261 | 0.9367 | 1 | 0.7098 | 0.7989 | 0.8588 | 0.8588 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2425 | 188.5 | 145.5 | 71.5 | 62.1 | 3.4 | 524.7 | 2846.3 | 58.8 | 20.8 | 76.5 | 77.2 | 70.9 | 81.6 | 35 | 11.2 | 6562.7 | 5969.4 | 6704.8 | 9963.2 | 9570.2 | 10610.9 | 1.518 | 1.603 | 1.583 | 0.577 | 0.597 | 0.572 | 3.09 | 3.19 | -2.3 | 0.539 | 0.512 | 0.525 | 2.37 | 2.33 | 2 | 0.508 | 0.581 | 0.516 | -2.2 | 2 | 2.45 | 0.51 | 0.501 | 0.533 | -2.19 | -2 | 2.44 | Fair_IR_PI | 5969.4 | 9570.2 | 1.518 | 0.597 | 3.19 | 0.581 | 2.45 | 0.8262 | 0.9605 | 0.925 | 0.9821 | 1 | 0.7507 | 0.8631 | 0.8839 | 0.8839 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2426 | 100 | 201.7 | 65 | 50 | 1 | 399.3 | 2701.2 | 60 | 20 | 75 | 77.1 | 70 | 81.3 | 35 | 11.6 | 10000 | 9755.3 | 9367.9 | 20000 | 19111.8 | 18028.1 | 2 | 1.959 | 1.924 | 0.5 | 0.5 | 0.5 | 2.96 | 2 | 2.34 | 0.5 | 0.517 | 0.506 | 2.22 | 2.83 | 2 | 0.51 | 0.5 | 0.508 | -2 | 2 | -2 | 0.5 | 0.5 | 0.511 | 2.33 | 2 | 2.23 | Good_Mixed | 9367.9 | 18028.1 | 1.924 | 0.5 | 2.96 | 0.517 | 2.83 | 0.9768 | 1 | 0.9632 | 0.9744 | 1 | 0.9639 | 0.9426 | 0.9739 | 0.9739 | Good | 1 | 0 | No_Anomaly | 0 |  | Winding_HV_CapChange_pct
2427 | 594 | 360.2 | 92.7 | 143.4 | 4.1 | 598.8 | 4384.6 | 49.4 | 30.2 | 105.7 | 108.2 | 92.4 | 115.8 | 44.2 | 13.4 | 9049.3 | 9800.8 | 7196.1 | 16474.2 | 19049.9 | 11805.2 | 1.82 | 1.944 | 1.64 | 0.626 | 0.5 | 0.59 | 3.44 | -2.2 | -3.59 | 1.408 | 0.522 | 0.5 | 2.58 | 2.15 | 2.08 | 0.541 | 0.505 | 0.5 | 2.4 | 2.52 | 2.1 | 0.5 | 0.522 | 0.535 | 2.45 | 2.67 | 2 | Critical_Thermal | 7196.1 | 11805.2 | 1.64 | 0.626 | 3.59 | 1.408 | 2.67 | 0.6277 | 0.7933 | 0.1402 | 0.9342 | 1 | 0.7761 | 0.8285 | 0.7306 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_R_TanDelta_pct>=1.0%: critical bushing tan delta | C2H4
2428 | 232.4 | 285.5 | 74.7 | 61.9 | 1.7 | 483.5 | 3088.8 | 53.5 | 25.5 | 83.1 | 83.6 | 76.1 | 88.2 | 38.5 | 12.8 | 5071.3 | 5594.9 | 7376.4 | 7511.8 | 8452.3 | 12713.6 | 1.481 | 1.511 | 1.724 | 0.635 | 0.555 | 0.635 | 3.34 | 2.68 | 2.77 | 0.518 | 0.556 | 0.554 | 2 | 2.17 | 3.43 | 0.586 | 0.549 | 0.561 | 2.82 | -2.72 | 2.13 | 0.547 | 0.551 | 0.578 | 2.9 | 3.15 | 2.92 | Poor_IR_PI | 5071.3 | 7511.8 | 1.481 | 0.635 | 3.34 | 0.586 | 3.43 | 0.8495 | 0.8617 | 0.715 | 0.9484 | 1 | 0.7156 | 0.7541 | 0.8306 | 0.8306 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2429 | 452.8 | 263.4 | 86.5 | 88.7 | 5.4 | 506.4 | 3593.1 | 59.1 | 22.6 | 80.3 | 80.5 | 73.5 | 86.3 | 36.6 | 14 | 9306.9 | 9244.8 | 9608.8 | 17876.7 | 17786.2 | 19029.8 | 1.921 | 1.924 | 1.98 | 0.804 | 0.795 | 0.813 | -7.27 | 6.45 | 6.85 | 0.5 | 0.538 | 0.512 | 2.12 | 2.57 | 2 | 0.504 | 0.5 | 0.524 | -2.28 | 3.25 | 2.9 | 0.526 | 0.547 | 0.5 | 2.23 | 2.12 | 2.9 | Poor_Winding_TD_Cap | 9244.8 | 17786.2 | 1.921 | 0.813 | 7.27 | 0.547 | 3.25 | 0.7111 | 0.915 | 0.8027 | 0.9194 | 1 | 0.2989 | 0.8848 | 0.7749 | 0.7749 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2430 | 100 | 120 | 66.9 | 50 | 1 | 350 | 2500 | 51.5 | 28.6 | 75.6 | 80.4 | 71.8 | 80.2 | 35.9 | 12.9 | 7770.3 | 8958.7 | 9551.8 | 14038.8 | 16730.7 | 18447.3 | 1.807 | 1.868 | 1.931 | 0.519 | 0.533 | 0.631 | 2.68 | 2.34 | 3.94 | 0.5 | 0.547 | 0.512 | 2.09 | 2 | 2.36 | 0.529 | 0.524 | 0.512 | 3.05 | 2.02 | 2.97 | 0.502 | 0.526 | 0.5 | 2.36 | 2.48 | 2.22 | Fair_Oil | 7770.3 | 14038.8 | 1.807 | 0.631 | 3.94 | 0.547 | 3.05 | 0.9992 | 0.815 | 0.9011 | 0.9461 | 1 | 0.784 | 0.884 | 0.9139 | 0.9139 | Good | 1 | 0 | No_Anomaly | 0 |  | Moisture_PPM
2431 | 711 | 399 | 96.4 | 103.6 | 14.7 | 712.8 | 4416.3 | 51.4 | 30.6 | 87.9 | 87 | 77.7 | 90.4 | 37.9 | 20.6 | 6443.8 | 7183.1 | 7495.1 | 10696.9 | 12320.3 | 13070.2 | 1.66 | 1.715 | 1.744 | 0.644 | 0.674 | 0.647 | -4.82 | 4.79 | 3.93 | 0.622 | 0.587 | 0.66 | 4.26 | 4.02 | -5.35 | 0.664 | 0.713 | 0.647 | 5.03 | 5.41 | 5.9 | 0.627 | 0.715 | 0.621 | 4.15 | 4.99 | 4.26 | Poor_Mixed | 6443.8 | 10696.9 | 1.66 | 0.674 | 4.82 | 0.715 | 5.9 | 0.5296 | 0.7881 | 0.6364 | 0.7276 | 1 | 0.5617 | 0.5116 | 0.6577 | 0.6577 | Fair | 1 | 1 | Bushing_TD_Cap | 0 |  | C2H2
2432 | 141.4 | 225.8 | 68.1 | 64.6 | 4.7 | 424.7 | 3205.2 | 60 | 20.3 | 75 | 76.2 | 70.1 | 80 | 36.1 | 13.1 | 9864.7 | 9626.2 | 9600.9 | 19192 | 18898.4 | 19201.8 | 1.946 | 1.963 | 2 | 0.503 | 0.5 | 0.509 | 2 | 2.34 | 2 | 0.508 | 0.555 | 0.5 | -2.51 | 2.18 | 2.29 | 0.508 | 0.515 | 0.511 | 2.23 | -3.28 | 2.65 | 0.551 | 0.574 | 0.58 | 2.4 | 3.06 | 2.63 | Good_Mixed | 9600.9 | 18898.4 | 1.946 | 0.509 | 2.34 | 0.58 | 3.28 | 0.8133 | 0.9791 | 0.9736 | 0.9414 | 1 | 0.9651 | 0.8266 | 0.9092 | 0.9092 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2433 | 1032.1 | 523.7 | 104.8 | 124.5 | 19.3 | 884.9 | 5935.3 | 58.3 | 20.9 | 80.7 | 81.8 | 71.8 | 86.5 | 36.6 | 11.4 | 8992.6 | 8956.1 | 8403.6 | 16554 | 16762.5 | 15815.8 | 1.841 | 1.872 | 1.882 | 0.557 | 0.567 | 0.557 | 3.25 | -3.53 | -2.67 | 0.5 | 0.544 | 0.5 | 2.51 | 2.84 | 2.61 | 0.501 | 0.527 | 0.5 | -2 | -2 | 2 | 0.538 | 0.526 | 0.5 | 2 | 2.38 | 3.01 | Poor_DGA | 8403.6 | 15815.8 | 1.841 | 0.567 | 3.53 | 0.544 | 3.01 | 0.3969 | 0.9574 | 0.8024 | 0.9783 | 1 | 0.7608 | 0.9045 | 0.7726 | 0.7726 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2434 | 149.9 | 129.7 | 65 | 58.9 | 3.8 | 350 | 2776 | 59.5 | 23.1 | 78.2 | 76.9 | 73 | 84.6 | 36.6 | 13.6 | 8938.8 | 9972.7 | 10000 | 17155 | 19566.2 | 19564.9 | 1.919 | 1.962 | 1.956 | 0.501 | 0.557 | 0.548 | -2 | 2.48 | 3.05 | 0.549 | 0.517 | 0.576 | 2.12 | -2.73 | 2.07 | 0.518 | 0.525 | 0.544 | 2.81 | -2.19 | 2.39 | 0.518 | 0.532 | 0.534 | 2.62 | 2.38 | 3.2 | Good_Mixed | 8938.8 | 17155 | 1.919 | 0.557 | 3.05 | 0.576 | 3.2 | 0.8674 | 0.9047 | 0.8688 | 0.9294 | 1 | 0.8617 | 0.812 | 0.8856 | 0.8856 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2435 | 711.9 | 442.9 | 95.2 | 104.7 | 16.1 | 747.7 | 4915.3 | 45.6 | 34.2 | 92 | 91.9 | 82.4 | 99.9 | 39.5 | 26.3 | 5327.9 | 6049.9 | 5634 | 8192.5 | 9325.2 | 8603.1 | 1.538 | 1.541 | 1.527 | 0.714 | 0.75 | 0.78 | 5.07 | -6.27 | 6.17 | 0.652 | 0.709 | 0.66 | 5.57 | -6.43 | 5.87 | 0.719 | 0.637 | 0.741 | 3.97 | 5.7 | -3.58 | 0.752 | 0.699 | 0.696 | 4.99 | 4.21 | 4.45 | Poor_Mixed | 5327.9 | 8192.5 | 1.527 | 0.78 | 6.27 | 0.752 | 6.43 | 0.5055 | 0.7438 | 0.488 | 0.5335 | 1 | 0.4005 | 0.4487 | 0.588 | 0.588 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2436 | 1092.8 | 720.5 | 113.5 | 135 | 21 | 1017.8 | 6268.9 | 59.1 | 21.8 | 78.7 | 78.2 | 71.8 | 83.8 | 35.6 | 13.3 | 8693 | 8526.3 | 9398.2 | 15313.5 | 16284.4 | 17729.5 | 1.762 | 1.91 | 1.886 | 0.548 | 0.573 | 0.567 | 2.75 | 3.35 | -2.88 | 0.568 | 0.559 | 0.554 | 3.46 | 3.06 | 2.75 | 0.577 | 0.597 | 0.647 | 3.98 | 2.83 | 4.37 | 0.599 | 0.567 | 0.591 | -4.04 | 3.46 | 2 | Poor_DGA | 8526.3 | 15313.5 | 1.762 | 0.573 | 3.35 | 0.647 | 4.37 | 0.3247 | 0.9331 | 0.8699 | 0.9367 | 1 | 0.768 | 0.6712 | 0.7153 | 0.7153 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2437 | 864.3 | 410.9 | 101.1 | 129.8 | 15.2 | 792.3 | 5340.9 | 46.8 | 31 | 90.8 | 85.9 | 81.4 | 97.1 | 39.5 | 24.3 | 6380.6 | 5912.4 | 6251.5 | 10277 | 9379.7 | 10050.4 | 1.611 | 1.586 | 1.608 | 0.754 | 0.759 | 0.74 | 5.92 | 5.93 | 5.92 | 0.592 | 0.703 | 0.642 | 5.26 | 3.53 | 5.03 | 0.664 | 0.688 | 0.597 | 4.72 | 5.4 | 4.11 | 0.699 | 0.592 | 0.629 | 2.97 | 3.82 | 4.36 | Poor_Mixed | 5912.4 | 9379.7 | 1.586 | 0.759 | 5.93 | 0.703 | 5.4 | 0.4643 | 0.7829 | 0.5568 | 0.6039 | 1 | 0.3924 | 0.5378 | 0.6076 | 0.6076 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2438 | 1337.1 | 880.3 | 135.1 | 179.1 | 28.8 | 1264.6 | 7767.5 | 37.2 | 41.5 | 101.8 | 105.8 | 90.1 | 111.9 | 43.8 | 31 | 2225.3 | 2239 | 2144.6 | 2675 | 2683.5 | 2500.5 | 1.202 | 1.199 | 1.166 | 0.918 | 0.865 | 0.868 | 8.61 | 8.38 | -9.05 | 0.727 | 0.754 | 0.703 | 6.02 | 8.08 | -8.06 | 0.803 | 0.717 | 0.766 | -7.97 | 8.62 | -5.78 | 0.778 | 0.708 | 0.832 | 7.04 | 6.33 | 5.88 | Very Poor_Mixed | 2144.6 | 2500.5 | 1.166 | 0.918 | 9.05 | 0.832 | 8.62 | 0.1478 | 0.6645 | 0.2108 | 0.3597 | 1 | 0.1449 | 0.311 | 0.392 | 0.392 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2439 | 446 | 307.8 | 84.9 | 83.5 | 11.5 | 586 | 4373.8 | 53.2 | 26.9 | 84.4 | 84.3 | 75.7 | 90.1 | 38.1 | 17.6 | 8021.7 | 6853.7 | 7050.7 | 13634.7 | 11697.8 | 11713.7 | 1.7 | 1.707 | 1.661 | 0.686 | 0.585 | 0.647 | 4.11 | 3.02 | 3.64 | 0.629 | 0.635 | 0.63 | 2 | -4.07 | -4.22 | 0.595 | 0.583 | 0.559 | 3.41 | 3.67 | 2.54 | 0.596 | 0.574 | 0.576 | 3.25 | -3.99 | 3.28 | Fair_Mixed | 6853.7 | 11697.8 | 1.661 | 0.686 | 4.11 | 0.635 | 4.22 | 0.6342 | 0.8397 | 0.6957 | 0.8203 | 1 | 0.637 | 0.6467 | 0.7355 | 0.7355 | Fair | 1 | 0 | No_Anomaly | 0 |  | C2H2
2440 | 1072.7 | 642.7 | 111.2 | 129.2 | 22.9 | 890.7 | 6221.7 | 56.4 | 21.9 | 75.5 | 75 | 70.9 | 80 | 35.2 | 10 | 10000 | 10000 | 10000 | 19440.7 | 19760.3 | 20000 | 1.944 | 1.976 | 2 | 0.55 | 0.573 | 0.533 | 2.68 | 2.65 | 2.43 | 0.5 | 0.562 | 0.522 | 2.01 | 2.2 | 2.09 | 0.511 | 0.529 | 0.545 | 2.79 | 3.23 | -2.43 | 0.539 | 0.559 | 0.509 | -2 | 2 | 2.11 | Poor_DGA | 10000 | 19440.7 | 1.944 | 0.573 | 2.68 | 0.562 | 3.23 | 0.3471 | 0.9307 | 0.977 | 1 | 1 | 0.8136 | 0.8434 | 0.7719 | 0.7719 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2441 | 1757.3 | 880.5 | 136.2 | 184.4 | 34.3 | 1360.3 | 8515.2 | 48.9 | 28.7 | 82 | 80.4 | 75.6 | 88.9 | 37.1 | 11.4 | 8649.1 | 8942.4 | 8112 | 16048.6 | 16437.9 | 14345.9 | 1.856 | 1.838 | 1.768 | 0.613 | 0.615 | 0.627 | 4.01 | 3.48 | -4.61 | 0.577 | 1.464 | 0.557 | 3.49 | 3.99 | 4.45 | 0.61 | 0.529 | 0.579 | 4.06 | 3.5 | 2.75 | 0.526 | 0.577 | 0.618 | 3.15 | 2.77 | -2.95 | Critical_DGA | 8112 | 14345.9 | 1.768 | 0.627 | 4.61 | 1.464 | 4.45 | 0.0675 | 0.8136 | 0.7575 | 0.9783 | 1 | 0.63 | 0.6385 | 0.6023 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Bushing_HV_Y_TanDelta_pct>=1.0%: critical bushing tan delta | C2H2
2442 | 233.5 | 150.4 | 68.1 | 50 | 1.5 | 401.4 | 2899.3 | 58.9 | 20 | 75.4 | 77.9 | 73 | 81.4 | 35.6 | 14.8 | 9522.4 | 10000 | 9661.3 | 18549.4 | 20000 | 19322.7 | 1.948 | 2 | 2 | 0.565 | 0.5 | 0.5 | 3.21 | 2 | -2.5 | 0.57 | 0.5 | 0.509 | 2.64 | 2.14 | 2.43 | 0.517 | 0.555 | 0.508 | 2 | 2.28 | 2.37 | 0.5 | 0.516 | 0.507 | 2.32 | 2 | 2.78 | Good_Mixed | 9522.4 | 18549.4 | 1.948 | 0.565 | 3.21 | 0.57 | 2.78 | 0.9165 | 1 | 0.9119 | 0.8988 | 1 | 0.9018 | 0.8809 | 0.9301 | 0.9301 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2443 | 429.3 | 287.1 | 84.1 | 93.4 | 1.4 | 468.1 | 4146.4 | 57.4 | 20.9 | 90.9 | 88 | 80.6 | 98.6 | 40.3 | 13.4 | 8602.2 | 9212.1 | 10000 | 16160.2 | 17683.3 | 19722.4 | 1.879 | 1.92 | 1.972 | 0.546 | 0.558 | 0.542 | 3.27 | 2.72 | 3.42 | 0.5 | 0.538 | 0.5 | 2.32 | -2.31 | 2.58 | 0.524 | 0.533 | 0.504 | 2 | 2.56 | 2.42 | 0.519 | 0.5 | 0.507 | 2.55 | 2.33 | 2 | Poor_Thermal | 8602.2 | 16160.2 | 1.879 | 0.558 | 3.42 | 0.538 | 2.58 | 0.7927 | 0.9574 | 0.534 | 0.9342 | 1 | 0.7799 | 0.9006 | 0.8445 | 0.8445 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2444 | 848.8 | 490 | 104.6 | 107.3 | 18 | 772.8 | 4789.6 | 60 | 20 | 75 | 78.2 | 71.5 | 81.3 | 36 | 12.2 | 9742.4 | 9639.1 | 10000 | 18351.7 | 18212.6 | 20000 | 1.884 | 1.889 | 2 | 0.572 | 0.57 | 0.529 | 2.55 | 3.39 | -2.5 | 0.574 | 0.542 | 0.578 | 2.78 | 3.19 | 2.3 | 0.529 | 0.564 | 0.55 | -2.81 | 2.93 | -3 | 0.574 | 0.55 | 0.557 | 2.11 | 2.67 | 3.37 | Fair_DGA | 9639.1 | 18212.6 | 1.884 | 0.572 | 3.39 | 0.578 | 3.37 | 0.4657 | 1 | 0.9298 | 0.9618 | 1 | 0.7914 | 0.7427 | 0.782 | 0.782 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2445 | 464.5 | 359.2 | 90.6 | 146.7 | 75.5 | 702.7 | 4524.8 | 49.4 | 29.2 | 105.7 | 106.4 | 95.5 | 115.8 | 45.1 | 17.1 | 8995.9 | 8576.5 | 8424.4 | 16440.4 | 16174.1 | 15033.6 | 1.828 | 1.886 | 1.785 | 0.63 | 0.523 | 0.611 | 3.73 | -2.93 | 3.3 | 0.571 | 0.505 | 0.512 | -3.23 | 2.81 | 3.25 | 0.606 | 0.58 | 0.555 | -2.38 | -2.47 | -3.06 | 0.531 | 0.507 | 0.5 | 2.41 | 3.49 | 2.37 | Critical_Thermal | 8424.4 | 15033.6 | 1.785 | 0.63 | 3.73 | 0.606 | 3.49 | 0.4108 | 0.8067 | 0.1261 | 0.8349 | 1 | 0.7199 | 0.8004 | 0.6587 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2446 | 315.6 | 214.2 | 75.3 | 97.5 | 1 | 592.3 | 3483.3 | 57.2 | 21.7 | 93.2 | 91.3 | 82.1 | 99.7 | 41.5 | 10 | 8648.4 | 10000 | 9446.2 | 15736.9 | 20000 | 18359.1 | 1.82 | 2 | 1.944 | 0.554 | 0.529 | 0.528 | -3.24 | 2.02 | 2 | 0.58 | 0.596 | 0.544 | 2.93 | 3.11 | 3.06 | 0.537 | 0.596 | 0.565 | -2.64 | 4.33 | 3.41 | 0.571 | 0.561 | 0.547 | 2.48 | 3.02 | -3.53 | Poor_Thermal | 8648.4 | 15736.9 | 1.82 | 0.554 | 3.24 | 0.596 | 4.33 | 0.8425 | 0.9355 | 0.4741 | 1 | 1 | 0.8563 | 0.7089 | 0.8278 | 0.8278 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2447 | 1018.5 | 550.5 | 111.3 | 127.4 | 21.2 | 892.1 | 6179.6 | 44.1 | 32.7 | 90.6 | 90.9 | 82.9 | 97.5 | 39.4 | 24.8 | 6155.5 | 4193.8 | 5400.3 | 9554.4 | 5983.4 | 8123.6 | 1.552 | 1.427 | 1.504 | 0.763 | 0.798 | 0.636 | 5.9 | 6.34 | 4.45 | 0.649 | 0.707 | 0.747 | 5.34 | 3.67 | 6.01 | 0.671 | 0.691 | 0.639 | 5.62 | 4.24 | -4.66 | 0.707 | 0.639 | 0.656 | 3.57 | 6.21 | 4.45 | Poor_Mixed | 4193.8 | 5983.4 | 1.427 | 0.798 | 6.34 | 0.747 | 6.21 | 0.3728 | 0.7617 | 0.513 | 0.5865 | 1 | 0.4332 | 0.4739 | 0.5712 | 0.5712 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2448 | 1698.3 | 982.4 | 146.3 | 197 | 33.4 | 1379 | 8843.5 | 35.2 | 44.6 | 107.8 | 103.8 | 95.3 | 117 | 44.3 | 32.6 | 1344.3 | 690 | 1820.6 | 1498.1 | 1200 | 2205 | 1.114 | 1.739 | 1.211 | 0.976 | 0.977 | 0.937 | 9.57 | -9.31 | -9.23 | 0.902 | 0.839 | 0.75 | -7.39 | -7.45 | 8.35 | 0.863 | 0.876 | 0.847 | 8.06 | 6.51 | 9.13 | 0.728 | 0.747 | 0.736 | 7.57 | 9.21 | -6.82 | Very Poor_Mixed | 690 | 1200 | 1.114 | 0.977 | 9.57 | 0.902 | 9.21 | 0.0398 | 0.6338 | 0.13 | 0.2982 | 1 | 0.0553 | 0.2325 | 0.3235 | 0.3235 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2449 | 294.6 | 190.8 | 77.9 | 72.1 | 1.2 | 390 | 3480.7 | 18.2 | 26.2 | 84.2 | 83.3 | 76.4 | 88.8 | 37.8 | 13.1 | 7298.7 | 7102.1 | 6809.2 | 12276.8 | 12476.7 | 11277.7 | 1.682 | 1.757 | 1.656 | 0.974 | 0.959 | 0.955 | 9.76 | 9.27 | 9.84 | 0.5 | 0.584 | 0.565 | 3.07 | -2.6 | 3.14 | 0.581 | 0.5 | 0.527 | 3.04 | 2.4 | 2.25 | 0.531 | 0.568 | 0.533 | 2.71 | 3.31 | 2.28 | Critical_Winding_TD_Cap | 6809.2 | 11277.7 | 1.656 | 0.974 | 9.84 | 0.584 | 3.31 | 0.8767 | 0.2671 | 0.7078 | 0.9414 | 1 | 0.0431 | 0.7966 | 0.6785 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2450 | 286.7 | 211.3 | 76.1 | 71.1 | 1 | 576.5 | 3381.6 | 60 | 20 | 75.5 | 79.3 | 72.3 | 82.3 | 35 | 18.1 | 796 | 690 | 1052.8 | 649.3 | 703.8 | 1073.8 | 0.816 | 1.02 | 1.02 | 0.681 | 0.679 | 0.758 | 5.02 | -5.51 | 5.83 | 0.552 | 0.583 | 0.565 | 2.54 | -2.34 | 2.97 | 0.582 | 0.573 | 0.633 | 2 | 2.77 | 3.24 | 0.62 | 0.581 | 0.579 | -2.37 | 3.28 | -2.94 | Critical_IR_PI | 690 | 649.3 | 0.816 | 0.758 | 5.83 | 0.633 | 3.28 | 0.879 | 1 | 0.9007 | 0.8054 | 0.6687 | 0.4593 | 0.6959 | 0.7666 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | IR_Min_10min<1000 Mohm: critical insulation resistance; PI_Min<1.0: critical polarization index | PI_HV
2451 | 474 | 356.7 | 86 | 87.5 | 11.5 | 676.5 | 3955.3 | 58.3 | 20 | 77.3 | 75.9 | 71.4 | 83.7 | 36.2 | 12.5 | 9534.2 | 10000 | 9524.4 | 18990.6 | 20000 | 18320.8 | 1.992 | 2 | 1.924 | 0.5 | 0.5 | 0.59 | 2.43 | 2 | -2.73 | 0.57 | 0.501 | 0.602 | 2.45 | 2.41 | 3.23 | 0.533 | 0.5 | 0.55 | 2.15 | 2.21 | 3.19 | 0.506 | 0.547 | 0.5 | -2.41 | 3.99 | 2.24 | Fair_DGA | 9524.4 | 18320.8 | 1.924 | 0.59 | 2.73 | 0.602 | 3.99 | 0.6117 | 1 | 0.9109 | 0.9552 | 1 | 0.9031 | 0.8308 | 0.8478 | 0.8478 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2452 | 1740.9 | 981.8 | 137.8 | 192.5 | 30.1 | 1310.4 | 8422.1 | 49.4 | 27.8 | 118.2 | 75 | 71.5 | 80.8 | 35.5 | 15.4 | 8622 | 9262.2 | 7954.9 | 15416.9 | 17703.6 | 14867.5 | 1.788 | 1.911 | 1.869 | 0.577 | 0.583 | 0.538 | 3.12 | 3.21 | 2.56 | 0.616 | 0.554 | 0.608 | 3.07 | 3.86 | 4.17 | 0.623 | 0.632 | 0.564 | -4.05 | 3.96 | -4.48 | 0.625 | 0.619 | 0.657 | 2.95 | 3.86 | 3.4 | Critical_DGA | 7954.9 | 14867.5 | 1.788 | 0.583 | 3.21 | 0.657 | 4.48 | 0.0751 | 0.8264 | 0.7261 | 0.8828 | 1 | 0.7667 | 0.6091 | 0.6117 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | WTI_HV>=110 C: critical HV winding temperature | C2H2
2453 | 711.3 | 488.4 | 97 | 109.4 | 16.5 | 775.2 | 5065.4 | 49.3 | 33 | 89.9 | 89.6 | 84.1 | 98.1 | 39.9 | 23.2 | 5738.3 | 4633.8 | 5591.8 | 8586 | 7142.6 | 9027.8 | 1.496 | 1.541 | 1.614 | 0.755 | 0.753 | 0.77 | 5.2 | 6.57 | 6.21 | 0.639 | 0.642 | 0.701 | 3.88 | 5.8 | 4.6 | 0.669 | 0.697 | 0.642 | 5.46 | 5.43 | 5.45 | 0.708 | 0.691 | 0.634 | -5.41 | 5.23 | 4.43 | Poor_Mixed | 4633.8 | 7142.6 | 1.496 | 0.77 | 6.57 | 0.708 | 5.8 | 0.4868 | 0.7581 | 0.5125 | 0.6416 | 1 | 0.3819 | 0.4764 | 0.5952 | 0.5952 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2454 | 1668.9 | 968.6 | 142.8 | 182.5 | 32.4 | 1338 | 8521.5 | 35.3 | 46.4 | 107.5 | 109.3 | 93.8 | 115.8 | 45.3 | 33.9 | 756.2 | 765.9 | 1287.4 | 1200 | 1200 | 1410.7 | 1.587 | 1.567 | 1.096 | 0.92 | 0.986 | 0.935 | 9 | 9.67 | 9.06 | 0.924 | 0.721 | 0.862 | 6.6 | 7.43 | 7.63 | 0.808 | 0.723 | 0.96 | 7.41 | 6.94 | 5.9 | 0.863 | 0.959 | 0.779 | 6.9 | 8.13 | 8.57 | Very Poor_Mixed | 756.2 | 1200 | 1.096 | 0.986 | 9.67 | 0.96 | 8.57 | 0.0711 | 0.6166 | 0.1084 | 0.2473 | 1 | 0.0727 | 0.2198 | 0.3247 | 0.3247 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2455 | 1603.9 | 826.9 | 139.6 | 181.1 | 34 | 1282.3 | 8338.9 | 32.7 | 47.2 | 108.4 | 106.9 | 94.6 | 117.3 | 43.3 | 33.3 | 875.6 | 1001.5 | 760.3 | 1200 | 1200 | 1200 | 1.37 | 1.198 | 1.578 | 0.931 | 0.941 | 0.926 | 8.78 | 8.97 | 9.31 | 0.947 | 0.729 | 0.839 | 8.01 | 6.08 | 7.28 | 0.868 | 0.796 | 0.905 | 8.53 | 9.18 | -6.31 | 0.901 | 0.874 | 0.945 | 6.41 | 7.54 | 9.11 | Very Poor_Mixed | 760.3 | 1200 | 1.198 | 0.941 | 9.31 | 0.947 | 9.18 | 0.0963 | 0.609 | 0.1191 | 0.2709 | 1 | 0.0934 | 0.1871 | 0.3294 | 0.3294 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2456 | 100 | 124.7 | 66.6 | 50 | 2.4 | 350 | 2617.7 | 58.3 | 22.6 | 76.2 | 75.3 | 72.3 | 80.5 | 35.4 | 10 | 7769.8 | 8851.1 | 9425.7 | 14226.5 | 16075.6 | 17932.9 | 1.831 | 1.816 | 1.903 | 0.5 | 0.528 | 0.5 | 2.16 | 2.94 | 2 | 0.519 | 0.544 | 0.516 | 2.45 | 3.33 | -2.21 | 0.532 | 0.586 | 0.549 | -2.62 | 2.8 | 2.71 | 0.524 | 0.548 | 0.511 | -2 | -2.08 | 2.64 | Fair_IR_PI | 7769.8 | 14226.5 | 1.816 | 0.528 | 2.94 | 0.586 | 3.33 | 0.9222 | 0.915 | 0.9436 | 1 | 1 | 0.9377 | 0.8083 | 0.9215 | 0.9215 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2457 | 1454.9 | 868.5 | 141.6 | 178 | 33.4 | 1220.1 | 7823.7 | 34.4 | 43.2 | 104.3 | 102.9 | 94 | 113.5 | 45.3 | 31.5 | 1792 | 790.9 | 1287.5 | 2165 | 1200 | 1451.2 | 1.208 | 1.517 | 1.127 | 0.85 | 0.851 | 0.918 | 7.54 | 7.79 | -7.73 | 0.837 | 0.799 | 0.791 | -8.27 | 5.63 | -7.25 | 0.825 | 0.799 | 0.835 | -5.87 | -6.75 | 6.62 | 0.867 | 0.743 | 0.81 | 8.53 | 6.64 | 8.77 | Very Poor_Mixed | 790.9 | 1200 | 1.127 | 0.918 | 7.79 | 0.867 | 8.77 | 0.1196 | 0.6474 | 0.1718 | 0.3406 | 1 | 0.2037 | 0.2508 | 0.3755 | 0.3755 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2458 | 672.3 | 441.8 | 93.9 | 98.4 | 10.2 | 685.5 | 4774.9 | 50.6 | 26.1 | 85 | 84.7 | 78.6 | 91.3 | 38.5 | 20.6 | 7226.7 | 7070.9 | 6228.2 | 12275.3 | 11570.4 | 9763.7 | 1.699 | 1.636 | 1.568 | 0.695 | 0.681 | 0.677 | 4.7 | -4.42 | 4.62 | 0.55 | 0.564 | 0.624 | 2.91 | -3.07 | -3.19 | 0.673 | 0.583 | 0.612 | 3.39 | 4.2 | -3.4 | 0.584 | 0.624 | 0.622 | -3.9 | 2.98 | 3.43 | Fair_Mixed | 6228.2 | 9763.7 | 1.568 | 0.695 | 4.7 | 0.673 | 4.2 | 0.5703 | 0.852 | 0.6593 | 0.7276 | 1 | 0.5283 | 0.6359 | 0.6956 | 0.6956 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2459 | 167.5 | 185.3 | 66.6 | 50.7 | 2.2 | 359.9 | 3003.2 | 57.9 | 21.2 | 80.5 | 75.5 | 71 | 84.9 | 36.1 | 13.9 | 9112.6 | 8890.1 | 9858.2 | 17823.1 | 16580.2 | 19144.9 | 1.956 | 1.865 | 1.942 | 0.522 | 0.534 | 0.502 | -2.31 | -2.74 | 2.46 | 0.502 | 0.521 | 0.533 | -2.23 | -2.48 | 2.24 | 0.5 | 0.505 | 0.548 | 2.29 | -2.22 | 2 | 0.526 | 0.527 | 0.507 | 2.26 | 2.09 | 2 | Good_Mixed | 8890.1 | 16580.2 | 1.865 | 0.534 | 2.74 | 0.548 | 2.48 | 0.9026 | 0.9486 | 0.8853 | 0.9219 | 1 | 0.8866 | 0.8845 | 0.9174 | 0.9174 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2460 | 154.3 | 135 | 65.5 | 50 | 2.6 | 455.3 | 3065.1 | 59.1 | 20.3 | 76.2 | 76.9 | 72.4 | 81.5 | 35.9 | 12.8 | 9287.7 | 10000 | 9710 | 17867.8 | 19754.9 | 18677.5 | 1.924 | 1.975 | 1.924 | 0.535 | 0.555 | 0.564 | -2.64 | 2.82 | 2.44 | 0.535 | 0.52 | 0.545 | -3.16 | 2 | 2 | 0.519 | 0.5 | 0.538 | 2 | 2.4 | 2 | 0.504 | 0.513 | 0.5 | 2.75 | -2.57 | 2 | Good_Mixed | 9287.7 | 17867.8 | 1.924 | 0.564 | 2.82 | 0.545 | 3.16 | 0.8847 | 0.9791 | 0.9145 | 0.9484 | 1 | 0.8107 | 0.8812 | 0.9097 | 0.9097 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2461 | 980 | 499.9 | 104.3 | 116.7 | 15.1 | 832.1 | 5048.8 | 43.2 | 36.4 | 91.1 | 90.5 | 83.1 | 96.9 | 40.4 | 26.5 | 7110.9 | 5234 | 5957.7 | 11240.5 | 7782.8 | 8910.7 | 1.581 | 1.487 | 1.496 | 0.738 | 0.743 | 0.726 | 5.94 | 5.66 | 5.64 | 0.623 | 0.632 | 0.628 | -3.94 | 5.22 | 4.41 | 0.637 | 0.697 | 0.718 | 4.69 | 3.98 | 4.48 | 0.658 | 0.683 | 0.708 | 5.25 | 3.18 | 4.79 | Poor_Mixed | 5234 | 7782.8 | 1.487 | 0.743 | 5.94 | 0.718 | 5.25 | 0.4541 | 0.7186 | 0.5077 | 0.5264 | 1 | 0.4153 | 0.5065 | 0.5862 | 0.5862 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2462 | 691.3 | 489.2 | 102.1 | 94.6 | 14.8 | 852 | 5458.8 | 60 | 20.9 | 77.7 | 79.5 | 71.5 | 81.5 | 36.6 | 12.4 | 7954.6 | 9433.9 | 9302.7 | 13872.3 | 17714 | 17545.4 | 1.744 | 1.878 | 1.886 | 0.559 | 0.585 | 0.5 | 2.99 | 2.93 | 2.47 | 0.588 | 0.533 | 0.5 | 2.09 | 2.68 | 2.27 | 0.535 | 0.532 | 0.538 | 3.36 | 2.39 | 2.4 | 0.541 | 0.565 | 0.559 | -2.52 | 2.83 | 2 | Fair_DGA | 7954.6 | 13872.3 | 1.744 | 0.585 | 2.99 | 0.588 | 3.36 | 0.4979 | 0.9574 | 0.8772 | 0.9575 | 1 | 0.8238 | 0.7986 | 0.794 | 0.794 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2463 | 1565.1 | 888.5 | 141.2 | 178.1 | 31.7 | 1235.9 | 7867.7 | 33 | 46.4 | 106.4 | 105.4 | 91.5 | 111.7 | 43.8 | 33.2 | 1785.1 | 1973 | 2403.6 | 2003.8 | 2191.2 | 2981.4 | 1.123 | 1.111 | 1.24 | 0.947 | 0.914 | 0.873 | 9.49 | -8.72 | 8.98 | 0.773 | 0.738 | 0.88 | 7.84 | 8.57 | -9.39 | 0.795 | 0.713 | 0.754 | 9.47 | 6.93 | 8.84 | 0.725 | 0.772 | 0.787 | 8.72 | 7.1 | 6.29 | Very Poor_Mixed | 1785.1 | 2003.8 | 1.111 | 0.947 | 9.49 | 0.88 | 9.47 | 0.1149 | 0.6166 | 0.1802 | 0.2748 | 1 | 0.1062 | 0.2604 | 0.3562 | 0.3562 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2464 | 1501.9 | 808.4 | 140.2 | 173.2 | 30.4 | 1191.8 | 7924.8 | 36.2 | 42.5 | 105.6 | 109.3 | 92.5 | 114.7 | 44.3 | 32.3 | 1664.5 | 971.8 | 1254.5 | 1918.6 | 1200 | 1320.7 | 1.153 | 1.235 | 1.053 | 0.877 | 0.914 | 0.9 | 8.02 | 8.49 | 9.11 | 0.798 | 0.875 | 0.75 | 6.04 | 7.89 | -6.46 | 0.845 | 0.855 | 0.934 | 6.02 | 7.92 | -7.78 | 0.812 | 0.903 | 0.805 | -6.56 | 8.21 | -8.85 | Very Poor_Mixed | 971.8 | 1200 | 1.053 | 0.914 | 9.11 | 0.934 | 8.85 | 0.1431 | 0.6544 | 0.139 | 0.3098 | 1 | 0.1425 | 0.2185 | 0.363 | 0.363 | Very Poor | 0 | 1 | Thermal | 0 |  | C2H2
2465 | 826.7 | 508.6 | 105.2 | 125.4 | 18.9 | 862.1 | 5357.4 | 48.1 | 32.9 | 89.1 | 89.2 | 81.9 | 98.1 | 40.5 | 25.4 | 5707.4 | 5962.1 | 5536.7 | 9663.6 | 8725.5 | 8692.5 | 1.693 | 1.463 | 1.57 | 0.701 | 0.68 | 0.725 | -5.26 | -5.15 | -4.84 | 0.716 | 0.626 | 0.663 | 5.14 | -3.92 | 5.25 | 0.6 | 0.603 | 0.638 | -5.71 | 4.88 | 4.76 | 0.645 | 0.616 | 0.724 | 5.39 | -5.24 | 5.06 | Poor_Mixed | 5536.7 | 8692.5 | 1.463 | 0.725 | 5.26 | 0.724 | 5.71 | 0.4248 | 0.7593 | 0.5305 | 0.5655 | 1 | 0.4829 | 0.5073 | 0.5976 | 0.5976 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2466 | 1191 | 666.5 | 117.3 | 149.4 | 24.5 | 1014.7 | 5585.1 | 55.7 | 22.8 | 75.8 | 80.1 | 70.6 | 84 | 36.4 | 14.8 | 9105.5 | 8800.7 | 9411.7 | 17840 | 16350.5 | 17658.5 | 1.959 | 1.858 | 1.876 | 0.634 | 0.575 | 0.544 | 4.16 | 3.83 | 2.55 | 0.523 | 0.511 | 0.538 | 2.39 | 2.18 | 2 | 0.531 | 0.541 | 0.549 | -2.27 | -2 | -2.77 | 0.513 | 0.529 | 0.537 | 2 | 2.24 | 2.35 | Poor_DGA | 8800.7 | 16350.5 | 1.858 | 0.634 | 4.16 | 0.549 | 2.77 | 0.2963 | 0.9108 | 0.8918 | 0.8988 | 1 | 0.7093 | 0.8372 | 0.7275 | 0.7275 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2467 | 1613 | 844.5 | 143.5 | 179.1 | 32.6 | 1202.7 | 8076.3 | 33.9 | 45.8 | 102.9 | 106.5 | 94.6 | 112.9 | 44.3 | 31.9 | 2175 | 1383.4 | 2480.3 | 2380.8 | 1461.7 | 3146 | 1.095 | 1.057 | 1.268 | 0.863 | 0.878 | 0.9 | 8.56 | 8.28 | -7.58 | 0.674 | 0.945 | 0.797 | 6.94 | 5.78 | 6.23 | 0.907 | 0.92 | 0.833 | 8.27 | -7.25 | -6.92 | 0.86 | 0.924 | 0.767 | -6.88 | 6.97 | -5.78 | Very Poor_Mixed | 1383.4 | 1461.7 | 1.057 | 0.9 | 8.56 | 0.945 | 8.27 | 0.1106 | 0.6222 | 0.1666 | 0.3252 | 1 | 0.1748 | 0.2334 | 0.3617 | 0.3617 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2468 | 626.1 | 486.4 | 96.2 | 113 | 8.6 | 678.5 | 5138.6 | 57.1 | 23.3 | 76.8 | 76.2 | 71.8 | 82.9 | 36 | 12.2 | 8767.8 | 9612.6 | 8829.3 | 16526.2 | 18439.7 | 15466.1 | 1.885 | 1.918 | 1.752 | 0.553 | 0.517 | 0.5 | 2.64 | -2.25 | 2.8 | 0.558 | 0.5 | 0.52 | -2.74 | 3.01 | 2.13 | 0.501 | 0.548 | 0.574 | 2.24 | 2.16 | 2.31 | 0.532 | 0.531 | 0.507 | -2.27 | 2.06 | 2.23 | Fair_DGA | 8767.8 | 15466.1 | 1.752 | 0.553 | 2.8 | 0.574 | 3.01 | 0.5646 | 0.9008 | 0.9136 | 0.9618 | 1 | 0.882 | 0.847 | 0.8246 | 0.8246 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2469 | 986 | 577.2 | 109.5 | 130.9 | 18.9 | 980.8 | 5709.7 | 45.3 | 34.5 | 89.7 | 91.8 | 82.9 | 99.3 | 40.2 | 24.4 | 6268.4 | 5260.9 | 6422.3 | 9963.5 | 7580.3 | 10375.6 | 1.589 | 1.441 | 1.616 | 0.746 | 0.717 | 0.758 | -6.75 | 5.19 | 6.35 | 0.695 | 0.615 | 0.675 | 4.21 | 3.23 | 4.96 | 0.665 | 0.625 | 0.641 | 3.93 | -5.5 | 5.07 | 0.612 | 0.645 | 0.673 | 3.84 | 4.69 | 3.15 | Poor_Mixed | 5260.9 | 7580.3 | 1.441 | 0.758 | 6.75 | 0.695 | 5.5 | 0.3783 | 0.7403 | 0.499 | 0.6005 | 1 | 0.3926 | 0.532 | 0.5741 | 0.5741 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2470 | 913.5 | 483.7 | 102.9 | 122.4 | 20.9 | 894.3 | 5555.7 | 57.8 | 20.6 | 79.4 | 78.5 | 73.4 | 82.1 | 35.5 | 13.2 | 9370.1 | 9702.1 | 8405.2 | 17648.9 | 18579.7 | 15954.7 | 1.884 | 1.915 | 1.898 | 0.523 | 0.544 | 0.537 | 2.52 | 2.17 | 3.22 | 0.5 | 0.567 | 0.539 | 2.1 | 2.28 | 2.56 | 0.522 | 0.547 | 0.502 | -2 | -2.29 | 2.87 | 0.549 | 0.5 | 0.515 | 2.2 | -2 | 2.23 | Poor_DGA | 8405.2 | 15954.7 | 1.884 | 0.544 | 3.22 | 0.567 | 2.87 | 0.4076 | 0.9672 | 0.8555 | 0.939 | 1 | 0.8406 | 0.8643 | 0.7837 | 0.7837 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2471 | 417.8 | 338.7 | 77.2 | 72.3 | 4.4 | 3118.3 | 23305.6 | 60 | 20.5 | 84.3 | 85.4 | 77.4 | 87.1 | 37.9 | 21.1 | 1527.7 | 897.5 | 1256.4 | 1558.2 | 915.4 | 1286.8 | 1.02 | 1.02 | 1.024 | 0.727 | 0.746 | 0.706 | -5.78 | 7.5 | 5.27 | 0.559 | 0.591 | 0.557 | 2.48 | -2.81 | -2 | 0.541 | 0.56 | 0.538 | 2.81 | -2.57 | -3.16 | 0.57 | 0.566 | 0.541 | 2.56 | 2.23 | -3.18 | Critical_IR_PI | 897.5 | 915.4 | 1.02 | 0.746 | 7.5 | 0.591 | 3.18 | 0.5614 | 0.9709 | 0.6922 | 0.7114 | 0.925 | 0.4005 | 0.7492 | 0.7006 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | CO>=1400 and CO2>=10000 ppm: critical cellulose degradation; IR_Min_10min<1000 Mohm: critical insulation resistance | CO
2472 | 881.7 | 564.6 | 108.3 | 120.4 | 17.2 | 873.2 | 5720.6 | 44.2 | 34.2 | 87.4 | 95.5 | 82.5 | 98.7 | 40.4 | 24.4 | 5777.3 | 6311.2 | 5694.8 | 9129.3 | 10091.5 | 9057.9 | 1.58 | 1.599 | 1.591 | 0.783 | 0.795 | 0.648 | 6.96 | 6.56 | -5.59 | 0.663 | 0.662 | 0.786 | 5.24 | 5.58 | 3.44 | 0.653 | 0.659 | 0.728 | -5.18 | 4.96 | -5.68 | 0.747 | 0.738 | 0.685 | 3.94 | -4.74 | 5.41 | Poor_Mixed | 5694.8 | 9057.9 | 1.58 | 0.795 | 6.96 | 0.786 | 5.68 | 0.4221 | 0.7438 | 0.4957 | 0.6005 | 1 | 0.3796 | 0.4442 | 0.5675 | 0.5675 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2473 | 211.6 | 161.6 | 68.8 | 63.6 | 2.2 | 426.2 | 3110.7 | 59.4 | 22.2 | 77.9 | 78.3 | 73.5 | 84.2 | 36 | 11.3 | 5282 | 5392.9 | 5790 | 8543.4 | 8379 | 9195.3 | 1.617 | 1.554 | 1.588 | 0.589 | 0.568 | 0.552 | -3.19 | 2.97 | 3.87 | 0.53 | 0.605 | 0.502 | -2.61 | 2.34 | 2.15 | 0.536 | 0.602 | 0.556 | -2.62 | 2 | 2.98 | 0.536 | 0.5 | 0.53 | -2.14 | -2 | 2.61 | Poor_IR_PI | 5282 | 8379 | 1.554 | 0.589 | 3.87 | 0.605 | 2.98 | 0.8616 | 0.9238 | 0.8581 | 0.9802 | 1 | 0.7354 | 0.8134 | 0.8704 | 0.8704 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2474 | 483.6 | 309.5 | 86.8 | 82.6 | 36.2 | 593.1 | 3805.7 | 53.1 | 25.9 | 82.6 | 77.3 | 75.6 | 85.3 | 37.2 | 15.3 | 744 | 703.5 | 923.3 | 792.8 | 717.6 | 950.5 | 1.066 | 1.02 | 1.029 | 0.71 | 0.68 | 0.729 | 5.44 | -5.44 | 4.7 | 0.501 | 0.5 | 0.512 | 3.03 | 2.22 | -2 | 0.56 | 0.5 | 0.567 | -3.04 | 2.61 | 2.74 | 0.537 | 0.572 | 0.544 | 2.49 | 2.95 | 3.24 | Critical_IR_PI | 703.5 | 717.6 | 1.02 | 0.729 | 5.44 | 0.572 | 3.24 | 0.5028 | 0.8552 | 0.7993 | 0.8855 | 0.775 | 0.4728 | 0.8305 | 0.6922 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication; IR_Min_10min<1000 Mohm: critical insulation resistance | C2H2
2475 | 189.7 | 120 | 65 | 50 | 3 | 383.8 | 3320 | 58.9 | 21.9 | 75.4 | 77.9 | 72.4 | 83.7 | 35 | 11.3 | 9300.1 | 9061.4 | 9676.4 | 17806.3 | 17760.4 | 19352.7 | 1.915 | 1.96 | 2 | 0.557 | 0.5 | 0.501 | 2.14 | -2.11 | 2.66 | 0.525 | 0.519 | 0.5 | 2.03 | 2.32 | 2 | 0.566 | 0.519 | 0.538 | -2.7 | 2.27 | -2.2 | 0.547 | 0.543 | 0.528 | 2.39 | 2 | 2.67 | Good_Mixed | 9061.4 | 17760.4 | 1.915 | 0.557 | 2.66 | 0.566 | 2.7 | 0.8861 | 0.9307 | 0.9076 | 0.9802 | 1 | 0.9196 | 0.8384 | 0.9126 | 0.9126 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2476 | 1492.9 | 829 | 134.7 | 183.9 | 25.8 | 1184.5 | 7504.6 | 37.7 | 40.8 | 99.3 | 102 | 88.7 | 110.7 | 43.4 | 31.3 | 1783.9 | 1539.5 | 1913.7 | 2165.4 | 1701.1 | 2211.2 | 1.214 | 1.105 | 1.155 | 0.94 | 0.9 | 0.944 | -8.57 | 7.55 | -9.21 | 0.818 | 0.732 | 0.672 | 7.04 | -5.44 | 8.41 | 0.871 | 0.898 | 0.798 | 6.67 | 8.12 | 5.69 | 0.872 | 0.694 | 0.785 | 8.03 | -6.21 | 7.93 | Very Poor_Mixed | 1539.5 | 1701.1 | 1.105 | 0.944 | 9.21 | 0.898 | 8.41 | 0.1652 | 0.6716 | 0.2637 | 0.3483 | 1 | 0.1261 | 0.2754 | 0.3929 | 0.3929 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2477 | 994.9 | 573.4 | 113.5 | 136.6 | 15.6 | 973.7 | 4761.4 | 48.4 | 32.8 | 93.8 | 90.2 | 81.9 | 98 | 40.2 | 24.9 | 5677.6 | 6207.4 | 5518.7 | 9381.4 | 9727.6 | 8495.1 | 1.652 | 1.567 | 1.539 | 0.754 | 0.678 | 0.76 | 5.26 | 4.65 | 6.32 | 0.802 | 0.77 | 0.738 | 4.87 | 5.2 | 5.52 | 0.721 | 0.635 | 0.664 | 4.28 | 4.35 | -4.69 | 0.694 | 0.708 | 0.782 | 6.06 | 5.63 | 4.6 | Poor_Mixed | 5518.7 | 8495.1 | 1.539 | 0.76 | 6.32 | 0.802 | 6.06 | 0.4013 | 0.7605 | 0.4959 | 0.5831 | 1 | 0.44 | 0.416 | 0.5668 | 0.5668 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2478 | 226.9 | 120 | 66.6 | 59.4 | 57 | 419.8 | 2504.5 | 51 | 26.4 | 81.2 | 81.3 | 75.9 | 87.7 | 35.9 | 17.4 | 8930.6 | 9263.1 | 8918.8 | 16541.5 | 17509.2 | 17568.1 | 1.852 | 1.89 | 1.97 | 0.943 | 0.927 | 0.933 | 9.21 | 9.35 | 8.49 | 0.521 | 0.544 | 0.559 | 2 | 2.86 | 3.75 | 0.5 | 0.576 | 0.51 | 2.16 | 2.82 | -2.47 | 0.518 | 0.569 | 0.585 | 2.72 | 2.64 | -2.49 | Critical_Winding_TD_Cap | 8918.8 | 16541.5 | 1.852 | 0.943 | 9.35 | 0.585 | 3.75 | 0.6279 | 0.8474 | 0.7663 | 0.8262 | 1 | 0.0925 | 0.7987 | 0.6933 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2479 | 183.5 | 181.6 | 66.4 | 52 | 1 | 462.4 | 2699.6 | 27.9 | 25.7 | 80.1 | 79.4 | 72.8 | 83.8 | 36.9 | 18.5 | 880.7 | 739.1 | 690 | 898.3 | 753.9 | 750.1 | 1.02 | 1.02 | 1.087 | 0.727 | 0.712 | 0.717 | 5.87 | 5.52 | -5.51 | 0.557 | 0.503 | 0.632 | 2.8 | 2.82 | 2.21 | 0.555 | 0.567 | 0.57 | 3.35 | -3.64 | -2.95 | 0.502 | 0.616 | 0.529 | -3.22 | 2.73 | -2.7 | Critical_IR_PI | 690 | 750.1 | 1.02 | 0.727 | 5.87 | 0.632 | 3.64 | 0.9504 | 0.2751 | 0.8309 | 0.7933 | 0.775 | 0.4365 | 0.7513 | 0.7137 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength; IR_Min_10min<1000 Mohm: critical insulation resistance | BDV
2480 | 1204 | 688 | 122.7 | 158.8 | 24.2 | 1062.1 | 6540.5 | 56.9 | 25.1 | 75.1 | 75 | 70.3 | 80 | 35 | 12.6 | 9949.8 | 9575.1 | 9288.5 | 19899.6 | 18185.9 | 18208.8 | 2 | 1.899 | 1.96 | 0.612 | 0.604 | 0.653 | -3.92 | 3.89 | 3.67 | 0.574 | 0.522 | 0.56 | -3.2 | 2.35 | 3.04 | 0.5 | 0.508 | 0.556 | -2 | -2.47 | 2.88 | 0.534 | 0.561 | 0.518 | -2.25 | -2.56 | 2.03 | Poor_DGA | 9288.5 | 18185.9 | 1.899 | 0.653 | 3.92 | 0.574 | 3.2 | 0.2661 | 0.8683 | 0.9919 | 0.953 | 1 | 0.6376 | 0.8165 | 0.7138 | 0.7138 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2481 | 926.8 | 585.9 | 109 | 118.1 | 17.6 | 764.7 | 5537.6 | 46.2 | 33.5 | 92.6 | 94.6 | 81.8 | 100.2 | 40.2 | 24.8 | 6386.2 | 4508.2 | 5186.7 | 10259.9 | 6663.9 | 7677.4 | 1.607 | 1.478 | 1.48 | 0.735 | 0.776 | 0.789 | -6.26 | 5.91 | 5.89 | 0.567 | 0.772 | 0.652 | 3.94 | 5.29 | -4.99 | 0.646 | 0.751 | 0.658 | -5.63 | -4.55 | 5.53 | 0.703 | 0.583 | 0.583 | 5.39 | -4.49 | 5.7 | Poor_Mixed | 4508.2 | 6663.9 | 1.478 | 0.789 | 6.26 | 0.772 | 5.7 | 0.4309 | 0.752 | 0.465 | 0.5865 | 1 | 0.3743 | 0.5003 | 0.5763 | 0.5763 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2482 | 319.4 | 164.3 | 71.2 | 76.9 | 3.3 | 421.2 | 2500 | 56.9 | 22.8 | 79.5 | 79.4 | 116.5 | 86.3 | 36.8 | 18.6 | 7803.1 | 8191.9 | 7732.5 | 13894.1 | 14552.7 | 13848.9 | 1.781 | 1.776 | 1.791 | 0.987 | 0.983 | 0.982 | -8.95 | -9.65 | -9.84 | 0.588 | 0.527 | 0.541 | 2.87 | 2.78 | 2 | 0.594 | 0.581 | 0.538 | 2.72 | 2 | 2.74 | 0.581 | 0.515 | 0.56 | -2.93 | 2.24 | -2.67 | Critical_Winding_TD_Cap | 7732.5 | 13848.9 | 1.776 | 0.987 | 9.84 | 0.594 | 2.93 | 0.8111 | 0.9108 | 0.6542 | 0.7902 | 1 | 0.0362 | 0.759 | 0.7187 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | OTI>=100 C: critical oil temperature | Winding_HV_TanDelta_pct
2483 | 211.1 | 175.4 | 68.4 | 50 | 2.2 | 431 | 2500 | 58.3 | 20.3 | 75 | 76.3 | 71.2 | 81.3 | 35.2 | 13.4 | 10000 | 8565.4 | 8746.9 | 19136.5 | 16002.3 | 16738.8 | 1.914 | 1.868 | 1.914 | 0.525 | 0.505 | 0.516 | -3.17 | -2.07 | 2.6 | 0.504 | 0.529 | 0.558 | 2.27 | 2.31 | 3.04 | 0.52 | 0.553 | 0.585 | -2.9 | 2.81 | 2.58 | 0.518 | 0.577 | 0.52 | 2.17 | -2.86 | 3.83 | Good_Mixed | 8565.4 | 16002.3 | 1.868 | 0.525 | 3.17 | 0.585 | 3.83 | 0.8884 | 0.9791 | 0.9566 | 0.9342 | 1 | 0.8864 | 0.7919 | 0.9086 | 0.9086 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2484 | 1389.2 | 809.1 | 139.2 | 163.8 | 28.5 | 1178.6 | 7351.1 | 33.9 | 45.3 | 102.7 | 102.9 | 89.9 | 111.1 | 43.5 | 31.8 | 2194.7 | 1839.5 | 2851.2 | 2693.5 | 2266.4 | 3428.7 | 1.227 | 1.232 | 1.203 | 0.903 | 0.868 | 0.892 | 8 | 7.64 | 7.5 | 0.733 | 0.863 | 0.855 | 6.5 | -6.79 | 5.92 | 0.876 | 0.688 | 0.747 | -6.42 | -8.32 | -6.67 | 0.694 | 0.846 | 0.861 | 7.08 | 6.43 | -5.92 | Very Poor_Mixed | 1839.5 | 2266.4 | 1.203 | 0.903 | 8 | 0.876 | 8.32 | 0.1776 | 0.627 | 0.2292 | 0.3291 | 1 | 0.1915 | 0.285 | 0.3971 | 0.3971 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2
2485 | 690.7 | 367.3 | 91.8 | 94.6 | 11.9 | 744.9 | 4681.1 | 51.6 | 28.4 | 87 | 85.8 | 78.3 | 95.3 | 38.3 | 23.4 | 7859.1 | 8071.4 | 7221.2 | 13258.5 | 14294.8 | 11881 | 1.687 | 1.771 | 1.645 | 0.679 | 0.667 | 0.67 | 4.75 | 4.81 | -3.87 | 0.576 | 0.683 | 0.609 | -4.71 | -4.26 | 3.06 | 0.572 | 0.568 | 0.577 | 4.28 | -4.74 | 3.31 | 0.609 | 0.67 | 0.602 | 4.34 | -2.53 | -4.87 | Poor_Mixed | 7221.2 | 11881 | 1.645 | 0.679 | 4.81 | 0.683 | 4.87 | 0.5618 | 0.8178 | 0.6202 | 0.6348 | 1 | 0.5466 | 0.6065 | 0.678 | 0.678 | Fair | 1 | 1 | Winding_TD_Cap | 0 |  | C2H2
2486 | 344.6 | 175.7 | 65 | 92.2 | 1 | 445.4 | 3291.4 | 59.3 | 20 | 88.4 | 87.9 | 78.3 | 95.6 | 38 | 10 | 8769.5 | 9114.7 | 10000 | 15751.6 | 17610.9 | 19017.8 | 1.796 | 1.932 | 1.902 | 0.559 | 0.547 | 0.581 | -3.17 | 2.56 | 3.36 | 0.604 | 0.547 | 0.5 | 2.81 | 2.34 | 2.42 | 0.539 | 0.512 | 0.5 | 3.27 | -2 | 3.16 | 0.522 | 0.585 | 0.534 | -2.44 | 2 | 2.95 | Poor_Thermal | 8769.5 | 15751.6 | 1.796 | 0.581 | 3.36 | 0.604 | 3.27 | 0.8796 | 1 | 0.596 | 1 | 1 | 0.7667 | 0.8206 | 0.8645 | 0.8645 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2487 | 990.1 | 576.5 | 111 | 117.7 | 17.7 | 872.7 | 5943.3 | 45.8 | 34.9 | 90.2 | 89 | 82.3 | 99 | 40.2 | 23.4 | 5960.8 | 7106.3 | 6494.2 | 9628.3 | 11443.2 | 10246.3 | 1.615 | 1.61 | 1.578 | 0.737 | 0.697 | 0.774 | -5.85 | -4.82 | -6.54 | 0.763 | 0.638 | 0.713 | 5.21 | -3.32 | 4.89 | 0.66 | 0.699 | 0.66 | -4.36 | 5.07 | 5.51 | 0.674 | 0.613 | 0.638 | -6.43 | 3.54 | -4.91 | Poor_Mixed | 5960.8 | 9628.3 | 1.578 | 0.774 | 6.54 | 0.763 | 6.43 | 0.4074 | 0.7356 | 0.5195 | 0.6348 | 1 | 0.4168 | 0.4837 | 0.5792 | 0.5792 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2488 | 1032.3 | 565 | 109.6 | 123.4 | 21.9 | 908.2 | 5337.9 | 46.2 | 33.8 | 87.6 | 87.7 | 79.7 | 95.6 | 39.4 | 26.8 | 6120.8 | 5463.9 | 6433.8 | 10247.2 | 8558.3 | 10684.8 | 1.674 | 1.566 | 1.661 | 0.685 | 0.724 | 0.769 | 5.23 | 4.92 | -5.38 | 0.579 | 0.648 | 0.722 | 3.94 | -6.59 | 4.05 | 0.632 | 0.642 | 0.664 | 5.71 | 3.72 | 4.71 | 0.686 | 0.611 | 0.586 | 4.42 | 4.27 | 5.21 | Poor_Mixed | 5463.9 | 8558.3 | 1.566 | 0.769 | 5.38 | 0.722 | 6.59 | 0.3784 | 0.7485 | 0.5849 | 0.5156 | 1 | 0.4565 | 0.529 | 0.5878 | 0.5878 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2489 | 610.8 | 403.4 | 88.6 | 95.8 | 49.7 | 525.5 | 4450.7 | 30.6 | 49.4 | 79.7 | 81.2 | 75 | 88.3 | 38.1 | 14.7 | 5075.8 | 5659.6 | 5272.6 | 7364.4 | 8661.9 | 7459.9 | 1.451 | 1.53 | 1.415 | 0.626 | 0.652 | 0.641 | 4.28 | 5.06 | 4.51 | 0.643 | 0.551 | 0.581 | 3.82 | 2.77 | 3.97 | 0.593 | 0.579 | 0.579 | -2.71 | 4.14 | 2.92 | 0.542 | 0.586 | 0.625 | 3.05 | 3.48 | 3.42 | Critical_Oil | 5075.8 | 7364.4 | 1.415 | 0.652 | 5.06 | 0.643 | 4.14 | 0.4696 | 0.5888 | 0.772 | 0.9014 | 1 | 0.5715 | 0.6652 | 0.6701 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2490 | 145.3 | 170.7 | 71.6 | 51.4 | 2.5 | 358.7 | 3137.7 | 30.6 | 86.9 | 79 | 78.8 | 72.5 | 83 | 35.6 | 16.3 | 3633.3 | 4091.2 | 4488.7 | 4859.5 | 5779.4 | 6377.2 | 1.337 | 1.413 | 1.421 | 0.66 | 0.728 | 0.692 | -4.84 | -5.21 | 5.6 | 0.5 | 0.556 | 0.528 | 2.99 | 2.08 | -2.2 | 0.519 | 0.506 | 0.523 | 2.43 | 2.53 | 2 | 0.5 | 0.512 | 0.51 | 2 | -2 | 2 | Critical_Oil | 3633.3 | 4859.5 | 1.337 | 0.728 | 5.6 | 0.556 | 2.99 | 0.8945 | 0.5833 | 0.8591 | 0.8578 | 1 | 0.4839 | 0.8918 | 0.8107 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2491 | 1620.8 | 934.2 | 143.7 | 188.9 | 34.3 | 1345.7 | 7899.1 | 34.3 | 47.4 | 107.3 | 109.3 | 95.7 | 118.2 | 45.2 | 31.9 | 1419.3 | 1992.9 | 1186.4 | 1490.3 | 2119.7 | 1268.8 | 1.05 | 1.064 | 1.069 | 0.94 | 0.986 | 0.949 | 9.79 | 9.84 | 9.21 | 0.875 | 0.903 | 0.909 | 5.93 | -7.51 | -8.52 | 0.827 | 0.825 | 0.821 | 7.33 | 7.14 | 6.82 | 0.939 | 0.769 | 0.938 | 6.53 | 6.41 | 6.23 | Very Poor_Mixed | 1186.4 | 1268.8 | 1.05 | 0.986 | 9.84 | 0.939 | 8.52 | 0.0713 | 0.6072 | 0.0877 | 0.3252 | 1 | 0.0465 | 0.2075 | 0.3196 | 0.3196 | Very Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2492 | 122.6 | 148.1 | 70.9 | 60.6 | 2.8 | 413.1 | 2504.6 | 54.2 | 26 | 75.2 | 76.8 | 72.5 | 80 | 35.7 | 14.8 | 5003.7 | 4212.6 | 4846.3 | 7477.7 | 5712.6 | 6844.4 | 1.494 | 1.356 | 1.412 | 0.608 | 0.685 | 0.592 | 3.92 | 4.28 | 3.23 | 0.5 | 0.534 | 0.57 | 3 | 3.59 | -2.38 | 0.55 | 0.547 | 0.591 | -3.85 | 3.21 | -3.28 | 0.514 | 0.517 | 0.571 | 3.09 | 2.87 | -2.69 | Poor_IR_PI | 4212.6 | 5712.6 | 1.356 | 0.685 | 4.28 | 0.591 | 3.85 | 0.8679 | 0.8536 | 0.9379 | 0.8988 | 1 | 0.635 | 0.7719 | 0.846 | 0.846 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H2
2493 | 948.9 | 592.1 | 109.6 | 135.1 | 21 | 825.8 | 5643.9 | 44.3 | 33.5 | 89.4 | 89.4 | 81.8 | 94.4 | 38.9 | 25.6 | 6678.5 | 6399.9 | 6215.9 | 10753.7 | 10213.8 | 10048.5 | 1.61 | 1.596 | 1.617 | 0.757 | 0.71 | 0.747 | 6.24 | 5.5 | 6.57 | 0.794 | 0.802 | 0.659 | 4.12 | 5.14 | 4.22 | 0.747 | 0.736 | 0.619 | 5.46 | 5.79 | 4.13 | 0.712 | 0.693 | 0.646 | -5.19 | 5.79 | 4.72 | Poor_Mixed | 6215.9 | 10048.5 | 1.596 | 0.757 | 6.57 | 0.802 | 5.79 | 0.3828 | 0.752 | 0.5565 | 0.5584 | 1 | 0.3941 | 0.4333 | 0.5627 | 0.5627 | Poor | 0 | 1 | DGA | 0 |  | C2H2
2494 | 1620.1 | 982.4 | 138.7 | 190.5 | 52.5 | 1291 | 8280.5 | 55.1 | 26.1 | 81.2 | 78.4 | 74.4 | 86.3 | 36.3 | 10 | 7373.2 | 7917 | 6428.7 | 13378.8 | 13778.7 | 10610.1 | 1.815 | 1.74 | 1.65 | 0.54 | 0.58 | 0.546 | 2.67 | 2.27 | 2.67 | 0.5 | 0.5 | 0.536 | 2 | -2 | 2.39 | 0.5 | 0.528 | 0.508 | 2.35 | 2 | 2.15 | 0.549 | 0.513 | 0.5 | 2 | 2.7 | 2.25 | Critical_DGA | 6428.7 | 10610.1 | 1.65 | 0.58 | 2.67 | 0.549 | 2.7 | 0.0668 | 0.852 | 0.8084 | 1 | 1 | 0.8123 | 0.9117 | 0.6876 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | C2H2>=35 ppm: critical arcing indication | C2H2
2495 | 904.1 | 507.1 | 96.7 | 119.6 | 19 | 833.1 | 5816.5 | 47 | 35.3 | 92.3 | 90.8 | 84.8 | 100.4 | 40.3 | 26.8 | 5800.2 | 5749.7 | 5294.1 | 9060.8 | 8912.8 | 8095.7 | 1.562 | 1.55 | 1.529 | 0.746 | 0.76 | 0.748 | 5.63 | 6.26 | -5.95 | 0.705 | 0.668 | 0.691 | 4.97 | 3.99 | 5.01 | 0.727 | 0.653 | 0.743 | 6 | -4.12 | 5.02 | 0.637 | 0.737 | 0.751 | 5.61 | 4.82 | -5.38 | Poor_Mixed | 5294.1 | 8095.7 | 1.529 | 0.76 | 6.26 | 0.751 | 6 | 0.4286 | 0.731 | 0.4706 | 0.5156 | 1 | 0.3909 | 0.4416 | 0.5619 | 0.5619 | Poor | 0 | 1 | Winding_TD_Cap | 0 |  | C2H2
2496 | 501.4 | 371.4 | 89 | 143.8 | 2.6 | 602 | 4382.6 | 53.8 | 55.4 | 105.1 | 106.9 | 92.3 | 114.1 | 44.4 | 12.3 | 8505.8 | 9308.5 | 8292.7 | 16142.6 | 17104.3 | 15200.1 | 1.898 | 1.837 | 1.833 | 0.576 | 0.519 | 0.552 | 2.95 | 3.02 | 3.2 | 0.54 | 0.541 | 0.549 | 2.23 | -3.05 | 2.48 | 0.515 | 0.562 | 0.521 | 2.81 | 3.15 | 2.46 | 0.56 | 0.525 | 0.518 | 2 | 2.37 | 2.73 | Critical_Thermal | 8292.7 | 15200.1 | 1.833 | 0.576 | 3.2 | 0.562 | 3.15 | 0.6641 | 0.5833 | 0.1582 | 0.9597 | 1 | 0.7883 | 0.8024 | 0.7146 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | Moisture>=50 ppm: critical moisture | Moisture_PPM
2497 | 204.8 | 233.5 | 73.4 | 109.9 | 1 | 500.2 | 3136.2 | 56.6 | 22.6 | 94.8 | 94.1 | 82.8 | 101.4 | 40.6 | 14.7 | 10000 | 9136.7 | 9091.1 | 20000 | 17990.9 | 18115.2 | 2 | 1.969 | 1.993 | 0.519 | 0.523 | 0.559 | 3.55 | 2.3 | -3.4 | 0.507 | 0.551 | 0.513 | 2.66 | 3.21 | 2.63 | 0.513 | 0.526 | 0.525 | 2.86 | 2.21 | 2.32 | 0.514 | 0.547 | 0.555 | 2 | -3.37 | 2.11 | Poor_Thermal | 9091.1 | 17990.9 | 1.969 | 0.559 | 3.55 | 0.555 | 3.37 | 0.8556 | 0.915 | 0.4394 | 0.9014 | 1 | 0.8142 | 0.8287 | 0.8359 | 0.8359 | Good | 1 | 0 | No_Anomaly | 0 |  | C2H4
2498 | 1022.9 | 559.2 | 106.9 | 123.3 | 23.9 | 868.5 | 5561.8 | 59.1 | 23.1 | 75.5 | 75.3 | 70.8 | 82.8 | 35 | 13.3 | 9495.7 | 8896.7 | 9791.6 | 18847.8 | 16900.9 | 19117.1 | 1.985 | 1.9 | 1.952 | 0.543 | 0.573 | 0.558 | 2.48 | -2.87 | -2.83 | 0.537 | 0.55 | 0.568 | 2.29 | 3.25 | -3.01 | 0.5 | 0.614 | 0.544 | 3.21 | 3.26 | 2.82 | 0.558 | 0.507 | 0.57 | 2.56 | 2.83 | -3.22 | Fair_DGA | 8896.7 | 16900.9 | 1.9 | 0.573 | 2.87 | 0.614 | 3.26 | 0.3736 | 0.9047 | 0.9576 | 0.9367 | 1 | 0.7935 | 0.7676 | 0.7538 | 0.7538 | Fair | 1 | 1 | DGA | 0 |  | C2H2
2499 | 588.6 | 374.3 | 84.1 | 83 | 1.9 | 661.8 | 4801.2 | 25.2 | 28.5 | 76.1 | 76.8 | 71.3 | 84.1 | 35.5 | 15.3 | 1967.1 | 1605.8 | 1603.7 | 2319.7 | 1741.1 | 1798.7 | 1.179 | 1.084 | 1.122 | 0.753 | 0.758 | 0.718 | -5.93 | 5.72 | 6.17 | 0.606 | 0.527 | 0.595 | 3.48 | 3.44 | -2.57 | 0.598 | 0.597 | 0.53 | -4.02 | 3.67 | 2.19 | 0.523 | 0.613 | 0.579 | -4.4 | 3.04 | 4.17 | Critical_IR_PI | 1603.7 | 1741.1 | 1.084 | 0.758 | 6.17 | 0.613 | 4.4 | 0.7269 | 0.2331 | 0.9159 | 0.8855 | 1 | 0.3985 | 0.689 | 0.6854 | 0 | Critical | 0 | 1 | Hard_Capped_Critical | 1 | BDV<=30 kV: critical oil dielectric strength | BDV
2500 | 1452.6 | 819.3 | 141.9 | 180.2 | 34.3 | 1321.7 | 8194.2 | 34.5 | 44.9 | 103.4 | 108.5 | 94.4 | 116.1 | 42.7 | 31.9 | 1368.2 | 1600.9 | 2061.7 | 1709.3 | 1759.9 | 2420.4 | 1.249 | 1.099 | 1.174 | 0.954 | 0.93 | 0.918 | 9.09 | 8.59 | 8.62 | 0.759 | 0.838 | 0.856 | 6.33 | 7.2 | -6.78 | 0.771 | 0.79 | 0.806 | 6.31 | 7.34 | 8.94 | 0.676 | 0.79 | 0.752 | 7.07 | 7.46 | 6.08 | Very Poor_Mixed | 1368.2 | 1709.3 | 1.099 | 0.954 | 9.09 | 0.856 | 8.94 | 0.1032 | 0.6309 | 0.1494 | 0.3252 | 1 | 0.1053 | 0.2838 | 0.3585 | 0.3585 | Very Poor | 0 | 1 | DGA | 0 |  | C2H2

## Summary
Transformer HI 48-Input Synthetic Training Dataset
Rows | 2500
Input Features | 48
Model targets | HI_Final (regression), Condition (classification), Anomaly_Flag (binary anomaly)
Hard-capped rows | 500
Generation approach | Weighted nonlinear scoring + hard capping + targeted anomalies
Note | Synthetic research/training dataset; validate thresholds against utility/OEM standard before field use.
Condition | Count
Good | 500
Fair | 500
Poor | 500
Very Poor | 500
Critical | 500
Anomaly Type | Count
Winding_TD_Cap | 738
DGA | 631
No_Anomaly | 589
Hard_Capped_Critical | 500
Thermal | 23
Bushing_TD_Cap | 19

## Feature_Weights
Feature | Weight | Group | Bad_Direction | Good_or_Normal | Hard_Cap | Sensitivity_Alpha | Reason
H2 | 0.035 | DGA | Higher is worse | <= 100 | >= 1800 | 0.85 | Hydrogen: PD/low-energy discharge marker; medium sensitivity
CH4 | 0.025 | DGA | Higher is worse | <= 120 | >= 1000 | 0.95 | Methane: low-temperature thermal/partial discharge marker
C2H6 | 0.015 | DGA | Higher is worse | <= 65 | >= 150 | 1.15 | Ethane: low-temperature thermal marker; lower severity than acetylene
C2H4 | 0.04 | DGA | Higher is worse | <= 50 | >= 200 | 0.75 | Ethylene: high-temperature thermal fault marker; high sensitivity
C2H2 | 0.08 | DGA | Higher is worse | <= 1 | >= 35 | 0.45 | Acetylene: high-energy arcing marker; highest DGA sensitivity
CO | 0.035 | DGA | Higher is worse | <= 350 | >= 1400 | 0.8 | CO: cellulose/paper thermal degradation marker
CO2 | 0.02 | DGA | Higher is worse | <= 2500 | >= 10000 | 1.35 | CO2: paper ageing trend; slower sensitivity than CO
BDV | 0.07 | Oil Quality | Lower is worse | >= 30 | <= 60 | 0.7 | Oil dielectric strength; low BDV has high impact
Moisture_PPM | 0.05 | Oil Quality | Higher is worse | <= 20 | >= 50 | 0.65 | Moisture accelerates insulation ageing and reduces BDV
WTI_HV | 0.025 | Thermal/Loading | Higher is worse | <= 75 | >= 110 | 0.75 | HV winding temperature; high thermal ageing impact
WTI_LV | 0.025 | Thermal/Loading | Higher is worse | <= 75 | >= 110 | 0.75 | LV winding temperature; high thermal ageing impact
OTI | 0.02 | Thermal/Loading | Higher is worse | <= 70 | >= 100 | 0.8 | Oil temperature; high temperature increases ageing rate
Loading_pct | 0.02 | Thermal/Loading | Higher is worse | <= 80 | >= 120 | 1 | Loading; contributes to thermal stress
Ambient_Temp | 0.01 | Thermal/Loading | Higher is worse | <= 35 | >= 50 | 1.2 | Ambient temperature; indirect thermal stress
Age_Years | 0.05 | Age | Higher is worse | <= 10 | >= 40 | 1.25 | Age is a slow ageing factor, not an instant fault marker
IR_HV_E_1min | 0.012 | Winding IR/PI | Lower is worse | >= 500 | <= 10000 | 0.55 | 1-min insulation resistance; low value is critical
IR_LV_E_1min | 0.012 | Winding IR/PI | Lower is worse | >= 500 | <= 10000 | 0.55 | 1-min insulation resistance; low value is critical
IR_TV_E_1min | 0.012 | Winding IR/PI | Lower is worse | >= 500 | <= 10000 | 0.55 | 1-min insulation resistance; low value is critical
IR_HV_E_10min | 0.012 | Winding IR/PI | Lower is worse | >= 1000 | <= 20000 | 0.55 | 10-min insulation resistance; low value is critical
IR_LV_E_10min | 0.012 | Winding IR/PI | Lower is worse | >= 1000 | <= 20000 | 0.55 | 10-min insulation resistance; low value is critical
IR_TV_E_10min | 0.012 | Winding IR/PI | Lower is worse | >= 1000 | <= 20000 | 0.55 | 10-min insulation resistance; low value is critical
PI_HV | 0.029 | Winding IR/PI | Lower is worse | >= 1.0 | <= 2.0 | 0.6 | Polarization index; <1 hard cap, >=2 good
PI_LV | 0.029 | Winding IR/PI | Lower is worse | >= 1.0 | <= 2.0 | 0.6 | Polarization index; <1 hard cap, >=2 good
PI_TV | 0.03 | Winding IR/PI | Lower is worse | >= 1.0 | <= 2.0 | 0.6 | Polarization index; <1 hard cap, >=2 good
Winding_HV_TanDelta_pct | 0.025 | Winding TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.6 | Winding insulation dielectric loss; high sensitivity
Winding_LV_TanDelta_pct | 0.025 | Winding TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.6 | Winding insulation dielectric loss; high sensitivity
Winding_TV_TanDelta_pct | 0.025 | Winding TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.6 | Winding insulation dielectric loss; high sensitivity
Winding_HV_CapChange_pct | 0.021667 | Winding TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.85 | Winding capacitance change; geometry/insulation change
Winding_LV_CapChange_pct | 0.021667 | Winding TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.85 | Winding capacitance change; geometry/insulation change
Winding_TV_CapChange_pct | 0.021667 | Winding TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.85 | Winding capacitance change; geometry/insulation change
Bushing_HV_R_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_HV_Y_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_HV_B_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_HV_R_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_HV_Y_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_HV_B_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_LV_R_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_LV_Y_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_LV_B_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_LV_R_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_LV_Y_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_LV_B_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_TV_R_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_TV_Y_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_TV_B_TanDelta_pct | 0.014 | Bushing TanDelta/Capacitance | Higher is worse | <= 0.5 | >= 1.0 | 0.55 | Bushing tan delta; high impact because bushing failures are critical
Bushing_TV_R_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_TV_Y_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication
Bushing_TV_B_CapChange_pct | 0.006 | Bushing TanDelta/Capacitance | Absolute change higher is worse | abs <= 2.0 | abs >= 10.0 | 0.8 | Bushing capacitance change; physical/electrical defect indication

## Limits_and_Capping
Rule_Type | Condition | Action | Reason
Hard Cap | C2H2 >= 35 ppm | HI_Final = 0; Condition = Critical | High-energy arcing indication; highest DGA sensitivity
Hard Cap | BDV <= 30 kV | HI_Final = 0; Condition = Critical | Oil dielectric strength critically low
Hard Cap | Moisture_PPM >= 50 ppm | HI_Final = 0; Condition = Critical | Severe moisture contamination
Hard Cap | WTI_HV >= 110°C OR WTI_LV >= 110°C | HI_Final = 0; Condition = Critical | Critical winding temperature
Hard Cap | OTI >= 100°C | HI_Final = 0; Condition = Critical | Critical oil temperature
Hard Cap | CO >= 1400 ppm AND CO2 >= 10000 ppm | HI_Final = 0; Condition = Critical | Severe cellulose/paper degradation indicator
Hard Cap | Any IR 1-min < 500 MΩ | HI_Final = 0; Condition = Critical | Winding insulation resistance critically low
Hard Cap | Any IR 10-min < 1000 MΩ | HI_Final = 0; Condition = Critical | 10-minute IR critically low
Hard Cap | Any PI < 1.0 | HI_Final = 0; Condition = Critical | Polarization index below 1.0 indicates serious insulation weakness
Hard Cap | Any winding TanDelta >= 1.0% | HI_Final = 0; Condition = Critical | Critical winding insulation dielectric loss
Hard Cap | Any winding capacitance change abs >= 10% | HI_Final = 0; Condition = Critical | Possible winding movement/partial breakdown
Hard Cap | Any bushing TanDelta >= 1.0% | HI_Final = 0; Condition = Critical | Critical bushing insulation dielectric loss
Hard Cap | Any bushing capacitance change abs >= 10% | HI_Final = 0; Condition = Critical | Physical/electrical bushing defect indication
Scoring | HI_Final >= 0.80 | Good
Scoring | 0.60 <= HI_Final < 0.80 | Fair
Scoring | 0.40 <= HI_Final < 0.60 | Poor
Scoring | 0.20 <= HI_Final < 0.40 | Very Poor
Scoring | HI_Final < 0.20 | Critical

## Sources
Source | URL | Used for
IEEE C57.104-2019 summary | https://www.hvassets.com/en/post/dissolved-gas-analysis-procedure-based-on-ieee-c57-104-2019 | DGA diagnostic framework and key gases
IEC 60422 official preview PDF | https://www.iec.ch/system/files/2024-02/iec_60422_-_1_feb_2024_-_v2e.pdf | Mineral insulating oil tests: BDV, water content, acidity, IFT
OMICRON transformer tan delta/capacitance | https://www.omicronenergy.com/en/solution/dissipation-power-factor-capacitance-measurement-on-power-transformers/ | Tan delta/capacitance rationale for insulation, winding displacement and bushing defects
Megger transformer bushings | https://www.megger.com/en-ca/applications/transformers/bushings | Bushing tan delta/C1/C2/capacitance diagnosis and failure modes
Transformer health index sensitivity paper | https://transformers-magazine.com/files/Transformer-health-index_Sensitivity-analysis-and-critical-discussion-%E2%80%93-Part-II.pdf | Need for nonlinear scoring and caution against masking faults with simple weighted average

## Training_Guide
How to use this dataset
Input feature range | Columns B:AW in Training_Data_48 are the 48 model inputs.
Regression target | HI_Final
Classification target | Condition
Anomaly detection target | Anomaly_Flag; Anomaly_Type can be used as multiclass anomaly family.
Do not train on | Scenario_Generator, subscores, HI_PreCap, Hard_Cap_Reason, Dominant_Risk_Parameter; these are explanation/output columns.
Recommended pipeline | Train/test split with stratification on Condition; RandomForest/XGBoost baseline; evaluate MAE/RMSE/R2 and confusion matrix.
Prediction logic | Apply hard capping after prediction also, using the same rules from Limits_and_Capping.
Important note | This is a synthetic training dataset for prototyping. Real deployment requires utility/OEM thresholds, temperature correction, recent trend/rate-of-change data, and expert validation.

## Trend_Based_Capping_48
Parameter | Group | Bad_Direction | Rule_Status | 1-Year Worsening % for HI=0 | 2-Year Cumulative Worsening % for HI=0 | Denominator Floor | Minimum Absolute Change | Activation Gate | Comparability / Confirmation | Exact Trend Hard-Cap Logic | Technical Reason | Source URLs | Important Note
H2 | DGA | Higher is worse | Active | 75 | 150 | 10 | 100 | Current H2 ≥ 900 ppm | Same sampling/lab method; confirm abnormal rise with repeat DGA. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Sudden hydrogen growth can indicate active discharge or thermal activity. Percentage rule is gated to avoid low-baseline noise. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
CH4 | DGA | Higher is worse | Active | 75 | 150 | 10 | 50 | Current CH4 ≥ 500 ppm | Same sampling/lab method; confirm with other hydrocarbon gases. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid methane growth at an elevated level suggests active low-temperature thermal/PD behaviour. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
C2H6 | DGA | Higher is worse | Active | 60 | 120 | 5 | 10 | Current C2H6 ≥ 75 ppm | Same sampling/lab method; assess with CH4/C2H4. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Ethane is a lower-temperature thermal marker; trend cap requires elevated concentration and material increase. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
C2H4 | DGA | Higher is worse | Active | 60 | 120 | 5 | 15 | Current C2H4 ≥ 100 ppm | Same sampling/lab method; assess with temperature-fault gas pattern. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Ethylene is associated with higher-temperature thermal faults; rapid sustained growth is high risk. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
C2H2 | DGA | Higher is worse | Active—strict | 75 | 150 | 1 | 2 | Current C2H2 ≥ 5 ppm | Repeat DGA promptly; confirm with H2/C2H4 and operating events. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Acetylene is the most sensitive arcing marker. Near-zero percentage jumps are ignored by absolute-change safeguards. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
CO | DGA | Higher is worse | Active | 50 | 100 | 50 | 100 | Current CO ≥ 700 ppm | Interpret with CO2, furan and loading/temperature history. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid CO growth may indicate accelerating cellulose thermal degradation. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
CO2 | DGA | Higher is worse | Active | 40 | 80 | 250 | 500 | Current CO2 ≥ 5000 ppm | Interpret with CO/CO2 ratio, furan and paper-ageing context. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | CO2 is a slower paper-ageing marker; a lower percentage threshold is used only after an elevated-level gate. | https://standards.ieee.org/ieee/C57.104/7476/ https://webstore.iec.ch/en/publication/66491 https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
BDV | Oil Quality | Lower is worse | Active | 20 | 30 | 10 | 5 | Current BDV ≤ 40 kV | Same electrode gap/method and comparable oil temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Large BDV decline near the poor range suggests rapidly worsening moisture or contamination. | https://webstore.iec.ch/en/publication/66421 https://standards.ieee.org/ieee/C57.106/5361/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Moisture_PPM | Oil Quality | Higher is worse | Active | 40 | 75 | 5 | 5 | Current moisture ≥ 30 ppm | Compare at similar oil temperature or use relative saturation correction. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Moisture accelerates paper ageing and depresses dielectric strength; the gate limits normal test scatter. | https://webstore.iec.ch/en/publication/66421 https://standards.ieee.org/ieee/C57.106/5361/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
WTI_HV | Thermal/Loading | Higher is worse | Active with normalization | 12 | 20 | 20 | 8 | Current WTI ≥ 95°C | Only compare when loading differs by ≤10 percentage points and ambient differs by ≤5°C. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Winding-temperature trend is meaningful only under comparable loading and ambient conditions. | https://standards.ieee.org/ieee/C57.91/7163/ | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
WTI_LV | Thermal/Loading | Higher is worse | Active with normalization | 12 | 20 | 20 | 8 | Current WTI ≥ 95°C | Only compare when loading differs by ≤10 percentage points and ambient differs by ≤5°C. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Winding-temperature trend is meaningful only under comparable loading and ambient conditions. | https://standards.ieee.org/ieee/C57.91/7163/ | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
OTI | Thermal/Loading | Higher is worse | Active with normalization | 12 | 20 | 20 | 8 | Current OTI ≥ 85°C | Only compare when loading differs by ≤10 percentage points and ambient differs by ≤5°C. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Top-oil temperature trend must be normalized for load and ambient temperature. | https://standards.ieee.org/ieee/C57.91/7163/ | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Loading_pct | Thermal/Loading | Higher is worse | Composite only | 20 | 35 | 20 | 10 | Current loading ≥110% and previous year ≥100% | HI=0 only if WTI/OTI is also ≥90% of its absolute hard limit. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Loading is operating stress, not a defect by itself; it requires thermal corroboration. | https://standards.ieee.org/ieee/C57.91/7163/ | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Ambient_Temp | Thermal/Loading | Higher is worse | No standalone cap |  |  | 10 |  | Not applicable | Use only for temperature correction. | No standalone trend hard cap. Use this parameter only for correction, weighting or a composite rule. | Ambient temperature is an external condition and must not independently force transformer HI to zero. | https://standards.ieee.org/ieee/C57.91/7163/ | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Age_Years | Age | Higher is worse | No standalone cap |  |  | 1 |  | Not applicable | Use as age-weighting or expected-degradation modifier. | No standalone trend hard cap. Use this parameter only for correction, weighting or a composite rule. | Age changes predictably and should modify weighting, not independently create a trend hard cap. | https://standards.ieee.org/ieee/C57.152/7662/ | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
IR_HV_E_1min | Winding IR/PI | Lower is worse | Active | 60 | 80 | 500 | 300 | Current corrected IR ≤1500 MΩ | Temperature-correct all readings to same reference temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | A major corrected 1-minute IR decline near the risk region indicates worsening leakage/insulation condition. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
IR_LV_E_1min | Winding IR/PI | Lower is worse | Active | 60 | 80 | 500 | 300 | Current corrected IR ≤1500 MΩ | Temperature-correct all readings to same reference temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | A major corrected 1-minute IR decline near the risk region indicates worsening leakage/insulation condition. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
IR_TV_E_1min | Winding IR/PI | Lower is worse | Active | 60 | 80 | 500 | 300 | Current corrected IR ≤1500 MΩ | Temperature-correct all readings to same reference temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | A major corrected 1-minute IR decline near the risk region indicates worsening leakage/insulation condition. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
IR_HV_E_10min | Winding IR/PI | Lower is worse | Active | 60 | 80 | 1000 | 600 | Current corrected IR ≤3000 MΩ | Temperature-correct all readings to same reference temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Large 10-minute IR decline indicates worsening absorption and insulation condition. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
IR_LV_E_10min | Winding IR/PI | Lower is worse | Active | 60 | 80 | 1000 | 600 | Current corrected IR ≤3000 MΩ | Temperature-correct all readings to same reference temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Large 10-minute IR decline indicates worsening absorption and insulation condition. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
IR_TV_E_10min | Winding IR/PI | Lower is worse | Active | 60 | 80 | 1000 | 600 | Current corrected IR ≤3000 MΩ | Temperature-correct all readings to same reference temperature. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Large 10-minute IR decline indicates worsening absorption and insulation condition. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
PI_HV | Winding IR/PI | Lower is worse | Active | 30 | 45 | 1 | 0.25 | Current PI ≤1.30 | Same test voltage, duration and temperature-correction practice. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid PI decline near the critical range indicates loss of insulation polarization behaviour. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
PI_LV | Winding IR/PI | Lower is worse | Active | 30 | 45 | 1 | 0.25 | Current PI ≤1.30 | Same test voltage, duration and temperature-correction practice. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid PI decline near the critical range indicates loss of insulation polarization behaviour. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
PI_TV | Winding IR/PI | Lower is worse | Active | 30 | 45 | 1 | 0.25 | Current PI ≤1.30 | Same test voltage, duration and temperature-correction practice. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid PI decline near the critical range indicates loss of insulation polarization behaviour. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Winding_HV_TanDelta_pct | Winding TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct and use same test configuration. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid dielectric-loss growth near 1.0% is a strong deterioration signal. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Winding_LV_TanDelta_pct | Winding TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct and use same test configuration. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid dielectric-loss growth near 1.0% is a strong deterioration signal. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Winding_TV_TanDelta_pct | Winding TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct and use same test configuration. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid dielectric-loss growth near 1.0% is a strong deterioration signal. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Winding_HV_CapChange_pct | Winding TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Same tap position, test connection and reference baseline. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid growth in absolute capacitance deviation may indicate winding movement or insulation geometry change. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Winding_LV_CapChange_pct | Winding TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Same tap position, test connection and reference baseline. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid growth in absolute capacitance deviation may indicate winding movement or insulation geometry change. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Winding_TV_CapChange_pct | Winding TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Same tap position, test connection and reference baseline. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid growth in absolute capacitance deviation may indicate winding movement or insulation geometry change. | https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_HV_R_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_HV_Y_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_HV_B_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_HV_R_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_HV_Y_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_HV_B_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_LV_R_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_LV_Y_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_LV_B_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_LV_R_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_LV_Y_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_LV_B_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_TV_R_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_TV_Y_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_TV_B_TanDelta_pct | Bushing TanDelta/Capacitance | Higher is worse | Active | 50 | 100 | 0.1 | 0.2 | Current tanδ ≥0.75% | Temperature-correct; compare with nameplate/factory and prior results. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid bushing tan-delta growth near 1.0% indicates deteriorating dielectric losses. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_TV_R_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_TV_Y_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.
Bushing_TV_B_CapChange_pct | Bushing TanDelta/Capacitance | Absolute change higher is worse | Active | 75 | 150 | 1 | 3 | ¦Current cap-change¦ ≥6% | Compare with original C1/nameplate baseline and same test setup. | Set Dynamic HI = 0 only when activation gate is satisfied and minimum absolute change is met, plus any one condition: (1) latest-year worsening ≥ 1-year limit AND previous interval also worsened; (2) total T-2 to T0 worsening ≥ 2-year cumulative limit AND latest interval worsened; (3) sudden latest-year worsening ≥ 1.5 × 1-year limit. Apply the original absolute hard caps independently. | Rapid absolute C1 capacitance deviation may indicate bushing layer deterioration; absolute 10% remains the current hard cap. | https://standards.ieee.org/ieee/C57.19.100/11436/ https://standards.ieee.org/ieee/C57.152/7662/ https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf | Proposed conservative model policy. IEEE/IEC generally require trend/rate interpretation but do not publish one universal annual percentage for every parameter. Validate with OEM, utility history and real field data.

## Trend_Capping_Sources
Source | Use in Trend Policy | URL
IEEE C57.104-2019 | DGA interpretation, concentration and trend/rate principles | https://standards.ieee.org/ieee/C57.104/7476/
IEC 60599:2022 | Interpretation of dissolved/free gases and recommended future action | https://webstore.iec.ch/en/publication/66491
USBR FIST 3-30 | Explicitly emphasizes sudden gas production-rate increase and comparison with older DGAs | https://www.usbr.gov/power/data/fist/fist3_30/fist3_30.pdf
IEEE C57.152-2025 | Field diagnostic tests including IR, PI, tan delta and capacitance | https://standards.ieee.org/ieee/C57.152/7662/
IEEE C57.91 | Loading, ambient and thermal-ageing context | https://standards.ieee.org/ieee/C57.91/7163/
IEC 60422 | Oil supervision and maintenance guidance | https://webstore.iec.ch/en/publication/66421
IEEE C57.106 | Mineral insulating-oil evaluation and maintenance | https://standards.ieee.org/ieee/C57.106/5361/
IEEE C57.19.100 | Power-bushing application/condition context | https://standards.ieee.org/ieee/C57.19.100/11436/
USBR Transformer Maintenance and Diagnostics | Comparison of diagnostic results with previous/factory data | https://usbr.gov/tsc/techreferences/mands/mands-pdfs/Trnsfrmr.pdf

## Trend_Capping_Guide
Trend-Based Hard Capping — Implementation Guide
Higher-is-worse formula | Worsening % = (Current − Previous) / MAX(¦Previous¦, Denominator Floor) × 100
Lower-is-worse formula | Worsening % = (Previous − Current) / MAX(¦Previous¦, Denominator Floor) × 100
Capacitance-change formula | Use absolute magnitudes: (¦Current¦ − ¦Previous¦) / MAX(¦Previous¦, Denominator Floor) × 100
Why denominator floor is required | It prevents false 500–1000% alarms when the previous value was close to zero.
Why minimum absolute change is required | A percentage threshold alone is unreliable for gases, tan delta and capacitance when values are small.
Recommended HI=0 rule | Use trend hard cap only after activation gate + absolute-change safeguard + persistent/cumulative/sudden deterioration logic.
Current absolute hard caps | Always apply the existing Limits_and_Capping rules independently after model prediction.
Ambient and age | Never independently hard-cap HI from ambient temperature or age trend.
Loading | Use loading trend only as a composite cap with corroborating WTI/OTI stress.
Thermal values | Compare WTI/OTI only at comparable loading and ambient temperature, otherwise normalize first.
IR/PI/tan delta | Use identical test method and temperature correction before calculating trend.
Critical disclaimer | The percentages are conservative research/model thresholds, not universal percentages directly mandated by IEEE/IEC. Calibrate using actual transformer test histories before operational deployment.