## Sheet1
Parameter | 0–10 yr | 11–20 yr | 21–30 yr | 31–40 yr | >40 yr | Reason
H₂ ppm | 700 | 850 | 1000 | 1100 | 1200 | Excess hydrogen indicates partial discharge or overheating.
CH₄ ppm | 490 | 595 | 700 | 770 | 840 | Elevated methane indicates low-temperature thermal faults.
C₂H₆ ppm | 70 | 85 | 100 | 110 | 120 | High ethane indicates oil overheating.
C₂H₄ ppm | 105 | 128 | 150 | 165 | 180 | High ethylene indicates high-temperature thermal faults.
C₂H₂ ppm | 14 | 17 | 20 | 22 | 24 | Acetylene indicates electrical arcing and is a critical fault indicator.
CO ppm* | 700 | 850 | 1000 | 1100 | 1200 | High CO indicates cellulose (paper insulation) degradation.
CO₂ ppm* | 5600 | 6800 | 8000 | 8800 | 9600 | High CO₂ with CO indicates advanced paper ageing.
Moisture ppm | 28 | 34 | 40 | 44 | 48 | High moisture reduces dielectric strength and insulation life.
HV/LV WTI °C | 95 | 100 | 105 | 105 | 105 | High winding temperature accelerates insulation ageing.
OTI °C | 85 | 90 | 95 | 95 | 95 | High oil temperature indicates thermal overstress.
Loading % | 100 | 110 | 120 | 120 | 120 | Overloading causes excessive heating and accelerated ageing.
Winding Tan δ % | 0.7 | 0.85 | 1 | 1 | 1 | High winding tan delta indicates insulation deterioration or moisture.
Bushing Tan δ % | 0.7 | 0.85 | 1 | 1 | 1 | High bushing tan delta indicates deteriorated bushing insulation.
Capacitance change % | 5.6 | 6.8 | 8 | 8.8 | 9.6 | Capacitance deviation indicates insulation or mechanical degradation.
BDV minimum kV | 49 | 42 | 35 | 30 | 25 | Low BDV indicates contaminated or wet insulating oil.
IR 1-min minimum MΩ | 1400 | 1200 | 1000 | 850 | 700 | Low insulation resistance indicates weak insulation.
IR 10-min minimum MΩ | 2800 | 2400 | 2000 | 1700 | 1400 | Low 10-minute IR indicates severe insulation degradation.
PI minimum | 1.75 | 1.5 | 1.25 | 1.1 | 1 | Low PI indicates wet or contaminated insulation.
CFT IR minimum MΩ | 1400 | 1200 | 1000 | 850 | 700 | Low Core-Frame-Tank IR indicates core insulation failure.